## Drop Codes (hidden)
RoomClassification | IA | QualificationTest
Not Classified | Direct Impact | Yes
Grade A | Indirect Impact | No
Grade B | No Impact | n/a
Grade C
Grade D

## URS Document
User Requirement Specification |  |  | CPI Internal Tender Reference & Title:- | 1354 | Containment Room Modifications at CPIs Coxon Building
| The evalution team will consider bidders combined responses below and give a single overall score based on the adjacent rating in column D, of which the total Quality element score of this sheet will equate to value in column G |  |  |  | The total percentage available which will contribute towards the Quality scoring element of this tender is contained within column G, of which the evaluation team will assess in the "Office Use Only" section below at the base of this form | 30%
USER REQUIREMENT |  |  |  |  | Tenderer Response
Requirement codes |  |  |  |  | Guidance: Tenderers must provide responses within the following Columns;
M | Mandatory. (This must be the minimum requirement for the usage for the equipment, any further performance requirements above the minimum, must be marked as Desirable) |  |  |  | 1. Column F - Please provide details of your equipment functionality in relation to CPI requirements specified in column E
O | Optional requirement which may be quoted for and an assessment made by CPI prior to purchase |  |  |  | 2. Column G - Please confirm if your product complies with CPI's functionality requirements specified in Column E, by providing a Yes (Y) or No (N) response
D | Desirable, but not necessary - if this can be supplied. Tenderer should suggest alternative if appropriate
Parameter |  | Requirement |  | Requirement (M/O/D) -see codes | Answer or Details with regards to meeting the Requirement | Complies? (Y/N)
System performance
1.1 | Construction | The document OPTION 1 CPI-NFC-GA-022 revD shows the desired layout of the containment room post modification. The extension will have the same internal height as the existing build. |  | M
1.2 |  | The existing build has a ceiling void above the main room which contains the HVAC system, the roof of this void is to be removed to create a plant deck, and this will allow easy access for maintenance and other work. The extension will also be open top. The below image shows the existing build with the roof removed. |  | M
1.3 |  | A cage ladder is required to access the roof for maintenance, the roof perimeter also requires railing to remove the requirement of fall restraint PPE. |  | M
1.4 |  | The new extension will also be open access. The roof of the extension should support 2 persons per panel as well as any HVAC/other hardware to be installed for the operation of the extension. |  | M
1.5 |  | Internal surfaces will be easily cleaned, suitable for pharmaceutical processing and resistant to a number of solvents. Changes to electrical services etc. that would be required to achieve this should be included. |  | M
1.6 |  | Construction will consider possible build up areas of material and design and work to a minimise this. |  | M
1.7 |  | Any filters will be ‘safe-change’ and the design will enable sufficient space for operators to ergonomically and safely achieve their contained change. |  | M
1.8 |  | The existing roller door needs to be replaced with an opaque double fire exit with door closures, the fire exit will have push bars to operate and will open into F0.28, the door also will create a seal when closed to minimise material release from the containment room. This will not present a smaller opening than the current construction. |  | M
1.9 |  | An exhaust duct and fan is required from the containment room to the Coxon roof, the duct will connect to a stack at roof level. Alternatives which enable robust material containment will be considered. |  | M
1.1 |  | A sample transfer hatch (minimum 50cm x 50 cm x 50cm objects should freely pass) should be included. |  | M
1.11 |  | We intend to use a Raman laser within the room, so any internal design should contain laser light, preferably through materials of construction, but laser blinds are permissible for the sample transfer hatch. |  | M
2.1 | Operation | The containment room will be controlled at the existing HDMI panel, either altering the existing software/hardware or installing new software/hardware. |  | M
2.2 |  | The containment room will have a negative pressure cascade from AREA 1 to the containment room (F0.28.1). The required pressures are as follows: AREA 1 @ +5 Pa, AREA 2 @ -10 Pa, containment room (F0.28.1) @ -15 Pa and AREA 3 @ -10 Pa. All pressures are in relation to F0.28 pressure which is monitored and controlled by the BMS system. |  | M
2.3 |  | All doors will be interlocked, only one door to open at a time. A time delay is required between one door closing to the other being operated, this is to allow the pressure within the different AREAs to settle. The doors will be operated using push buttons with indication lights to show when the door is active or inactive. A time delay of 5 seconds is required between a door closing to another being opened. |  | M
2.4 |  | The door interlocks will be controlled from inside the build when the laser is in operation. Ideally this will be through direct link to the laser instrument, but separate operator control is permissible. |  | M
2.5 |  | Ventilation air will be single pass. Air will be taken from F0.28 into the containment room and exhausted via a stack on the roof of the Coxon building. Alternative air flow designs which enable robust material containment will be considered. |  | M
2.6 |  | The ventilation system intake will be designed with safe changed HEPA filters or one way valves to prevent contaminated air from re-entering F028, safe change filters will be used throughout the build and for exhausting to external. Alternative venting designs which enable sufficient environmental containment to be maintained within the WHOLE building (up to exposure limits of 0.1 μg/m3/8hr time weighted average) will be considered. |  | M
3.1 | Safety Operations | In the event of a fire, all door interlocks will open. |  | M
3.2 |  | In the event of an O2 depletion alarm, all door interlocks will open. |  | M
3.3 |  | All doors will have an emergency door release button for the interlocks. |  | M
3.4 |  | All AREAs of the containment room require emergency lighting. |  | M
4.1 | Facilities | The containment room will be integrated into the O2 depletion system and fitted with a sensor and audible/visual alarm. |  | M
4.2 |  | The containment room will be integrated into the fire detection system and fitted with an alarm and sensor. |  | M
4.3 |  | All HEPA filters used in the ventilation will be safe change and sufficient space to ergonomically enable their safe change will be included in the design. |  | M
4.4 |  | A solvent extract connection point is to be extended and capped with a damper ready for future connection. |  | D
4.5 |  | The existing lighting in F0.28.1 will remain, lighting in all other AREAs is required and should be like for like or the same as existing in F0.28.1. |  | M
Installation & Utilities
5.1 | Installation | Scheduling of the work shall be done in collaboration with CPI to minimise disruption to the facility. |  | M
5.2 |  | Completion of the work must be completed by April 2020. |  | M
Software and Connectivity
6.1 | Connectivity | The control of the containment room will be added to the BMS for remote operation and monitoring. |  | M
Regulatory, Support & Warranties
7.1 | CE Marking | The build and all components should be CE marked if requried. |  | M
7.2 | Training | Full training should be provided along with access to technical documents and support |  | M
7.3 | Warranties | Warranty period should cover at least 12 months from installation |  | D
7.4 | Extended warranty | Extended warranty of up to 5 years |  | D
7.5 | Service support | On site support within 24 hours of requesting assistance. Please provide details of expected call-out charges. |  | D
7.6 |  | Details of preventative maintenance programmes required (if any) above Warranty requirements |  | D
OFFICE USE ONLY - This section below this line is for CPI Evaluation and Internal USE only
| Notes for Evaluation Team: |  | Name of Bidder to be inserted here | 1354 | Containment Room Modifications at CPIs Coxon Building
Please assess all of the answers given, with particular attention to the Mandatory answers provided, taking into account, the Desirable and Optional answers too, however, you do not need to score each individual answer, but based on the scoring range 0-5, just give one singluar score (default set at "5" in the red and yellow box below, and as we have to provide feedback to bidders, you must also provide comments on which section(s) above where you felt that they did not meet the requirements.
| Evaluation Panel |  | Name of CPI Evaluator to insert here | dd/mm/yyyy | Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements | 5
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
|  |  | Name of CPI Evaluator to insert here | dd/mm/yyyy | Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements | 5
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
|  |  | Name of CPI Evaluator to insert here | dd/mm/yyyy | Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements | 5
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Head Office: CPI, Wilton Centre, Wilton, Redcar, Cleveland, TS10 4RF, UNITED KINGDOM
Tel: +44 (0)1642 455 340 Email: info@uk-cpi.com Web: www.uk-cpi.com