Call-Off Schedule 20 (Call-Off Specification)

This Schedule sets out the characteristics of the Deliverables that the Supplier will be required to make to the Buyers under this Call-Off Contract

Statement of Requirements

Contract Reference: CCNE24A05

Contract Title: Provision of Cabinet Electrical Maintenance Servicing (CEMS)

Contents

1.	PURPOSE	3

2.	BACKGROUND TO THE CONTRACTING AUTHORITY	3

3.	BACKGROUND TO REQUIREMENT/OVERVIEW OF REQUIREMENT	3

4.	DEFINITIONS	4

5.	SCOPE OF REQUIREMENT	5

6.	THE REQUIREMENT	7

7.	KEY MILESTONES AND DELIVERABLES	12

8.	MANAGEMENT INFORMATION/REPORTING	13

9.	VOLUMES	13

10.	CONTINUOUS IMPROVEMENT	14

11.	SUSTAINABILITY	14

12.	QUALITY	17

13.	PRICE	18

14. STAFF AND CUSTOMER SERVICE	18

15.	SERVICE LEVELS AND PERFORMANCE	19

16.	SECURITY AND CONFIDENTIALITY REQUIREMENTS	20

17.	PAYMENT AND INVOICING	20

18.	CONTRACT MANAGEMENT	21

19.	LOCATION	21

Annex A MOD Supplier Assurance Questionnaire

Annex B MOD Cyber

Annex C MOD SAL

Annex D MOD letter for OS programme

# PURPOSE

  - The Contracting Authority require the undertaking of Cabinet Electrical Maintenance Servicing (CEMS).

  - There are 980 electrical cabinets across the British Forces Cyprus (BFC) / Sovereign Base Areas Administration (SBAA) estate which will require a minimum of two (2) suitably qualified and experienced electricians to conduct electrical maintenance and inspections on electrical cabinets within the eight (8) BFC/SBAA sites, in order to maintain compliance within the Institution of Engineering and Technology (IET) wiring regulation standards which include BS7671 and Joint Service Publication (JSP) 453. The MOD directive for Cabinet Electrical Maintenance Servicing (CEMS) requires inspections to be undertaken by a team of two (2) individuals as a minimum. Please note that the number of electrical cabinets can fluctuate in line with various change programs but it is envisaged never to go above 1100 and over the next 5 years should reduce.

# BACKGROUND TO THE CONTRACTING AUTHORITY

2.1 Contracting Authority: Ministry of Defence, Headquarters British Forces Cyprus (HQ BFC), J6 Branch.

2.2 HQ BFC branch J6 provide Communication Information System (CIS) support to BFC/SBAA and are responsible for the Cabinet Electrical Maintenance Servicing (CEMS) contract.

# BACKGROUND TO REQUIREMENT/OVERVIEW OF REQUIREMENT

3.1 The Contracting Authority has a responsibility to ensure that all electrical cabinets within the BFC/SBAA estate are electrically safe and that the availability of the network is maintained to the highest levels possible.

3.2 CEMS inspections are critical to maintaining a safe and secure environment within the BFC/SBAA estate. There are currently approximately 980 cabinets across the estate. This is not envisaged to grow past 1100, but as infrastructure projects deliver, that number will fluctuate.

3.3 There are approximately 170 Communication Information System (CIS) Cabinets that contain Uninterruptable Power Supply (UPS) systems across the BFC/SBAA estate that require an annual visual inspection and status report produced. The report is to detail any problems and rectification costs. The supplier is to ensure that a method of rectification and payment is achievable within the current contract, but at additional cost to the Authority. If this activity results in an outage, then it is to be coordinated with the Authority. The Authority will instruct the supplier on how to proceed with any UPS related issues.

3.4 CIS Cabinet cooling fan’s preventative maintenance is required in line with the CEMS and UPS schedule and reporting if applicable to that installation. The report is to detail any problems and rectification costs. The supplier is to ensure that a method of rectification and payment is achievable within the current contract, but at additional cost to the Authority. If this activity results in an outage, then it is to be coordinated with the Authority. The Authority will instruct the supplier on how to proceed with any Fan related issues.

# DEFINITIONS

| Expression or Acronym | Definition |
| --- | --- |
| BFC | means British Forces Cyprus |
| CC&S | means Climate Change and Sustainability |
| CEMS | means Cabinet Electrical Maintenance Servicing |
| CIS | means Communication Information System |
| CITR | means Cabinet Installation Test Report |
| CP&F | means Contracting, Purchasing & Finance |
| DIO | means Defence Infrastructure Organisation |
| DDP | means Defence Digital Publication |
| EICR | means Electrical Installation Condition Report |
| HQ BFC | means Headquarters British Forces Cyprus |
| IET | means Institution of Engineering and Technology |
| JSP | means Joint Service Publication |
| KPI | means Key Performance Indicator |
| MEQ | means Model Evaluation Question |
| MOD | means Ministry of Defence |
| P&D | means Pits & Ducts |
| PPN | means Public Procurement Notice |
| RAG | means Red, Amber, Green |
| SBAA | means Sovereign Base Areas Administration |
| SLA | means Service-Level Agreement |
| SuMP | means Sustainability Management Plan |
| SuOR | means Sustainability Operations Report |
| UAD | means User Access Device |
| UPS | means Uninterruptable Power Supply |

# SCOPE OF REQUIREMENT

5.1 	This contract covers Cabinet Electrical Maintenance Servicing (CEMS):

5.1.1 	CEMS: Electrical cabinets must be serviced and inspected in line with UK legislation and relevant governance frameworks (based upon BS7671 & Joint Service Publication 453 with inspections carried out: On commission following installation of a new electrical cabinet, annual visual inspection, and Electrical Installation Condition Report (EICR) conducted every 5 years.

5.1.2 	Limited minor rectification and correctional works are to be carried out for CEMS within the agreed contract (labour only). Costs for materials and consumable will be reimbursed. A list of pre-approved works to be agreed between Authority and Supplier to enable efficient rectification of minor issues. A quote for all materials and consumables outside the pre-approved list must be presented to and approved by the Authority before proceeding with works which have additional costs beyond those which have been pre-approved.

5.1.3 CEMS servicing and inspections must be carried out within the required timelines. See Paragraph 6 for full details of the requirement.

5.1.4 Preventative maintenance regime process for maximum of 175 cabinets which have an internal Uninterruptable Power Supply (UPS) system or external UPS to the cabinet. See Paragraphs 5.2 and 6 for full details of the requirement. When the supplier identifies the requirement for UPS corrective maintenance, the issue and corrective requirements are to be reported to the Authority. Costs for implementing corrective maintenance will be borne by the Authority.

5.1.5 CIS Cabinet cooling fan's inspection and preventative maintenance in line with CEMS and UPS schedule if applicable to that installation. See Paragraphs 5.3 and 6 for full details of the requirement.

5.2 There are a maximum of 175 Communication Information System (CIS) Cabinets that contain Uninterruptable Power Supply (UPS) systems across the BFC/SBAA estate that require a preventative maintenance regime and management process. The Authority require all UPS to be visually checked to ensure operational performance and CIS availability is maintained. The activity where it is reasonably practical should be conducted with the cabinet electrical testing visual inspection regime to minimise downtime for each cabinet installation. Schedule to be agreed by Supplier and Authority.

5.2.1 All defects are to be economically repaired if possible. Example being replacing batteries and not the whole unit and control modules.  The method of fault rectification will be left to the SME to determine and will be based on the overriding requirement noted above to provide a service that maximises operational capability.

5.2.2 Corrective maintenance to be included within the support contract. A call-off allocation will be provided by the Authority which can be drawn against within the funded contract for the purchase of new units, or batteries and ancillaries to support the current fleet.

5.2.3 The supplier is to procure, install, test, and dispose of all component parts of the UPS assembly and sub-assemblies. Providing all through life support within the contracted period. Any disposals should be conducted in line with UK standards.

5.2.4 The contractor is to provide the necessary information to inform the HQ BFC J6 team as to the current status of all UPS within the BFC/SBAA estate and highlight any risks or concerns to CIS equipment. Examples would be:

5.2.4.1 UPS Volts In/Out, Frequency.

5.2.4.2 Battery capacity. Run time B.T: XX minutes (where XX is               the measurement of time that the batteries will support the CIS during a power outage)

5.2.4.3 Current load as % and Amps

5.2.4.4 Alarm status

5.2.4.5 System temperature Celsius

5.2.4.6 Room temperature Celsius

5.2.5 The contractor is to provide monthly status reporting against the UPS preventive maintenance regime to demonstrate Operational availability. This can be provided in a simple RAG chart or similar.

5.2.5.1 Red - Has failed and needs replacement parts.

5.2.5.2 Amber - Due a service or unknown status.

5.2.5.3 Green - Serviced within the last year and Status Ok for output supporting. No Impact.

5.3 	CIS cabinet fans are to have preventative maintenance carried out.

5.3.1 	Removal of filters and cleaned.

5.3.2 	Removal of debris and dust removed from the units.

5.3.3 If specified by the equipment manufacturer, lubricant is to be applied to ensure longevity. Manufacturer maintenance guidance will be provided by the Authority when required.

5.3.4 Any defects and faults that cannot be repaired are to be reported to the HQ BFC J6 contract manager. Costs for materials and consumables will be reimbursed. A quote for all materials and consumables must be presented to and approved by the Authority before proceeding with works which have additional costs.

# THE REQUIREMENT

6.1 	Contract covers Cabinet Electrical Maintenance Servicing (CEMS).

6.1.1 CEMS servicing requirements. CEMS servicing and inspections must adhere to the requirements below.

6.1.1.1 Inspection Regime:

- Maintain currency with UK legislation and relevant governance frameworks to plan & execute appropriate inspection regimes.

- UK legislation and governance framework (based upon BS7671 & Joint Service Publication 453) takes precedence but as a guide, inspections will be carried out: on commission following installation of a new electrical cabinet, annual visual inspection, and Electrical Installation Condition Report (EICR) conducted every 5 years.

- All UPS are to be inspected each year and the status reported to the Authority.

- CIS Cabinet cooling fan’s inspection and preventative maintenance to be carried out in line with CEMS and UPS schedule if applicable to that installation.

6.1.1.2 Boundary/Limits of Responsibility:

- In terms of electrical testing the responsibility of the supplier will be everything upline of the Defence Infrastructure Organisation (DIO) demarcation point. Figure 1 below provides the visual understanding of that specific point.

Figure 1

6.1.1.3 Scheduling:

- Yearly schedules of inspections to be produced by the Supplier as part of the tender submission and on an annual basis thereafter. Supplier to work with Authority to agree exact format.

- Production of a monthly report which is to detail: actions carried out in line with the agreed inspection and maintenance schedule, issues, risks, and recommendations for rectification and follow up work. The report must provide statistics on Cabinet testing detailing: the amount that have; Passed, Failed and the type of failures summaries as per the codes (C1, C2, C3 & FI as per CITR form and BS).  Monthly report to also include monthly schedules and progress reports. Exact format to be agreed with Authority. Further: Copies of certification to be retained by contractor and electronically provided to the Authority.

- The Supplier is to agree outages that the Authority has arranged on per occasion basis using the Authority owned Planned Outage procedures.

- The Authority retains the ability to amend schedules at short notice to respond to MOD priorities. The Authority accepts short notice changes to the schedule could incur a cost related to additional resource needed to recover the planned schedule if it cannot be covered within the usual resource.

      - Remedial Action:

- Provide recommendations for remedial action following CEMS inspections.

- Supplier is to align with BFC/SBAA standard operating procedures (provided as attachment on a case-by-case basis) to provide the information required to enable the Authority to raise works requests and associated documentation (statement of requirements, statement of needs).

- Carry out low-level rectification works detailed below within resource and skillset (labour only, bill for spares and consumables to be raised separately):

- Earth bonding.

- Power Distribution Unit (PDU) replacement.

- Power cable replacement up to the DIO junction of maintenance detailed in Figure 1 if the wrong size is present.

- Carry out UPS battery replacements as required to ensure UPS units function correctly. The Supplier to provide a costed option for battery replacement as necessary for consideration by the Authority. A current status assessment can be provided by the Authority.

- Cabinet fan cooling units. Replace units that cannot be repaired. Funded outside of the contract by the Authority. Installation of fan replacement is to be delivered within the contract. Supplier to provide replacement part item code details for procurement by the Authority.

      - Configuration Management:

- First-hand data capture of all Change Management information relating to BFC/SBAA Cabinet Electrical Maintenance Servicing infrastructure. Supplier and Authority to agree format.

- Maintenance of the master-spreadsheet, to be hosted on MODNet. Register to be updated with all completed certification on a weekly basis. This must include Cabinet, UPS, and Fan status. Supplier will be provided with access to a MODNet UAD, accounts and the master-spreadsheet for the period of this contract.

- Supplier must update Master spreadsheet with cabinet status within 5 working days following inspections.

- EICR certificates to be attached to cabinets in a suitably prominent position following inspection/testing. Approved MOD CITR documentation to be used. Supplier must provide electronic copies of EICR certificates to the Authority within 5 working days post certification.

      - Enabling:

- The supplier must be self-sufficient in terms of enabling tasks, to include but not limited to:

- Access to appropriate vehicle and equipment to carry out the contract. This will not be supplied by The Authority.

- Supplier’s management Chain to respond to enquiries and comment from The Authority related to tasks completed, planned or to be scheduled.

      - Other Tasks:

- Supplier must have the ability to carry out additional tasks within the scope of the contract, to include but not limited to:

- Fault finding and minor rectification works.

- Collaborating with the BFC/SBAA managed services provider to restore services.

- Low level modifications to ensure CIS availability is restored and maintained.

- Management of outages in accordance with MOD procedures and direction, inclusive of DDP 153 and BFC Planned Outage process.

      - Cabinet Onboarding:

- Supplier must add new cabinets to the CEMS schedule when required. All new cabinets will be initially tested by the project delivery team and will come with initial EICR certificate.

# KEY MILESTONES AND DELIVERABLES

7.1 	The following Contract milestones/deliverables shall apply:

| Milestone/Deliverable | Description | Timeframe or Delivery Date |
| --- | --- | --- |
| 1 | Current CEMS contract expires 31 March 2025. New contract must be in place by 31 March 2025 so that inspections can begin on 01 April 2025 | TBC – Delivery date to be mutually agreed with the supplier, this date must be by 31 March 2025 |
| 2 | Supplier shall provide a Cabinet and UPS maintenance schedule for 12 months ahead. | Within 30 days of contract start date and annual renewal for subsequent years |
| 3 | Quarterly KPI review status or: UPS CEMS Fans. | Initial review within 30 days of contract start date then quarterly afterwards |
| 4 | Supplier shall undertake inspections and maintenance in line with agreed schedule and provide monthly reports on status, actions carried out, issues, risks and recommendations for rectification and follow up work. | First report within 30 days of contract start date then monthly thereafter to HQ BFC J6 |
| 5 | Supplier shall update Master spreadsheet with cabinet status following inspections. | Within 5 working days of completion of an inspection |
| 6 | Supplier shall provide electronic copies of EICR certificates to the Authority | Within 5 working days of completion of an inspection |
| 7 | EICR. Certificates to be attached to cabinets following inspections. Approved MOD CITR documentation to be used. | Within 5 working days of completion of an inspection |
| 8 | Supplier shall provide Exit Plan. | Within 90 days of contract start date |

# MANAGEMENT INFORMATION/REPORTING

8.1 CEMS: Production of a monthly report which is to detail: actions carried out in line with the agreed inspection and maintenance schedule, issues, risks, and recommendations for rectification and follow up work. The report must provide statistics on Cabinet testing detailing: the amount that have; Passed, Failed and the type of failures summaries as per the codes (C1, C2, C3 & FI as per CITR form and BS).  Monthly report to also include monthly schedules and progress reports. Exact format to be agreed with Authority. Further: Copies of certification to be retained by contractor and electronically provided to the Authority.

# VOLUMES

9.1 CEMS: There are currently approximately 980 electrical cabinets across the seven sites within the BFC/SBAA estate and the maximum number of electrical cabinets to be inspected within the contract will not exceed 1100. There are currently approximately 170 cabinet UPS systems within the BFC/SBAA estate and the maximum number to be inspected within the contract will not exceed 175. Servicing/inspection schedule is:

a. On commission of a new CIS cabinet installation.

b. Annual visual inspection.

c. EICR conducted every 5 years.

d. Circa 92 cabinet inspections to be carried out per calendar month. Schedule to be agreed by Supplier and Authority.

e. All UPS are to be inspected each year and the status reported to the Authority. Circa 15 UPS preventative inspections to be carried out per calendar month. Schedule to be agreed by Supplier and Authority.

f. CIS Cabinet cooling fan’s inspection and preventative maintenance to be carried out in line with CEMS and UPS schedule if applicable to that installation.

# CONTINUOUS IMPROVEMENT

10.1 The Supplier will be expected to continually improve the way in which the required Services are to be delivered throughout the Contract duration.

10.2 The Supplier should present new ways of working and suggestions for continuous improvement to the Authority during quarterly Contract review meetings. More regular contract review meetings may be required at certain periods.

10.3 Changes to the way in which the Services are to be delivered must be brought to the Authority’s attention and agreed prior to any changes being implemented.

# SUSTAINABILITY

11.1 The supplier shall provide an outline Sustainability Management Plan (SuMP). The SuMP will outline any project-specific expected sustainability risks and opportunities and address management and improvement where applicable over the life of the contract.

11.2 The supplier shall also provide a Sustainability Operations Report (SuOR). As a minimum, project-specific environmental, social & economic objectives and commitments should be outlined within the SuOR. It must also report on what Climate Change and Sustainability (CC&S) risks and opportunities have been identified and managed throughout the lifecycle of the contract.

11.3 Details of what is required and when are contained in the call-off contract’s terms and conditions.

11.4 As required by PPN06/20 government commercial activities should deliver Social Value aligning with the government’s priorities, as a result elements of social value shall be included as part of this contract. The supplier shall provide responses against the following two (2) Model Evaluation Questions (MEQ):

| Theme | Policy Outcome |  | Weighting |  |  | (As percentage of Social Value): | 10% Out of 10% |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1. Tackling Economic Inequality | Increase supply chain resilience and capacity |  | MAC | 3.5 | Manage Cyber Security Risks |  |  |
|  |  | Model Evaluation Question (MEQ) | Using a maximum of 4 sides of A4 describe the commitment your organisation will make to ensure that opportunities under the contract deliver the Policy Outcome and Award Criteria. Please include: ● your ‘Method Statement’, stating how you will achieve this and how your commitment meets the Award Criteria, and ● a timed project plan and process, including how you will implement your commitment and by when. Also, how you will monitor, measure and report on your commitments/the impact of your proposals. You should include but not be limited to: ○ timed action plan ○ use of metrics ○ tools/processes used to gather data ○ reporting ○ feedback and improvement ○ transparency ● how you will influence staff, suppliers, customers and communities through the delivery of the contract to support the Policy Outcome, e.g. engagement, co-design/creation, training and education, partnering/collaborating, volunteering. |  |  |  |  |
|  |  | Sub-Criteria for MAC 3.5: | Manage Cyber Security Risks. |  |  |  |  |
|  |  | Model Response Guidance: | Activities that demonstrate and describe the tenderer’s existing or planned: ● Understanding of risks affecting the contract, including those affecting the market, industry, sector and country (of origin or of source), and to identify the risks and ways of mitigating and managing them. ● Measures to mitigate and manage cyber security risks within the supply chain relating to the contract, including: ○ engaging with the supply chain to identify and build resilience against cyber security risks ○ actions to be taken to actively raise cyber security awareness. ● Commitment to adopting the required technical standards and best practice as a basis for appropriate cyber security controls (appropriate to the contract and risk profile), such as: ○ the ‘10 Steps To Cyber Security’ advocated by the National Cyber Security Centre for establishing a cyber risk management regime. ○ more stringent cyber security measures in the supply chain where necessary, such as Cyber Essentials and Cyber Essentials Plus certification, and having a specific cyber insurance policy for the contract. ○ NCSC Cloud Security Guidance ○ NCSC 14 Cloud Security Principles ○ Technology Code of Practice |  |  |  |  |
|  |  | Tenderer’s Response: | In compiling your answer, please refer to the Social Value Model Quick Reference Table, under Model Response Guidance for tenderers and evaluators for examples of types of evidence the tender evaluators are looking for: |  |  |  |  |
|  |  |  | Please upload your response in line with guidance provided by the Authority |  |  |  |  |

# QUALITY

12.1 CEMS: Servicing and Inspections must be carried out in compliance with guidelines and regulations identified in Paragraph 6 THE REQUIREMENT. The monthly report requested in Paragraph 8 MANAGEMENT INFORMATION/REPORTING must detail compliance with the requirements for this contract.

# PRICE

13.1 Prices are to be submitted as per guidance supplied by Crown Commercial Services.

13.2 A monthly payment schedule will apply to this contract. This will comprise of an agreed fixed monthly cost plus any additional charges which have been approved by the Authority before commencement of works and/or procurement.

13.3 All bills must be itemised and submitted to the Authority for scrutiny and sign-off before payment will be made.

# 14. STAFF AND CUSTOMER SERVICE

14.1 The Supplier shall provide a sufficient level of resource throughout the duration of the Contract in order to consistently deliver a quality service.

14.2 The Supplier is to ensure all staff have the relevant qualifications and experience required to deliver the Contract in line with the stated requirements in this document.

14.3   Individuals undertaking work within the cabinets must hold a valid security clearance at minimum level: Security Check (SC). Any Third-party suppliers must be escorted by the supplier, whose escorting staff must have as a minimum: valid SC clearance.

14.4 CEMS requirements:

- Working Knowledge of electrical maintenance regulations including BS7671 and Joint Service Publication 453.

- Professionally qualified to UK Electrical Wiring Regulation Standards.

- Working knowledge of Microsoft Office including O365, Excel and SharePoint.

- Understanding of Risk and ability to apply Risk Management (as per Joint Service Publication 892).

- Full UK Driving Licence (B) or equivalent within Cyprus.

- Ability to work alone and unsupervised or as part of a team.

- Awareness of Health & Safety Issues.

- Ability to manage own workload and prioritise where necessary.

- Ability to carry out low-level management tasks (for example, escorting and coordinating with MOD and other third parties).

# SERVICE LEVELS AND PERFORMANCE

15.1 The Authority will measure the quality of the Supplier’s delivery by:

| KPI/SLA | Service Area | KPI/SLA description | Target |
| --- | --- | --- | --- |
| 1 | EICR | All electrical cabinets within the estate to be inspected and all maintain valid EICR dates. Ensure inspection codes and rules are adhered to wrt timelines and actions are followed as per BS7671. | 99% |
| 2 | Inspections | Supplier must conduct cabinet visual inspections on each in scope cabinet (up to 1100) every 12 months. All UPS (up to 175) are to be inspected each year and the status reported to the Authority. The Supplier must undertake annual inspection and preventative maintenance of all cabinet fans where applicable to an installation. | 99% |
| 3 | Electrical testing | Supplier must conduct cabinet electrical testing on each in scope cabinet every 5 years. | 99% |
| 4 | Preventative Maintenance | Supplier must provide a Cabinet inspection and UPS preventive maintenance schedule for 12 months ahead. This is to be annotated in a master spreadsheet. Target percentages relates to the totality of all cabinets and UPS within that schedule. | 95% |
| 5 | EICR certificates | Supplier is to ensure EICR certificates are attached to cabinets within 5 working days of completing inspection. | 99% |
| 6 | UPS KPI | The Supplier is to conduct a survey of UPS faults within 2 working days of notification from the Authority. | 95% |
| 7 | UPS KPI | The Supplier is to provide Costed options to the Authority within 3 working days of UPS fault notification. | 95% |
| 8 | Social Value KPI | Supplier is to provide annual evidence of adherence to effective cyber security controls as well as evidence of relevant cyber certification | 99% |

# SECURITY AND CONFIDENTIALITY REQUIREMENTS

16.1 Individuals who work on this contract must sign a confidentiality agreement and adhere to the Official Secrets Act.

16.2 Individuals undertaking work within the cabinets must hold a valid security clearance at minimum level: Security Check (SC). Any Third-party suppliers must be escorted by the supplier, whose escorting staff must have as a minimum: valid SC clearance.

# PAYMENT AND INVOICING

17.1 Invoices to be submitted through the MOD Contracting, Purchasing & Finance (CP&F) system to an agreed monthly schedule. Access to CP&F payment system will be provided to the supplier. Monthly invoice dates to be agreed by supplier and Authority.

17.2 Payment can only be made following satisfactory delivery of SLAs and KPIs unless prior agreement has been sought from the Authority. Payment will be made after Authority verification and sign-off. Out of scope activities such as UPS corrective maintenance will be paid on completion of the work and correct invoicing no later than 30 days from the date on which the Authority has determined that the invoice is valid.

17.3 Before payment can be considered, each invoice must include a detailed elemental breakdown of work completed and the associated costs.

17.4 Invoices should be submitted to: British Forces Cyprus through the CP&F payment system. Access to the CP&F payment system will be provided to the supplier to enable invoice upload. Invoices will be paid no later than 30 days from the date on which the Authority has determined that the invoice is valid.

17.5 Supplier must obtain a MOD CP&F account to enable payment. The Authority will provide guidance on how to obtain a CP&F account.

# CONTRACT MANAGEMENT

18.1 CEMS: Contract to be managed by the supplier to ensure all requirements within this document are met. Management reviews will be via production of a monthly report and contract review meetings.

18.2 Production of a monthly report which is to detail the actions carried out, issues, risks and recommendations for rectification/follow up work. To also include schedules and progress report. Exact format to be agreed with Authority.

18.3 CEMS: Copies of certification to be retained by contractor and electronically provided to the Authority.

18.4 Attendance at Contract Review meetings shall be at the Supplier’s own expense. Either on-line or in person to be agreed on a case-by-case basis.

# LOCATION

19 The location of the Services will be carried out at eight (8) sites within the BFC estate:

- Episkopi Garrison

- RAF Akrotiri including Salt Lake.

- Dhekelia Garrison

- Nicosia - British High Commission

- Ayios Nikolaos

- Mt Troodos

- Mt Olympus

- Limassol Port