## Price Schedule
Pricing Schedule - Refurbishment Works at John Moulton Hall Community Centre
|  | £ |  | £
PRELIMINARIES |  |  | £
1.1 | Site Management: Allow for all necessary site management including a designated site foreman.
1.2 | Health and Safety: Provide written risk assessments before commencing any work. Allow for carrying out all the work in accordance with current health and safety regulations.
1.3 | Fencing and access: Form a secure construction site area with temporary fencing to prevent unauthorised access to the site including building, footpaths and car parking area to rear of the building during the carrying out of the works. Clear away all temporary fencing on completion of the works. Allow for maintaining access to the building during the carrying out of the works.
1.4 | Signage: Allow for all site health and safety signage for both the public and the workforce to be in accordance with current health & safety regulations.
1.5 | Goods & Materials: Allow for all goods and materials to be supplied new in accordance with the contract specification and drawings or equal approved, in good condition and only brought to site as and when needed. Allow for protection and security of all goods and materials until the completion of the works.
1.6 | Workmanship: Allow for all workmanship to be in accordance with the contract specification and drawings and to approved construction industry standards and codes of practice.
1.7 | Plant, tools and equipment: Allow for all neccesary small plant, tools and equipment for the carrying out of the works including arranging for power as required. Note the community centre may be used for power provision during the carrying out of the works.
1.8 | Welfare facilities: Allow for all necessary temporary welfare facilities to be in accordance with current health and safety regulations including arranging for power, water and sanitation as required. Note the community centre may be used for welfare provision during the carrying out of the works.
1.9 | Waste and Cleaning: Allow for removing all waste from site to approved tips as the work proceeds including the use of covered skips as required. Leave the site clean and tidy on completion of the works.
1.10 | Insurances: Allow for public and employers liability insurances to the levels of imdemnity as required.
FOYER / ENTRANCE HALL |  |  | £
2.1 | Suspended Ceiling: Provide and install new suspended ceiling system comprising fine fissured 600 x 600mm mineral fibre square edged ceiling tiles within a white T24mm exposed grid with standard perimeter trim to walls in position 2.4m above existing floor level (note: existing ceiling height is 3.5m) as agreed on site prior to commencement of works. Allow for formimg sloping bulkhead to front entrance windows and boxing to roof access panel.
2.2 | Floor Covering: Remove existing vinyl floor coverings and make make good sub-floor. Provide and lay latex screed ready to receive new coverings. Provide and lay new Altro Walkway 20 or similar approved vinyl safety flooring fixed with low emmision adhesive all in accordance with manufacturer's recommendations. Heat weld all joins. Allow for formimg thresholds and abutments to skirtings and for all necessary cutting and fitting around obstructions.
2.3 | Redecoration: Prepare and redecorate existing walls with 2coats matt emulsion paint. Prepare and redecorate existing timber surfaces with 2coats white gloss paint.
CORRIDOR |  |  | £
3.1 | Suspended Ceiling: Provide and install new suspended ceiling system comprising fine fissured 600 x 600mm mineral fibre square edged ceiling tiles within a white T24mm exposed grid with standard perimeter trim to walls in position 2.4m above existing floor level (note: existing ceiling height is 3.5m) as agreed on site prior to commencement of works.
3.2 | Floor Covering: Remove existing vinyl floor coverings and make make good sub-floor. Provide and lay latex screed ready to receive new coverings. Provide and lay new Altro Walkway 20 or similar approved vinyl safety flooring fixed with low emmision adhesive all in accordance with manufacturer's recommendations. Heat weld all joins. Allow for formimg thresholds and abutments to skirtings and for all necessary cutting and fitting around obstructions.
3.3 | Corridor Doors: Remove existing double action doors and frames complete and make good. Provide and fit new 30 minute fire resistant softwood frame to fit existing opening with appropriate intumescent/smoke seals within the frame ito comply with current fire regulations. Provide and fix 2nr new 30 minute fire resistant 50mm thick solid timber core double action fire doors to match existing sizes with rectangular fire resistant glazed vision panel in each leaf together with anti-finger trap joint and appropriate intumescent/smoke seals to comply with current fire regulations. Allow for servicing and repairing existing double action floor spring door closers as required to comply with current fire regulations. Provide and fit satin anodised aluminium 300 x 75mm push and 800 x 150mm kick plates fixed with screws to both sides of each door leaf. Prepare and decorate new fire doors and frames with 1coat primer, 1 undercoat and 2coats white gloss paint.
3.4 | Kitchen Door: Remove existing door and frame and make good. Provide and fit new 30 minute fire resistant door and frame to fit existing opening complete with appropriate intumescent/smoke seals within the frame and door as required to comply with current fire regulations. Provide and fit door latch with deadlock together with satin anodised aluminium door handles. Prepare and decorate new fire door and frames with 1coat primer, 1 undercoat and 2coats white gloss paint.
3.5 | Electrical Cupboard Door: Remove existing door and frame and make good. Provide and fit new 30 minute fire resistant door and frame to fit existing opening complete with appropriate intumescent/smoke seals within the frame and door as required to comply with current fire regulations. Provide and fit door latch with deadlock together with satin anodised aluminium door handles. Prepare and decorate new fire door and frames with 1coat primer, 1 undercoat and 2coats white gloss paint.
3.6 | Redecoration: Prepare and redecorate existing walls with 2coats matt emulsion paint. Prepare and redecorate existing timber surfaces with 2coats white gloss paint.
LINK ROOM / KITCHENETTE |  |  | £
4.1 | Kitchens Units: Remove existing kitchen units including sink and fittings. Provide and fit new stainless steel sink with monoblock tap and wastes and plumbing.
4.2 | Provisional Sum: Allow a provisional sum of £500 for provision and installation of additional kitchen units and worktop. | 500
4.3 | Safe Cupboard: Remove existing heavy duty safe cupboard within link room / kitchenette and dispose of to an approved tip off site and make good.
4.4 | Suspended Ceiling: Provide and install new suspended ceiling system comprising fine fissured 600 x 600mm mineral fibre square edged ceiling tiles within a white T24mm exposed grid with standard perimeter trim to walls in position 2.4m above existing floor level (note: existing ceiling height is 3.5m) as agreed on site prior to commencement of works.
4.5 | Floor Covering: Remove existing vinyl floor coverings and make make good sub-floor. Provide and lay latex screed ready to receive new coverings. Provide and lay new Altro Walkway 20 or similar approved vinyl safety flooring fixed with low emmision adhesive all in accordance with manufacturer's recommendations. Heat weld all joins. Allow for formimg thresholds and abutments and for all necessary cutting and fitting around obstructions.
4.6 | Redecoration: Prepare and redecorate existing walls with 2coats matt emulsion paint. Prepare and redecorate existing timber surfaces with 2coats white gloss paint.
LEARNING CENTRE |  |  | £
5.1 | Existing Stud Partitioning and Doors: Remove all existing plasterboard and timber stud partitioning complete with doors and make good ceiling and wall and floor surfaces.
5.2 | Suspended Ceiling: Provide and install new suspended ceiling system comprising fine fissured 600 x 600mm mineral fibre square edged ceiling tiles within a white T24mm exposed grid with standard perimeter trim to walls in position as high as possible above windows as agreed on site prior to commencement of works. Allow for trimming and boxing aound windows as required.
5.3 | Floor Covering: Remove existing carpet tile floor coverings and make make good sub-floor ready to receive new coverings. Provide and lay new carpet tile floor coverings all in accordance with manufacturer's instructions. Allow for formimg thresholds and abutments to skirtings and for all necessary cutting and fitting around obstructions.
5.4 | Redecoration: Prepare and redecorate existing walls with 2coats matt emulsion paint. Prepare and redecorate existing timber surfaces with 2coats white gloss paint.
MAIN HALL |  |  | £
6.1 | Main Hall Doors: Remove existing double action doors and frames complete and make good. Provide and fit new 30 minute fire resistant softwood frame to fit existing opening with appropriate intumescent/smoke seals within the frame ito comply with current fire regulations. Provide and fix 2nr new 30 minute fire resistant 50mm thick solid timber core double action fire doors to match existing sizes with rectangular fire resistant glazed vision panel in each leaf together with anti-finger trap joint and appropriate intumescent/smoke seals to comply with current fire regulations. Allow for servicing and repairing existing double action floor spring door closers as required to comply with current fire regulations. Provide and fit satin anodised aluminium 300 x 75mm push and 800 x 150mm kick plates fixed with screws to both sides of each door leaf. Prepare and decorate new fire doors and frames with 1coat primer, 1 undercoat and 2coats white gloss paint.
6.2 | Floor Covering: Inspect and repair all loose and damaged wood block flooring as necessary. Ensure all wood blocks are solidly fixed and all staples, nails and the like are removed from the floor. Sand wood blocks at a 45 degree angle to the grain using a 40 grit floor sanding belt and specialist multi directional sanding equipment to level the floor and remove any deep scratches followed by a 60 grit sanding belt. Ensure all passes are perpendicular to each other. Sand and level room edges with a 40 grit sanding disk followed by a 60 grit sanding disk. Prepare and fill any gaps between wood blocks with epoxy resin and dust from 60 grit sanding process mixed into a wood paste. Allow wood filler to conpletely dry. Sand wood blocks at a 45 degree angle to the grain using a 100 grit floor sanding belt to remove all wood filler residue. Ensure final pass is perpendicular to previous pass. Sand room edges with a 100 grit sandind disk and all corners with a corner sander and triangle detail sander. Buff wood blocks with a 120 grit sanding screed disk to ensure removal of any scratches. Vacuum clean the floor followed by a slightly damp micro fibre mop to remove all dust. Apply 1coat prime coat followed by 2coats hard wearing commercial quality water based wood floor lacquer using a short pile roller. Ensure each coat is completely dry and buff wood blocks with a 150 grit sanding screed disk and vaccum clean thoroughly between each coat. Protect from foot traffic and allow the lacqer to cure for 3 days.
6.3 | Redecoration: Prepare and redecorate existing walls with 2coats matt emulsion paint. Prepare and redecorate existing timber surfaces with 2coats white gloss paint.
GENTS TOILET |  |  | £
7.1 | WC Pans: Remove 2no. existing ceramic WC pans with high level cisterns complete. Provide and install into existing positions 2no. white close-coupled ceramic WC suites complete with plastic WC seat and all fittings and connect to existing services.
7.2 | Urinals: Deep clean 2nr existing ceramic urinal bowls slab using non abrasive approved propriatory cleaner and extra-strength disinfectant . Allow for testing appliances and reporting findings.
7.3 | Wash Hand Basins: Deep clean 2nr existing ceramic wash hand basins using non abrasive approved propriatory cleaner and extra-strength disinfectant . Allow for testing appliances and reporting findings.
7.4 | Cubicle Doors: Prepare & redecorate 2no. existing timber flush faced toilet cubicle doors and door frames on both sides with 2coats blue gloss external quality paint.
7.5 | Wall Tiling: Deep clean all existing wall and cubicle partition ceramic wall tiles and grouting with an approved proprietary non-abrasive hydrogen peroxide based stain remover or similar. Wash down all walls with approved disinfectant and then clean water. Wipe dry all surfaces on completion.
7.6 | Provisional Sum: Allow a provisional sum of £500 for wall tiling repairs to all toilets | 500
7.7 | Floor Covering: Remove existing vinyl floor coverings and make make good sub-floor. Provide and lay latex screed ready to receive new coverings. Provide and lay new Altro Walkway 20 or similar approved vinyl safety flooring fixed with low emmision adhesive all in accordance with manufacturer's recommendations. Heat weld all joins. Allow for formimg thresholds and coved abutments and for all necessary cutting and fitting around obstructions.
7.8 | Redecoration: Prepare and redecorate ceilings including skylight voids and duct covers with 2coats matt emulsion paint.
LADIES TOILET |  |  | £
8.1 | WC Pans: Deep clean 2nr existing ceramic WC pans using non abrasive approved propriatory cleaner and extra-strength disinfectant . Allow for testing appliances and reporting findings.
8.2 | Wash Hand Basins: Deep clean 2nr existing ceramic wash hand basins using non abrasive approved propriatory cleaner and extra-strength disinfectant . Allow for testing appliances and reporting findings.
8.3 | Cubicle Doors: Prepare & redecorate 2no. existing timber flush faced toilet cubicle doors and door frames on both sides with 2coats blue gloss external quality paint.
8.4 | Wall Tiling: Deep clean all existing wall and cubicle partition ceramic wall tiles and grouting with an approved proprietary non-abrasive hydrogen peroxide based stain remover or similar. Wash down all walls with approved disinfectant and then clean water. Wipe dry all surfaces on completion.
8.5 | Floor Covering: Remove existing vinyl floor coverings and make make good sub-floor. Provide and lay latex screed ready to receive new coverings. Provide and lay new Altro Walkway 20 or similar approved vinyl safety flooring fixed with low emmision adhesive all in accordance with manufacturer's recommendations. Heat weld all joins. Allow for formimg thresholds and coved abutments and for all necessary cutting and fitting around obstructions.
8.6 | Redecoration: Prepare and redecorate ceilings including skylight voids and duct covers with 2coats matt emulsion paint.
DISABLED TOILET |  |  | £
9.1 | WC Pan: Deep clean 2nr existing ceramic WC pans using non abrasive approved propriatory cleaner and extra-strength disinfectant . Allow for testing appliances and reporting findings.
9.2 | Wash Hand Basin: Deep clean 1nr existing ceramic wash hand basin using non abrasive approved propriatory cleaner and extra-strength disinfectant . Allow for testing appliances and reporting findings.
9.3 | Wall Tiling: Deep clean all existing wall and cubicle partition ceramic wall tiles and grouting with an approved proprietary non-abrasive hydrogen peroxide based stain remover or similar. Wash down all walls with approved disinfectant and then clean water. Wipe dry all surfaces on completion.
9.4 | Floor Covering: Remove existing vinyl floor coverings and make make good sub-floor. Provide and lay latex screed ready to receive new coverings. Provide and lay new Altro Walkway 20 or similar approved vinyl safety flooring fixed with low emmision adhesive all in accordance with manufacturer's recommendations. Heat weld all joins. Allow for formimg thresholds and coved abutments and for all necessary cutting and fitting around obstructions.
9.5 | Redecoration: Prepare and redecorate ceilings including skylight voids and duct covers with 2coats matt emulsion paint.
ELECTRICAL INSTALLATIONS - APPENDIX E |  |  | £
10.1 | Foyer / Entrance Hall Lighting: Remove all existing redundant light fittings and electrics from existing ceiling. Allow for facilitating the installation of the new suspended ceiling. Provide and install new recessed 600 x 600mm 4000K maximum 38Watt consumption 3200Lumens non-dimmable LED flat panel light fittings with 3 hour emergency pack into new suspended ceiling grid in positions shown on drawings. Allow for relocating and lowering all existing PIR presence and motion detectors to below new suspended ceiling. Allow for all new wiring and wooden pattresses as required.
10.2 | Corridor Lighting: Remove all existing redundant light fittings and electrics from existing ceiling. Allow for facilitating the installation of the new suspended ceiling. Provide and install new recessed 600 x 600mm 4000K maximum 38Watt consumption 3200Lumens non-dimmable LED flat panel light fittings with 3 hour emergency pack into new suspended ceiling grid in positions shown on drawings. Allow for relocating and lowering all existing PIR presence and motion detectors to below new suspended ceiling. Allow for all new wiring and wooden pattresses as required.
10.3 | Link Room / Kitchenette Lighting: Remove all existing redundant light fittings and electrics from existing ceiling. Allow for facilitating the installation of the new suspended ceiling. Provide and install new recessed 600 x 600mm 4000K maximum 38Watt consumption 3200Lumens non-dimmable LED flat panel light fittings with 3 hour emergency pack into new suspended ceiling grid in positions shown on drawings. Allow for relocating and lowering all existing PIR presence and motion detectors to below new suspended ceiling. Allow for all new wiring and wooden pattresses as required.
10.4 | Learning Centre Lighting: Remove all existing redundant light fittings and electrics from existing ceiling. Allow for facilitating the installation of the new suspended ceiling. Provide and install new recessed 600 x 600mm 4000K maximum 38Watt consumption 3200Lumens non-dimmable LED flat panel light fittings with 3 hour emergency pack into new suspended ceiling grid in positions shown on drawings. Allow for relocating and lowering all existing PIR presence and motion detectors to below new suspended ceiling. Allow for all new wiring and wooden pattresses as required.
10.5 | Main Hall Lighting: Remove all existing light fittings. Provide and install new 1800mm long 4000K maximum 60Watt consumption 6000 Lumens linear twin lamp non-dimmable LED batten light fittings in positions shown on drawings. Provide and install ceiling mounted emergency bulkhead light fittings in positions shown on drawings. Allow for new lighting suspension system to the height required. Allow for new wiring and cabling as required.
10.6 | Library Lighting: Remove all existing light fittings. Provide and install new 1800mm long 4000K maximum 60Watt consumption 6000 Lumens linear twin lamp non-dimmable LED batten light fittings in positions shown on drawings. Provide and install ceiling mounted emergency bulkhead light fittings in positions shown on drawings. Allow for new lighting suspension system to the height required. Allow for new wiring and cabling as required.
10.7 | Gents Toilet Lighting: Existing light fittings to remain
10.8 | Ladies Toilet Lighting: Existing light fittings to remain
10.9 | Disabled Toilet Lighting: Existing light fittings to remain
10.10 | Fire Alarm: Allow for facilitating the installation of the new suspended ceiling. Allow for relocating and lowering existing fire alarm and smoke and heat detectors to below all new suspended ceilings in positions shown on drawings. Allow for connecting existing IO unit to the Building Management System (BMS) control panel in the boiler room. Allow for all new wiring and wooden pattresses as required.
10.11 | Security Alarm: Allow for facilitating the installation of the new suspended ceiling. Allow for relocating and lowering all existing security alarm detectors to below all new suspended ceilings in positions shown on drawings. Allow for all new wiring and wooden pattresses as required.
10.12 | Disabled Toilet Alarm: Allow for facilitating the installation of the new suspended ceiling. Allow for relocating and lowering existing Disabled Toilet alam beacon and sounder to below new suspended ceiling in position shown on drawings. Allow for all new wiring and wooden pattresses as required.
10.13 | CCTV: Allow for facilitating the installation of the new suspended ceiling. Allow for relocating and lowering all existing CCTV cameras to below all new suspended ceilings in positions shown on drawings. Allow for all new wiring and wooden pattresses as required.
10.14 | Wi-Fi & Data: Allow for facilitating the installation of the new suspended ceiling. Allow for relocating and lowering existing Wi-Fi router to below new suspended ceiling in position shown on drawings. Allow for all new wiring and wooden pattresses as required.
10.15 | Mechanical Wiring: Allow for electrical connections from all new heat emitters and room thermostats to power supplies.
10.16 | Small Power: Isolate and remove all redundant electric fittings and wiring and cabling from within existing stud partition in the Learning Centre. Allow for facilitating the installation of all new suspended ceilings. Provide and install new 13A spur switched fused connection at high level for Foyer/Main Entrance and Main Hall heat emitters in positions shown on drawings. Provide and install new double sockets at low level in Link Room / Kitchenette and Office in positions shown on drawings. Allow for relocating all existing power supplies into all new suspended ceilings. Allow for all new wiring and containment as required.
10.17 | Containment & Dado Trunking: Provide and install all new containment and PVCu dado trunking to positions shown on drawings as required to complete the installation of all new and relocated services.
10.18 | Testing & Commissioning: Carry out all necessary labelling and testing and certification to comply fully with NIC EIC BS7671.
10.19 | Documentation: Provide and hand to employer 2nr Hard Copies and 1nr Electronic Pdf Copy of all necessary Health and Safety (H&S) and Operation and Maintenance (O&M) Manuals together with 'As Installed' Drawings in AutoCAD 2011 format
MECHANICAL INSTALLATIONS - APPENDIX F |  |  | £
11.1 | Existing Boiler & Controls: Existing gas fired boiler and pressurisation unit and expansion vessel is to remain. Allow for alterations to existing heating system to suit new heating syatem. Allow for visual inspection of all boiler plant and controls with a full heating demonstration of all plant and controls on completion. Report any findings and recommendations for bringing existing boiler system up to current regulations as work progresses.
11.2 | Provisional Sum: Allow a £500 provisional sum for carrying out any recommended work to existing boiler & controls. | 500
11.3 | Existing Heat Emitters: Drain down and remove all existing heat emitters. Set aside existing cast iron radiator for collection by employer.
11.4 | Radiators: Design and provide and install new sufficiently sized low surface temperature (LST) radiators with thermostatic radiator valves (TRV) in positions R1-R10 as shown on drawings.
11.5 | Fan Convectors: Design and provide and install new sufficiently sized SPC Belgravia Supreme Inverted or similar approved high level fan convectors with built-in thermostats in positions FC1-FC5 as shown on drawings.
11.6 | Radiant Panels: Design and provide and install new sufficiently sized high level radiant panels in positions RP1-RP2 together with independent local room thermostat controller located in discreet places (T) as shown on drawings.
11.7 | Heating Pipework and associated Insulation: Drain down and remove all existing heating pipework. Design and provide and install sufficiently sized new heating pipework runs in positions as shown on drawings. Allow for routing heating pipework at high level for fan convectors and through suspended ceiling voids with sufficient air vents where applicable. Provide and fit 25mm foil lagging with appropriate lagging identification to all heating pipework within ceiling voids.
11.8 | Existing Hot Water Cylinder: Existing hot water cylinder to remain.
11.9 | Domestic Pipework and associated Insulation: Existing hot and cold and secondary pipework is to remain. Allow for alterations to pipework at the point of a new appliance. Allow for lagging new and existing domestic pipework as required.
11.10 | Main Kitchen: Existing mechanical installation to remain.
11.11 | Link Room / Kitchenette: Provide and install new thermostatic mixing valve (TMV) to new sink. Allow for future dishwasher.
11.12 | Gents Toilet: Remove all existing wash hand basin taps and waste fittings. Provide and fit new chromium plated wash hand basin taps and waste fittings in existing positions. Provide and install new thermostatic mixing valve (TMV) to existing wash hand basins. Provide and install new cisternmister to existing urinals.
11.13 | Ladies Toilet: Remove all existing wash hand basin taps and waste fittings. Provide and fit new chromium plated wash hand basin taps and waste fittings in existing positions. Provide and install new thermostatic mixing valve (TMV) to existing wash hand basins. Provide and install new cisternmister to existing urinals.
11.14 | Disabled Toilet: Remove all existing wash hand basin taps and waste fittings. Provide and fit new chromium plated wash hand basin taps and waste fittings in existing positions. Provide and install new thermostatic mixing valve (TMV) to existing wash hand basins. Provide and install new cisternmister to existing urinals.
11.15 | Air Conditioning Units: Allow for testing and carryig out a condition report of the 2no. air conditioning units in the existing Learning Centre and their associated roof condensing units . Report any findings and recommendations for bringing existing air conditioning system up to current regulations as work progresses.
11.16 | Provisional Sum: Allow a £2,000 provisional sum for carrying out any recommended work to existing air conditioning system. | 2000
11.17 | Cleaning & Chlorination: Allow for cleaning and chlorination of all installations on completion.
11.18 | Testing & Commissioning: Carry out all necessary labelling and testing and certification to comply fully with current water and gas regulations.
11.19 | Documentation: Provide and hand to employer 2nr Hard Copies and 1nr Electronic Pdf Copy of all necessary Health and Safety (H&S) and Operation and Maintenance (O&M) Manuals together with 'As Installed' Drawings in AutoCAD 2011 format
CONTINGENCIES |  |  | £ | 5000
12.1 | Provisional Sum: Allow a £5,000 provisional sum for unforeseen problems. | 5000
---------------------
TOTAL PRICE (excluding VAT) to APPENDIX A (Form of Quotation): |  | £
---------------------
Signed:
Print Name:
Date:
Position: