## 1-1 Power v5
1-1 Power |  |  | Version 4
item | dates: | weeks | notes | single/3 - phase | amps | 2-1 indoor rehearsal | sub - total (amps) | cast Holding | sub - total (amps) | Cast Check in | sub - total (amps) | Office - Ops / SiTE | sub - total (amps) | Wardrobe workshop | sub - total (amps) | Props workshop | sub - total (amps) | Workforce break area | sub - total (amps) | Volunteer break area | sub - total (amps) | large Scenic storage | sub - total (amps) | Prayer Tents 1 | sub - total (amps) | Viewing / Control Tower | sub - total (amps) | Portacabin Office areas | sub - total (amps) | Toilets / Site | sub - total (amps) | Toilets / Rehearsals | sub - total (amps)
single phase power
lighting (internal) |  |  | LED flourescent lighting | single phase | 0.23 | 30 | 6.9 | 30 | 6.9 | 20 | 4.6 | 15 | 3.45 | 20 | 4.6 | 20 | 4.6 | 20 | 4.6 | 20 | 4.6 | 30 | 6.9 | 20 | 4.6 | 20 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0
Lighting (external at entrance / roller doors) |  |  |  | single phase | 16 | 2 | 32 | 2 | 32 | 2 | 32 | 1 | 16 | 1 | 16 | 1 | 16 | 1 | 16 | 1 | 16 | 2 | 32 | 1 | 16 | 1 | 16 | 3 | 48 | 1 | 16 | 2 | 32
PA (rehearsals) |  |  | 6 x speakers and amps | single phase | 32 | 2 | 64 | 1 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Public Address (internal/External) |  |  | announcements, safety | single phase | 32 | 1 | 32 |  |  |  |  | 1 | 32 | [13 empty] | 0 | 0 | 0 |  | 0 |  | 0
Comms and IEMS chargers |  |  |  | single phase | 63 | [22 empty] | 1 | 63
Fire Detection |  |  |  | single phase | 16 |  | 0 | [19 empty] | 0 |  | 0 |  | 0 |  | 0
TV's |  |  |  | single phase | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
computers / phones |  |  |  | single phase | 0.3 | 10 | 3 | 100 | 30 | 10 | 3 | 20 | 6 | 6 | 1.8 | 6 | 1.8 | 10 | 3 | 10 | 3 | 4 | 1.2 | 4 | 1.2 | 4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Printes / laminators |  |  |  | single phase | 0.5 | 1 | 0.5 | 0 | 0 | 2 | 1 | 4 | 2 | 2 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
wifi router |  |  |  | single phase | 0.5 | 2 | 1 | 2 | 1 | 2 | 1 | 4 | 2 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0 | 0 | 0 | 0
hot water urns |  |  |  | single phase | 16 |  | 0 | 3 | 48 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 1 | 16 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
kettle |  |  |  | single phase | 13 |  | 0 |  | 0 | 0 | 0 | 1 | 13 | 1 | 13 | 1 | 13 | 1 | 13 | 1 | 13 | 1 | 13 | 1 | 13 | 1 | 13 | 1 | 13 | 0 | 0 | 0 | 0
microwave |  |  |  | single phase | 4.5 |  | 0 | 2 | 9 | 0 | 0 | 1 | 4.5 | 0 | 0 | 0 | 0 | 2 | 9 | 2 | 9 | 0 | 0 | 0 | 0 | 2 | 9 | 1 | 4.5 | 0 | 0 | 0 | 0
fridge / freezer |  |  |  | single phase | 1.5 |  | 0 | 2 | 3 | 0 | 0 | 1 | 1.5 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 3 | 0 | 0 | 1 | 1.5 | 2 | 3 | 1 | 1.5 | 0 | 0 | 0 | 0
irons / steamers |  |  |  | single phase | 12.5 |  | 0 |  | 0 |  | 0 |  | 0 | 2 | 25 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
power tool chargers |  |  |  | single phase | 0.7 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 6 | 4.2 |  | 0 |  | 0 | 8 | 5.6 |  | 0 |  | 0 | 20 | 14 |  | 0 |  | 0
Workshop tools |  |  |  | single phase | 16 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 4 | 64 |  |  |  | 0 |  |  |  | 0
sink and hot water |  |  |  | single phase | 16 |  | 0 |  | 0 |  | 0 | 1 | 16 | 1 | 16 | 1 | 16 | 1 | 16 | 1 | 16 |  |  | 0 | 0
extractor fans / vacuum |  |  |  | single phase | 9 |  | 0 |  | 0 |  | 0 |  | 9 | 1 | 9 | 1 | 9 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Washing Machines |  |  |  | single phase | 10 |  | 0 |  | 0 |  | 0 |  | 0 | 2 | 20 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Tumble Dryers |  |  |  | single phase | 11 |  | 0 |  | 0 |  | 0 |  | 0 | 2 | 22 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
sewing machines |  |  |  | single phase | 0.75 |  | 0 |  | 0 |  | 0 |  | 0 | 4 | 3 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
additonal worklight |  |  |  | single phase | 2 |  | 0 |  | 0 |  | 0 |  | 0 | 10 | 20 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Portacabins |  |  |  | single phase | 32 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 3 | 96 |  | 0 |  | 0
heating / ventilation |  |  | 170kw | single phase | 32 |  | 0 |  | 0 |  | 0 | 1 | 32 | 1 | 32 | 1 | 32 |  |  |  | 0
heating / ventilation |  |  | 110 to 150kw | single phase | 16 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 1 | 32 | 1 | 32 |  |  | 1 | 32 | 1 | 32
Buggy Power |  |  |  | single phase | 16 |  | 0 |  | 0 |  | 0 | 4 | 64 |  |  | 4 | 64 |  |  |  | 0
Toilets units |  |  |  | single phase | 16 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 6 | 96 | 18 | 288
[7 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | total (AMPS) single phase |  |  | 141.4 |  | 163.9 |  | 45.6 |  | 219.45 |  | 183.9 |  | 226.1 |  | 113.1 |  | 113.1 |  | 58.7 |  | 68.3 |  | 78.8 |  | 240.5 |  | 112 |  | 320
3 - Phase Power
heating / ventilation |  |  | 2 x 300 kw running 16 amps / phase | 3 phase | 32 | 2 | 64 | 2 | 64 | 1 | 32 | 0 | 0 | 1 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Sound Power (FOP) |  |  |  | 3 phase | 32 | [20 empty] | 1 | 32
machinery |  |  |  | 3 phase | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
welding equipment |  |  |  | 3 phase | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reefer containers |  |  |  | 3 phase | 63 |  |  | 2 | 126
water pumps |  |  | for supply of water | 3 phase | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 32 | 1 | 32
|  |  |  | total (AMPS) 3 phase |  |  | 64 |  | 190 |  | 32 |  | 0 |  | 32 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 32 |  | 0 |  | 32 |  | 32
Farms | [33 empty] | Farm sub-totals (amps) |  | three phase |  | diversity 15% | kVa
1. FOP, Cast Holding, 2-1, reefer containers | 09/5/22 to 8/8/22 | 14 weeks | single phase |  |  |  | 141.4 |  | 163.9 | [17 empty] | 78.8 | [5 empty] | 320 | single | 234.7
|  |  | 3-phase |  |  |  | 64 |  | 190 | [17 empty] | 32 | [5 empty] | 32 | 3-phase | 318 | 552.7 | 560 | 448 | 322.3022
2. Cast checkin / Scenic workshop / Vols Break area / Prayer | 09/5/22 to 15/8/22 | 14 weeks | single phase | [7 empty] | 45.6 | [9 empty] | 113.1 |  | 58.7 |  | 68.3 | [8 empty] | single | 95.2333
|  |  | 3-phase | [7 empty] | 32 | [9 empty] | 0 |  | 0 |  | 0 | [8 empty] | 3-phase | 32 | 127.2333 | 140 | 112 | 80.5755
3. Site / Workshop / Office / Portacbins | 25/4/22 to 25/8/22 | 18 weeks | single phase | [9 empty] | 219.45 |  | 183.9 |  | 226.1 |  | 113.1 | [9 empty] | 240.5 |  | 112 |  |  | single | 365.0167
|  |  | 3-phase | [9 empty] | 0 |  | 32 |  | 0 |  | 0 | [9 empty] | 0 |  | 32 |  |  | 3-phase | 64 | 429.0167 | 450 | 360 | 258.9928
[38 empty] | Total kVa | 661.8705
supply distribution breakdown | type | [32 empty] | totals
16 amp single | c-form | [5 empty] | 6 |  | 6 |  | 6 |  | 10 |  | 8 |  | 12 |  | 4 |  | 4 |  | 2 |  | 2 |  | 2 |  | 3 |  | 5 |  | 19 | 89
32 amp single | c-form | [11 empty] | 2 |  | 1 |  | 2 |  | 2 |  | 2 |  |  |  | 1 |  | 1 |  | 3 |  |  |  |  | 14
63 amp single | c-form | [5 empty] | 1 | [7 empty] | 1 | [7 empty] | 1 |  | 1 |  |  |  | 2 |  |  |  |  | 6
125 amp single | c-form | [32 empty] | 0
16 amp 3 phase | c-form | [32 empty] | 0
32 amp 3 phase | c-form | [5 empty] | 2 |  | 2 |  | 2 |  |  |  | 1 | [11 empty] | 1 |  |  |  | 1 |  |  | 9
63 amp 3 phase | c-form | [7 empty] | 2 | [24 empty] | 2
125 amp 3 phase | c-form | [32 empty] | 0
n.b. Further stepdown will be required to 16amp C-form and 3-pin UK sockets