## Sheet1
| RFQ FY19-30 Clean room Q&A | Responses
1 | Now that we have had the opportunity to study the tender documents in more detail, it would appear that Item 11 on the spreadsheet headed Cleanroom Response template, calls for multiple 480V and 3PH power supplies capable of delivering 450 A per phase. This is indeed quite a large requirement and as it is 60Hz it would have to be generated on site, unless you have this frequency and power supply available | Original requirement #11 is now no longer relevant, please disregard this requirement and do not include this in your response.
Power Multiple 480V-3PH-60HZ (capable of 450A per phase) drops in the vehicle integration/test room. Multiple 240V-3PH-60HZ in the production area 120V equivalent available in all other areas., this is for all internal equipment as well as plant.
2 | Please furnish desired Tem. requirement inside clean room | Maintained temperature 18 – 22 degrees centigrade
3 | b. Heat Load room wise and area occupancy ( no. of people working ) in each room. | We anticipate there being multiple operators working on kit within same however they will be spread out.
TVAC and shaker will have their own heat removal systems in place
Environmental test area. 4 people:
3 people
20 people
4 people
6 people
4 | The cleanliness as in tender document is at rest ( Not during operation ) kindly confirm. | This is the minimal level of cleanliness at; set up, during equipment installation and during operation, ISO 8 for all areas apart from main Cleanroom
5 | Please provide cross section drawings to understand the True & false ceiling level. | Minimum false ceiling height is to be 4m above finished flooring level
6 | Technical area for keeping AHU / Electrical mains / BMS system etc. | The controls should be within the existing ground floor plant room. The positioning of the Air Handling Unit must be part of the contractors design – preferably not intruding into the MOC space.
7 | We understand that the guarantee period is comprehensive but we do not have to appoint technician to run the system for this guarantee period kindly confirm | A technician is not required on site at all times, however you must provide access to a technician via a call out service as when issues occur – this should be for a minimum of the three year anticipated support contract. The call out time should be at a maximum of 24 hours after a request is made.
8 | There is a requirement for multiple Compressed Air drops in all cleanrooms. Please confirm whether there is an existing system that we are extending or is this a new standalone system and we are to include for the generation equipment. | This needs to be a new system. Please specify the following as an optional price element.
If we are to include a generation plant, please confirm the specification ie Oil free, volume required, materials of construction.
All air must be clean and oil free
Please assume that all equipment will need to be run at the same time:
TVAC equipment:
Pressure: 7 bar
Consumption: 20 cubic meter per hour
Vibration kit
Pressure: 100 PSI
Clean rooms:
Pressure: 50 PSI
Note that the clean air lock needs its own supply for an air shower
In addition to the above, the number of required air drops in each space are:
TVAC = 1
Vib = 1
Prep air lock = 1
Gowning area = 1
1 air drop
8 air drops
4 air drops
4 air drops
9 | Please confirm materials of construction for the Compressed Air system pipework. | Stainless steel
10 | Please confirm that there is no additional LEV within any of the cleanrooms | Local Exhaust Ventilation will be required in the following room (this is because this space will accommodating soldering and epoxy gluing activities)
11 | Please confirm that the 3-phase power supply is 50hz and not 60Hz as stipulated in the enquiry | See question 1
12 | Please confirm the loading on floor with regard to trolleys/plant being used and the frequency of use. This will affect the flooring finish. Please advise if there is a preferred flooring finish. | Please assume that there will be heavy loads on the floor and therefore a suitable finish must be provided, we are anticipating a painted finish, however please advise if other options are available
13 | Please confirm the load bearing capacity of the “Facility Mechanical Allocation” to ensure suitability for any plant. | 7.5 kN/m2
14 | The wall between the Technical Support Area and the Production and Assembly Cleanroom Area is shown as a white hatched wall. Please confirm the construction of this wall ie Standard Panel, demountable panel, glazing, door etc.
The above image shows a glazed window, connection ports are required for all glazed windows shown
FYI: The below image shows a doorway between two spaces
15 | Are you able to provide the number of single-phase sockets required? (Per room if possible). Currently proposed is 1x twin socket per 3 linear metres. | 1x twin socket per 3 linear metres.
Please also provide a marginal value if we add or subtract from this value
16 | Please detail the number of ethernet points per liner meter? | 1x twin socket per 3 linear metres.
Please also provide a marginal value if we add or subtract from this value
17 | Assumed currently is comfort cooling for all rooms, are there specific temperature requirements? | See question 2
18 | Humidity requirement is this to be 40 – 60 as noted in URS. Is this specific or is a requirement less than 50% RHU (for example) acceptable. Please state an Humidity upper limit if so i.e. humidity to be no more than 50%. The range currently noted is achievable and specified, however may be cost saving options if only setting an upper limit. | The lower bound is 40 and the upper bound is 60
19 | Is humidity control required in change areas? This is uncommon and not currently specified, main production areas are specified with Humidity control as noted. | No
20 | Is there specific lighting lux requirement? | 1000 lux, adjustable between 500 and 1000 lux. With presence detection
21 | 1st Floor | Yes, please specific the maximum that you can achieve in this area
On visiting site is has been noted that maximum available height is 3.09m meaning a 4m ceiling cannot be achieved. Can you confirm that we are okay to specify an internal height to allow for install and FFU placement within the limit of 3.09m?
22 | Further Notes for Attention for the consideration of Catapult Satellite Systems | The concreate slab already has a damp proof membrane underneath. So please assume that an additional one is not required at this stage
Flooring is specified on the assumption that it will be ready to lay, a damp proof membrane is sometimes treated if needed. Flooring will need not to have high moisture content which could affect vinyl. This can be discussed at next stage if needed.
23 | As the ceilings are at 4m we have proposed doors at 3.5m due to a canopy requirement above. If a 4m door opening is required ceilings would be required to be at 4m. | The tender documents asked for the ceilings to be at 4 meters