## test
REDACTED Building Control Ltd. - Plans Assessment - Project Reference - 303564
Report Date: 21/02/24 Project: Conversion of the loft space of a single storey sports pavilion to form a day nursery. @ Pilsley Sports Pavilion, Rupert Street, Lower Pilsley, Chesterfield, Derbyshire S45 8DB REDACTED
|  |  | 9 Outstanding issues | 5 Issues under consideration | 13 Resolved issues
Reference | Description | Assigned To | Info Provided | Remarks | Status
1 | PART A – STRUCTURE
1.1 | Please confirm that the existing trusses where designed with the proposed loads factored into their design |  |  | A structural engineer has been engaged to asses the design and has prepared a design / calculations for where any additional load is proposed / trimming arrangement is proposed | a
2 | PART B - FIRE SAFETY
2.1 | Fire warning and detection conforming to BS 5839 Pt. 1 2017 with smoke detectors, fire alarm call points, sounders and panel. These to be interlinked with the existing fire warning system |  |  | Note for Fire Consultation | a
2.2 | Emergency lighting in accordance with BS 5266 2016 |  |  | Note for Fire Consultation | a
2.3 | Please ensure escape/exit signage which conforms to BS 5499 part 1 to all exits and circulation routes. Section 5.28 page 51 Approved Document B vol 2. |  |  | Note for Fire Consultation | a
2.4 | Final exit doors should have simple fastenings able to be operated quickly in an emergency, e.g. panic bar/push pad door release, designed to BSEN1125. Section 5.7 page 47 Approved Document B vol 2. |  |  | Note added to drawing | a
2.5 | The inner rooms will require means of alerting occupants to the outbreak of fire in the outer room, from which they lead off. Either a smoke detector is required, situated in the outer room, linked to the alarm, or vision between the rooms. |  |  | Smoke detection is proposed and has been indicated to all habitable inner rooms | a
2.6 | Service penetrations through compartment walls/floors or means of escape should be suitably fire stopped and/or with fire dampers/collars as appropriate. |  |  | Note added to drawing | a
2.7 | Please ensure surface linings to walls and ceilings in accordance with Table 6.1 of Approved Document B Volume 2. Rooms of max 30m2 linings permitted to Class 3, other rooms to be Class C-s3,d2 and circulation spaces Class B-s3, d2. |  |  | Note added to drawing | a
2.8 | Any electrically powered locks should return to the unlocked position on operation of the fire alarm, loss of power or system error and on activation of a manual door release unit (green break glass.) |  |  | Note added to drawing | a
2.9 | Please confirm proposed occupancy figures and management plan for evacuation in the event of a fire |  |  |  | r
2.1 | Plans have been sent to the local fire authority for consultation. Any comments will be forwarded as soon as they are received. |  |  | Noted | r
3 | PART F - VENTILATION
3.1 | Please ensure extract ventilation to the WC's - 6l/s per wc |  |  | This is specified on the accompanying project specification, under point 17.0 | a
4 | PART H - DRAINAGE AND WASTE DISPOSAL
4.1 | Provide details to the new foul water drainage system and the discharge point to the existing network. |  |  | Staff & Kids WC are to discharge to the existing stub stack of the ground floor sports pavilion. This is to be confirmed following exploration work on site. | a
5 | PART K - PROTECTION FROM FALLING, COLLISION AND IMPACT
5.1 | Stairs intended for all users of a building on a day-to-day basis should be design as a general access stair(s). Minimum 1200mm wide (measured between walls/upstands); a minimum width of 1000mm between handrails; maximum of 12 risers (in exceptional circumstances no more than 16, subject to agreement with Assent); open risers are not permitted; risers between 150-170mm; goings between 250-400mm; minimum head-height of 2m measured from the pitch line. Landings should have an unobstructed length of 1200mm and be clear of door swings. |  |  | Drawing amended and minimum dimension added | a
5.2 | All nosings are to be made apparent with permanently contrasting material 55mm wide on both the tread and the riser. There should be a light reflectance difference between the stairs and the nosing of at least 30 points |  |  | Note added to drawing | a
6 | PART M - ACCESS TO AND USE OF BUILDINGS
6.1 | An Access Strategy is required to demonstrate that the proposals are appropriate and meet the equivalent provisions in Approved Document M - Volume 2 |  |  |  | r
6.2 | A unisex wheelchair WC should be provided. The WC compartment should have a minimum size of 1500mm wide by 2200m wide, when the WC is the only unisex WC in the building the width should be increased to 2000mm. The WC should be in accordance with Diagram 18 of Approved Document M - Volume 2. |  |  |  | r
6.3 | Any tea making facility should be designed to accommodate both standing and seated users such that at least one section of the counter is max 760mm high with a min 700mm knee recess under. |  |  |  | r
6.4 | Wheelchair WC emergency assistance alarm system shall provide (a) Visual and audible indicators (b) reset control reachable from a wheelchair and the w.c. (c) signal distinguishable visually and audibly from the fire alarm. |  |  |  | r
6.5 | Wheelchair-accessible unisex toilet door to have an mechanism to be capable of being opened outwards, from the outside, in case of an emergency. |  |  |  | r
6.6 | Wall-mounted socket outlets, telephone points and TV sockets are located between 400mm-1000mm above finished floor level. Switches for permanently wired appliances are located between 400mm-1200mm above finished floor level. |  |  |  | r
6.7 | A level threshold should be provided to the entrance door |  |  |  | r
7 | COMMISSIONING, CERTIFICATION AND INFORMATION PROVISION
7.1 | Commissioning certification is required for the fire alarm system on completion confirming that the installation is in accordance with BS5839. |  |  | Noted, can this be conditioned
7.2 | Commissioning certification is required for the emergency lighting system on completion confirming that the installation is in accordance with BS5266. |  |  | Noted, can this be conditioned
7.3 | Commissioning certification is required for the electrical system on completion confirming that the installation is in accordance with BS 7671. |  |  | Noted, can this be conditioned
7.4 | Regulation 38 (Approved Inspector Regulations 2000) requires that fire safety information to aid the responsible person in carrying out the Fire Risk Assessment is provided, we are unable to issue our Final Certificate until we are satisfied that such information has been provided. For guidance on information to be provided please refer to Appendix G of Part B 2006 Edition Volume 2. |  |  | Noted
7.5 | An Energy Performance Certificate (EPC) is required for the completed building. |  |  | This information should follow