## Sheet1
Reference No | Questions | Response
1 | Are contractors to include for the interfacing into the Existing Fire Alarm System a. if so can you confirm the protocol of the Fire Alarm System b. if not can you confirm if we are to include costs from the Incumbent provider to supply, install & commission these interfaces and their contact details or will the council engage them directly | A) Open protocol B) N/A
2 | Can you provide a copy of the existing and proposed Cause & Effect Matrix | The BMS is notified; Mechanical Plant is shut down (extract fans, pumps, AC Condensers etc.) via the Motor control panels; The Access Control System releases normally secured doors/access points; The lifts returns to the ground floor; Fire Curtains are closed
3 | Are contractors to include for the Modification of the Existing Fire Alarm System Cause & Effect, if not can you confirm if we are to include costs from the Incumbent provider to undertake this work and their contact details or will the council engage them directly | Include all costs for modification
4 | If the Interfaces, C&E are to be undertaken by the incumbent maintenance provider, can you confirm if we are to include the costs for the incumbent maintenance provider to provide attendance during the C&E testing & Audibility Testing or will the council engage them directly, can you please provide contact details for the incumbent if we are to engage with them | N/A
5 | Can you confirm if all Testing is to be completed outside of normal working hours | Price of both options Option A: Normal Working Hours Option B: Outside Normal Hours
6 | Can you confirm if all installation works are to be completed outside of normal working hours, if so can you confirm the required working hours | Price of both options Option A: Normal Working Hours Option B: Outside Normal Hours
7 | Can you confirm if we are to provide new containment (Primary & Secondary) or are we to fix to structure and use existing containment where provided | Use existing containment & trays
8 | It would appear that the building is Grade listed, can you confirm what Grade? | Grade 2
9 | Can you advise what restrictions are in place for the running of cabling, drilling through walls, fixing to building fabric? | The basement accommodation and the 2nd floor offices are not ‘heritage sensitive’. Listed building consent may be required for the special areas of the ground and first floor.
10 | If there are restrictions in place for cabling, drilling and fixings to building fabric, then site intrusive surveys will be required for the planning of fixings, cable runs and pipe routes to minimise their visual impact and their impact on the fabric of the building. It's important to respect the character of the building. For example, don't cut through mouldings and decorative details while designing routes to minimise the lengths of cable runs. We would suggest that a PC Sum is added to the tender pricing document for an intrusive survey to identify/locate cable routes, fixings, existing containment & trays. Please advise? | Please allow for the PC sums as suggested
11 | Drawings Could you please issue the following if available? • Fire Strategy/Compartmentation Drawings • Primary Containment Drawings • Drawings showing Electrical Riser Locations • Roof Drawing | Fire Strategy/Compartmentation Drawings attached
12 | Fire Alarm During our walkaround it was confirmed that Chubb are the incumbent maintenance provider of the Fire Alarm System, they are engaged via Integral who are you incumbent FM Provider, can you please confirm the following 1. Who is responsible for providing the Interfaces for the integration to the Fire Alarm? Contractor or Chubb/Integral | Lambeth assumes that the integration to the fire alarm will form part of these works
13 | Who is responsible for producing the revised C&E Document & Testing this once the system has been installed? Contractor or Chubb/Integral | The responsible party will be the winner of this tender exercise.
14 | Who is responsible for reprogramming the Fire Alarm System and removing the sounders from the system (note this is a programming element only)? Contractor or Chubb/Integral | The responsible party will be the winner of this tender exercise.
15 | DO you require the detectors that have Sounders integrated that are currently installed to be replaced with detection only, if so who is responsible for this? contractor or Chubb/Integral | Lambeth require like for like replacements
16 | Can you please provide contact details for Integral | Lambeth expects the preferred bidder to be soleresponsible for the project and then handover to Integral Lambeth.Helpdesk@integral.co.uk
17 | Fire Stopping/Making Good Can you confirm that the contractor will be responsible for the following Firestopping of all penetrations made however this will not be certified Any Builders Works in areas that are not covered by Listed Consent Making Good in areas not covered by Listed Consent All other builders works/making good in areas where listed consent is required will be undertaken by the Council directly using its own approved contractors | Yes - Fire Stopping and making good to be part of the project
18 | Listed Consent/Conservation During our site visit it was clear that there are going to be concerns around the installation works on the Ground & 1st Floor, as such can you confirm that should be be successful in securing the contract that any change of scope or additional works that are identified as a result of the meetings with he conservation team will be accepted as variations and not expected to be included within our price? | Correct - post contract alterations requested for LBC purposes will be accepted as variations
19 | Roof As discussed please can you confirm that we are to allow for 20no horn speakers to be located on the roof areas in lieu of there not being a roof drawing available. | Make the allowance. Locations can be determined post contract
20 | Working Hours Following our site visit it our opinion that these works would have to be completed outside of normal working hours so can you confirm you are happy for us to cost this project on OOH working, if we secure the contract and we find there are areas we can complete in normal working hours then we would look to issue am agreed rebate. | Correct - price for OOH working
21 | PAVA Panel Location As discussed please confirm that you are happy with the location of the panel in the Basement Plant Room as highlighted below (Yellow Line) | Correct
22 | Containment Following our site visit please confirm the following agreed onsite Basement • Primary Containment in areas where insufficient space is available (Potential space for up to 48 Cables) • Secondary Containment in all areas (Galvanised Conduit) • Reuse existing containment and ducting for installation | Yes, subject to listed building consent where applicable
23 | Ground Floor • No primary Containment located (No access to voids on 1st floor to install cables) so all cables will need to be fixed to structure (This needs to be confirmed with conservation) • Secondary Containment in all areas (Either Galvanised or White Plastic Trunking) | Subject to listed building consent where applicable
24 | 1st Floor • No primary Containment located (No access to voids on 2nd floor to install cables) so all cables will need to be fixed to structure (This needs to be confirmed with conservation) • Secondary Containment in all areas (Either Galvanised or White Plastic Trunking) | subject to listed building consent where applicable
25 | 2nd Floor • No primary Containment located (No access to voids on 1st floor to install cables) so all cables will need to be fixed to structure (This needs to be confirmed with conservation) • Secondary Containment in all areas (Either Galvanised or White Plastic Trunking) | Subject to listed building consent where applicable
26 | Roof • Reuse Primary Containment where applicable and provide secondary containment | Correct
27 | Risers • Reuse primary containment where applicable but provide new containment | Correct
28 | PAVA System We discussed the viability of having a PAVA System as there is no real change of strategy or change of evacuation, it was discussed that part of the reason for the change was to try and manage potential events such as malicious activations, staff alerts etc etc and it was viewed because there is a PAVA System in the civic hall that this would work well in the town hall. One of the main benefits of PAVA, especially in buildings where there is a lot of public footfall, is the ability to be able to direct and instruct people to evacuate who may not be familiar with the building, however I assume that the access to the general public in the town hall is minimal so the benefits of a PAVA System do not seem aligned to the requirements. With that in mind it may be more financially viable or beneficial to look at a PA System, this can be used to provide things such as Staff Alerts, instructions and also potential announcements | You can provide a stand alone price for a PA system
29 | 2 Stage Tender We discussed during our walkaround that due to the challenges of installation and that there needs to be some clear consultation with Heritage Stakeholders that it may prove more beneficial for the council to undertake a 2 stage tender process as outlined below • Stage 1 – Design/PCSA Period – Engage with a specialist to undertake the surveying, designing and consultation with the stakeholders to ultimately produce a fully designed system that is in keeping with the requirements of the heritage requirements, providing clear information on things such as Containment provision, workmanship, access requirements, installation, integration etc. The final product being a fully quantified design that can then be issued out to tender along with all of the prerequisites • Stage 2 – Tender – By providing all tenderers with a fully designed and quantified tender provision, all of the bids you receive will be like for like and allow you to compare and assess against a clear set of deliverables and ER’s | At this stage we will work to a single stage tender
30 | Do you have any further drawings to help assist in our quotation? | Please see enclosed
31 | Quality question 2 states that we are to provide a Risk Assessment & Method Statement (RAMS) and Construction Phase Plan to be evaluated based on: 1. completeness of Construction H&S Plan 2. H&S Plan identifying hazards and controls 3. H&S Plan identifying address of emergency arrangements We believe that this would be prepared at post - contract stage if successful once all inital site visits /surveys are completed. Can you confirm that a previous example of the above will be acceptable? | Yes this can be arranged at post-contract stage if successful
32 | If the submission date is now 10th February , can you advise how this affects the rest of the dates in the procurement process? | Add 3 weeks to each of the dates
32 | Supplier should make the following alterations to the existing fire detection system: a.Install a repeater panel on the wall behind the security desk, in order that staff can immediately see and hear if the fire alarm has gone into pre-alarm state | Repeater panel can be located in ground floor main reception area
33 | Do you have a drawing showing location of fire alarm control panel in relation to security desk? | The location of the fire control panel is in the ground floor security room. The reception desk is on the ground floor as well. These are indicated in the floor plans made available
34 | How many loops does the existing fire alarm control panel have? | 6 Loops (see attached Schematic + Layour Plans)
35 | b. Install on the security desk, a repeater system to enable staff to speak to someone in a refuge area or see which emergency core has been activated
| Please confirm designated refuge area? | 1st floor Brixton Hill Stairwell
36 | Supplier should install a beacon on each floor for staff who cannot hear the alarm sounding
| How man beacons are required on each floor? | Use industry standard, where there is no industry standards the expectation will be for bidders to propose such unit prices. The Town Hall does have induction loops that people with partial hearing can also use
| Is the system Apollo or Hochiki protocol? | Contractors discretion