# APPENDIX B

SCHEDULES OF TECHNICAL REQUIREMENTS

B1	Aquarium Pump Motors

B2	Laboratory Seawater Pumps

B3	External Seawater Fill Point

APPENDIX B

SCHEDULE OF TECHNICAL REQUIREMENTS

B1	 AQUARIUM PUMP MOTORS

Manufacturer: 	Michael Smith Engineers Limited

Unit E

Scotswood Park

Forsythe Road

Sheerwater

Woking

GU21 5SU

Telephone:	01483771871

Contact:	Adrian Turner

Email:	a.turner@michael-smith-engineers.co.uk

Quote Ref:	15318

2No Brooke Compton

4.0 kW 112 Frame 2 pole motors

400V/3Ph/50 Hz IP55 B34 IE3

Painted in accordance with 3.3 coating

Finish colour RAL 5010 (Blue)

APPENDIX B

SCHEDULE OF TECHNICAL REQUIREMENTS

B2	 LABORATORY SEAWATER PUMPS

Supplier: 	Grundfos Pumps Limited								Grovebury Road

Leighton Buzzard

Bedfordshire

LU7 8TL

Telephone:	01525 850000

Contact:	Alexander Phelps

Website:	www.grundfos.co.uk

| No Off | 2 |
| --- | --- |
| Model | CRT-4-5 A-P-A-E-AUUE |
| Type | Vertical, non-self-priming, multistage, in-line centrifugal pump for installation in pipe systems |
| Electrical Supply | 380 – 415V/3Ph/50 Hz |
| Motor | 1.1 kW |
| Rated Current | 2.50 A |
| Starting Current | 450 – 500% |
| Rated Flow | 6 m3/h |
| Rated Head | 30.6 m |
| Pump Speed | 2900 rpm |

Notes:

1.	Pumps selected as like for like replacement of existing but with titanium components for protection against seawater corrosion.

APPENDIX B

SCHEDULE OF TECHNICAL REQUIREMENTS

B3	EXTERNAL SEAWATER FILL POINT

Existing fill point was originally supplied by Landon Kingsway and is marketed as an Oil Fill Point.

Dimensions:  650 W x 580 H x 300 D

Contractor to provide a bespoke GRP enclosure of similar dimensions c/w openable/lockable lid and housing suitable plastic isolation valve and hose connector.

The Contractor is able to offer as an option a similar Landon Kingsway replacement product but constructed from stainless steel for corrosion resistance