## Sheet1
Question number | Question description | Answer
1 | Clause 5.16.3 refers to an “IP based HTTPS Browser package” further details required please, i.e.: • Does the client have a specific browser system in mind, or system preference. • Which items of equipment are to be accessible ( full list required please ). • What information and level of access, is required for each item of equipment. • Is a PLC/Laptop required to be provided. | Internet Explorer & Firefox. I don’t understand the question Ditto No – TRP to supply.
2 | Clause 4.2.5 refers to Fibre Optic Network cabling, do we assume that the following applies: • All Fibre Optic cables will be supplied, installed and terminated by others, (except the one cable specifically excluded, i.e. between the Tennis Centre Pump House and the Diana Plant Room). • The client, or others, will provide and install “Fibre Optic to Copper” Ethernet switches at each of the 9No locations referred to in clause 5.16.3. | Yes. NO – TRP will have the fibre-optic network running by then. It is the contractor's job to provide the physical connection to it. 100m for copper links.
3 | Do we assume that all network cabling, at each of the 9No locations, is to be carried out under cover of this contract, as follows: • All equipment, connected onto the “network” at each location, will be connected by means of copper cables. • Network cabling can be carried out using CAT5 cable. • CAT5 cabling can be clipped direct, or installed within proprietary cable containment systems, as deemed appropriate. | Yes. Yes. Yes.
4 | The existing automatic control system at Italian gardens includes a Mitsubishi and an Allen Bradley PLC, in this regard: • Does the client have a preference in regards to PLC manufacturer and type. • It is our understanding that PLC/s will be required to control and co-ordinate all equipment. The PLC/s will have to be connected to all associated control equipment via an Ethernet network, does the client have a network protocol preference. • Is Control to be via a single PLC with distributed I/O, OR are PLC’s required at various locations, at our discretion. | No. Standards based IP network will be installed, min 10M prefer 10/100M duplex. Not sure which is best for the design, PLC at each location might be most robust option.
5 | Have the approximate Pump Motor sizes, been ascertained. | Yes.
6 | Can you please confirm that “Form 2“, “single wardrobe style” Motor Control Panels will be acceptable, at each location. | This will be acceptable.
7 | Can you please provide a full “P and I diagram” of the Pumping system. | No – the drawing is schematic and may change based on location of buried tank etc., and other things as yet unknown. The key is that the schematic is understood and price accordingly and on a like for like basis
8 | We understand that the Ultra 5, Ultrasonic level controllers, are complete with Modbus RTU, NOT Modbus TCP IP-as such they cannot easily be connected to the Fibre Optic network, as requested within the specification. Can you please clarify the exact requirement. | They must talk to the network, either with the necessary adaptation or with alternative ultrasonic level controllers that can. This may therefore, if necessary be offered as an alternative
9 | Have Grundfoss already been approached in regards to the CU352 and CU362 controllers, and GRM, referred to- if so can you please provide a project reference to enable a quote to be obtained. | They have been approached but there is not a project reference for the contractors to pull off. The supply is direct from the contractor and other manufacturers may be approached. However, the contact for discussion at Grundfos is Nick Christopher
10 | We are struggling to collate a competitive tender within the tender timetable set out within the ITT. We wish to request an extension until 7 December if possible. | The tender submission deadline has now been extended until 5pm on Thursday 3rd December.
11 | For a cable length prospective, we need to know the locations of the following: • Flowmeter Hyde Park Reservoir Supply Line. • Flowmeter Round Pond Supply Line. • Flowmeter Diana Princess of Wales Fountain Supply Line. • Flowmeter Irrigation Tanks and Toilet Supply tanks Supply Line. • Flowmeter Rotton Row sports pitches irrigation Supply Line. | TBC
12 | Can you please confirm distance between the “Buried Tank” and associated “Pumphouse”, for cabling purposes. | TBC
13 | From where do we derive the main Power supply for the “Buried Tank Pumphouse”: • Distance • Power supply capabilities. | The power requirement for the new pumping station is 89.3A to which we’ll need to add a light, a small heater and other ancillaries. We have allowed for a 100A supply, plus allowance for starting currents. (Only the Rotten Row Booster Pump and the Toilet and Irrigation Tanks Booster Pumps will be operated via VFD) Load tests have been done within the electrical plant room attached to the Diana Fountain plant room and it has been established that there is a 400 amp 3 phase service head in the intake room of the memorial feeding all the fountain equipment off of a very large mains control switch. There is space to install a 100 amp 3 phase system for your requirements. The Load test readings were as follows. • Existing Pumps running at 90% from the existing 400 amp head and everything on = Phase1 loading 221amps, Phase 2 loading 236 amps, Phase 3 loading 238 amps • Therefore by adding 100 amps per phase will allow for 10% variation and have enough capacity for your requirements i.e. Ph1 = 321, Ph2 = 336, Ph3 = 338 amps.
14 | The Bill of Quantities does not include an item for the soft landscaping around the pump house. The hedges and shrubs around the pump house have not yet been specified. How would you like the soft landscaping to be priced / provided for? | The tender shows that this will be done by TRP. It is on the drawings.
15 | Does The Royal Parks have an approved supplier of fencing and gates that can supply ironworks meeting their requirements for the pump house area? | No, We have used a company called Alpha Rail.
16 | Do Park Rules allow a Contractors works vehicle(s) to be locked within their compound overnight? | Yes.
17 | The Tender Response Document (Schedule 6 Q3) requires details of previous contracts featuring, amongst other things, pumping from below ground whilst this Contract does not. Would other contracts reflecting the composition of these works be acceptable? | Yes, this will be acceptable.
18 | Schedule 4 : Section 5.6 refers to the panel being bespoke manufactured, are we to design this using the CU362 and CU352 controllers specified? | Yes.
19 | Schedule 4: Section 5.6 refers to a GRM card. Presumably this is a GSM card. | GRM if Grundfos being used see Grundfos.
20 | Schedule 4: Sections 5.6.1-4 refer to the attached data sheets. Where are the Data Sheets to be found? | The data sheets have been uploaded to the Contracts Finder web site - see document entitled 'Proposed pumps - Diana BH No. 2 Water Distribution'.
21 | Ref the Contract Specific Works Information Cl 5.1 Buried Tank. • Please supply details of the intrusive ground investigation which has taken place in this location (with ground water details) • The material to be used for the base and surround to the tank • The number of power cabling ducts to be built into the tank shell | Please see the document entitled 'AVZ ground investigation report, Hyde Tennis Centre Western boundary, July 2015', which has been uploaded to the Contracts Finder web site.
22 | Ref Bill of quantities item 5.7.2 and Contract Specific Works Information Cl 5.7.2 The bill tem describes ‘Trench work’ 240-250m length The specific WI Clause describes 2nr 110mm ducts, 2nr 90mm PE pipes, a 180mm PE pipe and all associated cabling. Drawing Nr 12 shows 2 nr 110mm ducts (purple), 1 x 160mm PE pipe? (thick purple 180mm?), 1 x 90mm PE pipe (green), 1 x 90mm PE pipe –potable- (blue) Does the bill item include for the pipework described and as shown on the drawing or is it literally just trench excavation and backfilling of same?spec. | Some of the pipe / duct work is already installed, see Dwg. No. 514.1.T.07 for the as-built of the Diana BH No. 2 work. This is covered in Section 5.7.1 as follows: 5.7.1 Installation between existing Diana Plant Room and Diana Borehole No. 2 A new power supply is to be taken from the location adjacent to the Diana Plant Room as shown on Dwg. No. A2_245.T.12 Supply of water between borehole and tank and via the existing Ø110mm communication duct installed in 2012 and as shown on Dwg. No. A2 _514.1.T.07 Diana BH No. 2 pipe work as-built. This may require periodic exposure of the ducting depending on rigidity of the cabling. Within the same duct a new 10mm fibre-optic cable shall be installed plus signal cabling to signal the Diana Fountain Tank supply pump from the fountain tank, plus signal cabling to signal the Diana Borehole No. 2 starter panel in the Diana Plant room from the new Tennis Centre pump house. In summary: • Existing Ø110mm duct - New power cabling from new power connection into existing duct and extension within duct to Diana Borehole No. 2 (and onward continuation) • Existing (same) Ø110mm duct – New 1 No. 2c x 2.5mm signal cable to signal Diana Fountain Tank supply pump (fitted within new tank) from existing plant room • Existing (same) Ø110mm duct - 1 No. 2c x 2.5mm2 signal cable to signal the starter for the Diana Borehole No. 2 pump panel situated in the existing Diana Plant Room • Existing (same) Ø110mm duct - 1 No Ø10mm direct-install fibre cable (free-issue) Some is not and is new between the borehole and the tank/new PH as follows: 5.7.2 Trench between Diana BH No. 2 and Tennis Centre • Ø110mm duct for o 1 No. power cable (described above) and fitted with ‘Electric Cable Below’ tape at appropriate location and o 2 No. 3c x 2.5mm2 SWA XLPE signal cable to open and close the pair of motorised valves in the new chamber • Ø180mm PE pipe for borehole water transfer to tank • Ø90mm potable standard PE as tee’d off Ø160mm potable standard PE north of new pump house • Ø90mm PE to connect the new Diana Fountain Tank supply pump to the existing Ø90mm PE ‘spare’ • Ø110mm duct for o 1 No. 2c x 2.5mm signal cable to signal Diana Fountain Tank supply pump (fitted within new tank) o 1 No. 2c x 2.5mm2 signal cable to signal the starter for the Diana Borehole No. 2 pump panel situated in the existing Diana Plant Room o 1 No. 2c x 2.5mm2 signal cable to take water meter at borehole signals back to Tennis Centre Pump House o 1 No Ø10mm direct-install fibre cable (free-issue) (unbroken run from Diana Plant Room) 5.7.3 Additional duct between South side of Rotten Row and Tennis Centre within Trench 2.4.6.B above See from Dwg. No. 245.T.12 that the main trench southwards from the borehole and just south of Rotten Row includes an additional duct. • Ø110mm duct (spare) – approximately 120m Note to tenderers: This last Ø110mm duct is shown on Dwg. No. 245.T.12 but not on the Dwg. No. 245.T.08. One 450mm x 600mm c/w D400 lid shall be fitted at the northern end of this duct or as directed on site between the start of the duct and the Tennis Centre. The duct shall rise immediately adjacent to the other Ø110mm duct within the Pump House.
23 | Is it intended that this is a single trench housing multiple pipes and ducts? | Yes
24 | Please clarify exactly what is contained in this bill item. | Please see red text pulled from the tender above.
25 | Contract Specific Works Information Cl 5.4 Fence and gate Please provide a drawing and specification for the gate and posts (and an approved manufacturer if possible) , if this cannot be provided please state a provisional sum for the manufacture, painting and installation of the gates. | TBC