## Sheet1
£
Caledonian - Haygrove School |  |  | Opening Up Investigations & Assessment
Revision | 01
Item | Element / Aspect | Purpose | Concern / Focus | Opening up Scope
1 | External wall - Insulated Render | H+S | Fixings | Incorporated in others.
2 | External wall - Insulated Render | Quality | Panel/rail fixings | 1) Photograph and/or mark up existing locations of cladding panels prior to removal. 2) Remove insulated render section to a window/door break to minimise the need for any cutting. Full height at ground to first floor junction and first to second floor junction. 3) Locate joint in VCL and fold back VCL and temporarily secure in place. Where natural joint cannot be located ensure suitable taping material is available for reinstatement. 4)Remove and Set aside removed sections of wall build up with fixings retained for inspection/reuse 6) Remove any drip details to head of masonry panel where masonry panels are located below. 7) Upon completion, allow to reinstate as existing.
3 | External wall - Rainscreen | Fire | Cavity fire barriers | 1) During the removal of item 02 (above) locate position of vertical and horizontal cavity barriers. 2) Cavity barriers to remain insitu unless required to removed under instruction of engineer. should not be cut for removal unless manufacturers literature can be identified to confirm acceptance. Existing fixing arrangements to be determined prior to any removal. 3) Upon completion, allow to reinstate as existing.
4 | External wall - Rainscreen | Quality | Drainage/air voids | N/A
5 | External wall - Rainscreen | Quality | Buildup of barriers/linings | As per item 02
6 | External wall | Quality | DPC placement | 1) Allow to remove external leaf of brickwork to area shown. 2) Allow to remove insulation to expose wall ties, DPC, DPM lap, cavity debris. 3) Allow to remove small area of internal construction to assess wall tie restraint and assess full section detail. 4) Allow to reinstate to match existing upon completion.
7 | External wall | Quality | Cavity - debris
8 | External wall | H+S | Wall ties - Density / Frequency
9 | External wall | H+S | Wall ties - Restraint to SFS
10 | External wall | Quality | Window frame cavity cover | 1) Cavity closer should be visible following removal of brickwork as per the above. 2) At 4no other locations internally allow to remove window reveal and head to identify cavity closers. 3) Allow to reinstate to match existing upon completion.
11 | External wall | H+S | Window operator restraint | N/A
12 | External wall | Quality | Cavity tray/weephole | 1) Cavity tray should be visible following removal of brickwork as per the above.
13 | External wall | Fire | External columns (mid room) | 1) Complete removal of wall build up. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of existing construction to expose structure below. Set aside for reuse. 4) Allow to reinstate to match as existing upon completion Note: Please refer to record drawings for Typical module details for designed build up.
14 | External wall | Fire | External columns (corner) | 1) Complete removal of wall build up. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of existing construction to expose structure below. Set aside for reuse. 4) Allow to reinstate to match as existing upon completion Note: Please refer to record drawings for Typical module details for designed build up.
15 | External wall | Fire | Suspended floor lab level GF to F1 | 1) Complete removal of wall build up. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of existing construction to expose structure below. Set aside for reuse. 4) Allow to reinstate to match as existing upon completion Note: Please refer to record drawings for Typical module details for designed build up.
16 | External wall | Fire | Suspended floor lab level F1 to F2 | 1) Complete removal of wall build up. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of existing construction to expose structure below. Set aside for reuse. 4) Allow to reinstate to match as existing upon completion Note: Please refer to record drawings for Typical module details for designed build up.
17 | Structural | Quality | Foundation / GF Slab | 1) Locate pad foundation grid line within tarmac path. 2) Complete all necessary pre excavation checks for services etc 3) Excavate trial pit to top of foundation and bottom of foundation. Expose pad to frame connection and also perimeter strip foundation either side of pad to limited width 4) Allow to back fill and reinstate as existing A) Where exposing GF slab internally, locate module to module bay joint and locally remove floor finish and set aside for reuse B) Breakout and remove 3mm C20/25 concrete infill, 12mm CP board infill & 2 No. 18mm OSB3 board infill to expose floor construction. C) Alternatively allow for 100mm core hole sample. D) Reinstate to match existing
18 | Structural | H+S | Steel connections - floor beam to floor beam | 1) inspect internally. 2) Above suspended ceiling cut out wall and soffit build up construction to access steel members. 3) identify beam sizes and connection details.
19 | Structural | H+S | Steel connections - soffit beams
20 | Structural | H+S | Steel connections - columns
21 | Structural | H+S | Steel - diagonal bracing | 1) Inspect internally. 2) Cut out small pockets of wall construction to expose beams ends to confirm beams sizes and connection details.
22 | Roof | Quality | Parapet / fascia - fixings | N/A - By Others
23 | Roof | Quality | Single ply - instalation
24 | Roof | Quality | Single ply - integrity (electronic)
25 | Roof | Quality | Standing seam - integrity/weatherporofing
26 | Roof - RW | Quality | RW outlet - Fall
27 | Roof - RW | Quality | RW oultet - Leaf guard
28 | Roof - RW | Quality | RWP system - Debris
29 | Floor | Quality | DPM placement | As per item 17
30 | Floor | Quality | GF below floor ventilation (air bricks, internal walls, void depth) | 1) complete exposure of foundation as per item 17 2) Directly below position of above ground air brick, breakout and set aside brickwork from top of foundation to expose periscopic air vent penetration through to sub-floor void. 3) Where possible dislocate periscopic air vent to allow visibility through to subfloor void. 4) Where not possible to dislocate air vent, cut out section of sheathing board to allow visibility into sub floor void. 5)Allow to reinstate to match existing upon completion
31 | Floor | Fire | Fire stopping - unit junctions | 1) Refer to Cavity Barrier Setting Out drawing. 2) Within specified location locally remove floor finish to expose module unit junction 3 )Breakout and remove 3mm C20/25 concrete infill, 12mm CP board infill & 2 No. 18mm OSB3 board infill to expose floor construction. 4) Use borescope to check for linear ventilated cavity barrier 5) Allow to reinstate to match existing upon completion
32 | Floor | Fire | Fire stopping - shafts/risers | 1) Within located risers cut out and remove existing fire stopping to confirm build-up. Existing firestopping generally consisting of ablative coated batt and intumescent mastic or cured fire rated compound 2) Allow to reinstate to match existing upon completion
33 | Floor | Fire | Fire stopping - shafts/risers | As above
34 | Wall internal (etc) | Fire | Buildup determination | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Section of wall element to be removed to be cut at natural joints or stud centres. I.e. 600mmc/c wide to allow for easier reinstatement. 4) Allow to reinstate to match existing upon completion
35 | Wall internal (etc) | Fire | Buildup determination Staircase | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Section of wall element to be removed to be cut at natural joints or stud centres. I.e. 600mmc/c wide to allow for easier reinstatement. 4) Allow to reinstate to match existing upon completion
36 | Wall internal (etc) | Fire | External columns (mid room) | As Item 13
37 | Wall internal (etc) | Fire | External columns (corner) | As item 14
38 | Wall internal (etc) | Fire | External columns (internal columns) | As Item 13 & Item 14
39 | Wall internal (etc) | Fire | External columns (diagonal bracing) | As item 21
40 | Wall internal (etc) | Quality | Damp - Areas of occurance | 1) Damp within Head teachers office. 2) Exact extent of opening up to be agreed following survey of dampness extent. 3) Allow to remove constuction to window head and above ceiling. 4) Allow to reinstate to match existing upon completion.
41 | Wall internal (etc) | Fire | Electrical outlets | Identify 3no. locations per floorin varying types of wall construction as noted on the internal wall compartmentation GA's. 1) Identify and isolate electrical circuit prior to removing electrical face plates 2) Unscrew and pull forward electrical accessory faceplate to expose backbox and Prescence of putty pad without disconnecting electrical connections. 3) Where presence or absence of putty pad is not obvious, full disconnection of electrical accessory may be required. 4) Allow to reinstate to match existing upon completion
42 | Wall internal (etc) | Fire | Plant room | 1) Within specified location, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
43 | Wall internal (etc) | Fire | PE Store / Caretakers Store | 1) Within specified location, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
44 | Wall internal (etc) | Fire | FD frame to partition abutment | Identify 2no. Locations per floor. 1) Within specified location gently pry off architrave from full perimeter of door to both faces 2) Allow to reinstate to match existing upon completion including decorations and mastic.
45 | Wall internal (etc) | Fire | FD Ironmongery bedding / intumescent / seals | To the same locations as identified in Item 44 above: 1) Within specific location remove hinge one at a time to check for interdens behind hinge. 2) Remove and replace hinges one at a time to prevent need for full removal and re-hanging of door 3) Remove all other ironmongery from door including, handles, locks and latches from frame to check for specification and installation of interdens
46 | Ceilings (inc. H/L) | Quality | Damp - Areas of occurance | N/A
47 | Ceilings (inc. H/L) | Fire | Corridor cross doors (both sides) | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
48 | Ceilings (inc. H/L) | Fire | Corridor dead end | 1) Within specified location widespread removal of ceiling tiles to enable check of compartmentation. 2) Above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
49 | Ceilings (inc. H/L) | Fire | Kitchen | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
50 | Ceilings (inc. H/L) | Fire | Plant room | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
51 | Ceilings (inc. H/L) | Fire | PE Store / Caretakers Store | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
52 | Ceilings (inc. H/L) | Fire | Damper framing deconstruction | 1) In location to be identified, remove and set aside ceiling tiles 2) Depending on installation detail cut out fire stopping around penetration to confirm build up of damper framing. 3) Allow to reinstate to match existing upon completion
53 | Ceilings (inc. H/L) | Fire | Compartment lines (ad hoc) | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
54 | External | Quality | Below Gnd drainage - CCTV and Report (dia, fall, connection, etc) | By Others.
55 | External | H+S | Soil / GI - Playing Fields | By Others.
56 | External | H+S | Tarmac - Access zones | By Others.
57 | Wall internal (etc) | Quality | MDF joint panel cover strips. | Covered under other Items
58 | Floor | Quality | Undulating sprung floor. | 1) In specified location take up area of floor finish to establish sub base. 2) Core may be required if removing floor finish does not identify defect.
59 | External RWP/Gulley | Quality | Capacity/Debris | 1) Complete all necessary pre excavation checks for services etc 2) Excavate around gulley to expose gulley pot. 3) Remove cover plate from RWP to inspect. 3) Allow to back fill and reinstate as existing
NOTES FOR INSPECTION
At each opening up location Kier are to:
Photograph prior to opening.
Photographs at each stage of opening up.
Identify and products names on materials.
Identify any concerns in relation to materials and/or the method of construction or detail.
At each opening ip location AECOM will:
Photograph the construction in detail.
List construction Build Up
Identify materials/brands/manufacturers
Measure section through opened are to produce section drawing.
Record who is present duing inspection.

## Sheet2
Buckton
Haygrove
SFG
All