### THE OFFICE FOR NUCLEAR REGULATION

STATEMENT OF SERVICE REQUIREMENT FOR THE PROVISION OF SUPPORT ON PROBABILISTIC SAFETY ANALYSIS FOR THE GDA OF THE UK AP1000

1	BACKGROUND TO THE PROJECT

1.1	In December of 2011 ONR formally completed Step 4 of the Generic Design Assessment (GDA) of Westinghouse Electric Company’s (WEC) UK AP1000 reactor design.  WEC is the Requesting Party for the UK AP1000 GDA (referred to as “the RP” in this specification).

1.2	Step 4 of the GDA was an in‐depth ONR assessment of the safety case evidence for a generic site envelope undertaken in accordance with the regulatory regime of Great Britain.  The general intention of Step 4 was to move from the safety arguments and system level assessment of Step 3 to a fully detailed examination of the available evidence, on a sampling basis.  The aim of Step 4 was to identify any fundamental safety or security shortfalls and allow ONR to come to a judgment of whether (or not) a Design Acceptance Confirmation (DAC) or Interim Design Acceptance Confirmation (iDAC) can be issued (see http://www.onr.org.uk/new-reactors/ngn03.pdf).

1.3	On completion of Step 4 ONR’s assessment was largely complete and the generic design was found to be generally acceptable but some nuclear safety, security or environmental issues remained.  These outstanding issues were identified as GDA Issues, for which the Requesting Party will be required to provide credible resolution plans. ONR was satisfied with the resolution plans and was therefore able to issue an iDAC for the AP1000 generic design.

1.4	These GDA Issues are considered by ONR as significant, but resolvable, and require resolution before nuclear island safety-related construction of such a reactor could be considered.  ONR’s Step 4 PSA assessment can be found at http://www.onr.org.uk/new-reactors/ap1000/reports.htm.

1.5	Following the issue of the iDAC in 2011, WEC paused their GDA related activities.  In August 2014, WEC recommenced GDA in order to close-out the outstanding GDA Issues.  During this close-out stage, which is the subject of this statement of service requirements, the Requesting Party will submit additional information in response to all the GDA Issues; and the regulators will undertake sufficient assessment to be able to judge whether this additional information adequately addresses all the GDA Issues.  Following the satisfactory completion of the GDA Issue close-out stage, the regulators may then be able to issue a final DAC.

1.6	During the close-out phase ONR will assess the information supporting the GDA Issues by conducting reviews of an appropriate depth, on a sampling basis, of the PSA model, data and supporting analyses, to confirm that the claims and arguments are underpinned by robust evidence.

1.7	ONR expects to start the close-out stage GDA on 1st April 2015 and complete it at the end of 2016.

- SCOPE OF THE SERVICES REQUIRED

2.1	The Technical Support Contractor (TSC) is required to provide technical support to ONR, during the close-out phase of GDA, to review the UK AP1000 PSA.  There are three PSA review tasks which need to be completed.  These are:

a)	A focussed review of the “base case” PSA for internal hazards at power.  This is the PSA that WEC will modify to address the two GDA PSA Issues;

- Review of the manner in which the base case PSA has been updated to address GDA Issue GI-AP1000-PSA-01 (Success Criteria);

- Review of a substantially updated fire PSA to address GDA Issue GI-AP1000-PSA-02 (Fire PSA).

  - ONR considers that the benefits from task 1) the focussed review of the base case PSA will be valuable for the review of how the overall PSA has been updated with revised success criteria and risk modelling to address GDA Issue PSA-01 (Success Criteria).  It is this updated risk model that will also form the basis for the fire PSA.  Hence TSCs are requested to provide proposals for:

- Tasks 1), 2) and 3) together, or;

- Tasks 1) and 2) together, or;

- Task 3) separately from the other two tasks.

2.3	Document Submissions to ONR to Support Tasks 1), 2) and 3)

- The scope of the documentation which will be submitted to ONR for each of the three tasks is as follows.

- Task 1) focussed review of the base case PSA

- This will be the CAFTA model and documentation for the internal events at power PSA that WEC will use to address the two GDA PSA Issues.  It may have been updated in various ways since ONR completed its Step 4 PSA assessment in 2010.

- Task 2) GI-AP1000-PSA-01 (Success Criteria):

- The Success Criteria and risk modelling methodology.

- The identification of initiating events and their grouping.

- Supporting technical work for the risk models including the revised Success Criteria analysis to the Level 1 and Level 2 PSA and the plant damage states.

- The Level 1 and Level 2 PSA for internal initiating events during operation at power.

- The overall risk evaluation: quantification, sensitivity and uncertainty analyses, interpretation of the PSA results and a gap analysis.

- A discussion of the risk significance of plant modifications made since ONR completed its Step 4 PSA assessment.

- For the internal events shutdown plant state PSA it is anticipated that the application of AP1000 specific performance analysis will be presented for a few initiating events/accident sequences.

- Task 3) GI-AP1000-PSA-02 (Fire PSA):

- The Fire PSA methodology.

- The plant area partitioning and fire equipment selection analysis.

- The fire ignition frequencies and cable impact analysis (e.g. hot short analysis).

- The Human Reliability Analysis (HRA) and the Main Control Room (MCR) fire analysis.

- Level 1 and Level 2 PSA for the initiating event of internal fire during operation at power.

- Supporting technical work for the risk models including the fire analysis calculations, for example CFAST and potentially the FDS or NRC Fire Dynamics Tools.

- Overall risk evaluation: quantification, sensitivity and uncertainty analyses, interpretation of the PSA results, ALARP analysis and a gap analysis.

- A discussion of the risk significance of plant modifications made since ONR completed its Step 4 PSA assessment.

2.4	More Detailed Scope of Service to Support Tasks 1), 2) and 3)

- The more detailed scope of services required during the GDA close-out stage for PSA-01 (Success Criteria) and PSA-02 (Fire PSA) includes:

- Task 1) focussed review of the base case PSA.

- Undertake a high level review of the internal events at power PSA with respect to the findings of the ONR Step 4 PSA assessment.  This is to understand the overall standard and status of the base case PSA, and whether any significant updates of the PSA have been made which would influence ONR’s Step 4 observations.

- Task 2) PSA-01 (Success Criteria).  This aspect of the PSA has previously been assessed in Step 4 of the GDA process.  The scope of work is therefore not to undertake a review from “scratch” but to address the adequacy of the technical work used to update the PSA to address ONR Step 4 assessment comments on success criteria.  For this project the PSA will be updated with success criteria specific to the AP1000 design - compared with the previous version of the PSA in which AP600 success criteria have been read across to the AP1000 design.  This has the potential to have significant implications across the whole of the internal events at power PSA.  Hence the TSC will need to cater for a review sufficient to fully understand the application of the updated AP1000 success analysis to the PSA.

- Review of the methods, and their implementation, upon which the RP has based its revised success criteria analysis and updated its risk models.  Any review of the human reliability analysis should be undertaken together with the GDA human factors team.

- Review of the updated success criteria analysis for the UK AP1000 PSA for internal events at power, and its suitability for use in the PSA.  This should be done in coordination with the ONR fault studies team.  The MAAP code is to be used by the RP for the revised success criteria analysis.  MAAP4 was used for the previous version of the PSA.  Should MAAP4 be used by the RP to update the success criteria, review of its validation status will not be needed, however re-familiarisation will be, including the implications for the revised PSA.  The review should cater for the potential that the RP updates the success criteria using the MAAP5 computer code.  If so, a technical view on the validation status of MAAP5 will be needed to address the experimental and benchmarking exercises undertaken, and conclusions presented on the implications for the revised PSA.  For example, comment on nodalisation and the use of the code within its capabilities.  The codes LOFTRAN and CENTS may also be used by the RP to supplement the use of MAAP.

- The scope of the risk models to be reviewed are LOCAs, Transients, Steam Line Break, SG Tube Rupture and Anticipated Transient Without Scram (ATWS).  The review should concentrate on the changes made to the base case risk model to accommodate the revised success criteria (see Task 1 above).  The review should be sufficient to provide technical comment on the following topics (see Resolution Plan for GI-AP1000-PSA-01):

  - The assumptions and limitations that apply.

  - The identification and grouping of initiating events.

  - The timelines and the links to the relevant procedures and appropriate clues for operator action.

  - The time windows for operator action and their documentation.

  - Sufficiency of the thermal-hydraulic and neutronic analysis to cover all the variety of accident sequences that may arise.

  - The minimum equipment requirement and performance standard for success.

  - The adequacy of any changes to the accident sequence modelling and the associated system analysis.

  - The adequacy of any updated analysis of the reliability data analysis: data for initiating events frequencies (internal initiating events during operation at power), component failure probabilities and unavailabilities, common cause failure probabilities, probabilities of consequential events.

  - Any conservatisms in the analysis are presented and their impact is understood and justified.

  - The auditability and traceability of the analysis, and the standard of documentation provided.

- The TSC should plan for some in-depth spot checks of models and data to check how those methods and techniques have been applied by the RP in practice.  Up to five or six initiating events would be appropriate.

- The review work above should be developed to provide comments on the adequacy of the PSA to support the overall demonstration for the safety of the AP1000 plant:

  - Comment on the gap analysis which presents the PSA results from the revised success criteria work and compares this with the PSA results from the previous PCSR.

  - Comment on the impact of the risk significant design changes on the PSA.

  - Comment on the significance of changes to the PSA with respect to ONR numerical targets 7, 8 and 9 of ONR’s Safety Assessment Principles (SAPs).  This should take into account the gap analysis and the RPs presentation of risk significant modifications to the plant.

  - Comment on the adequacy of the updated PSA to support an ALARP assessment for the PCSR.

- The TSC should plan to support ONR inspectors at workshops and meetings with the RP in the UK and US.

- Task 3) PSA-02 (Fire PSA).  This aspect of the PSA has previously been assessed.  However, ONR comments from its Step 4 assessment can only be addressed by a substantial update of the previous fire PSA.  Hence although the scope of work may not require a review from “scratch”, it will need to cater for this eventuality.

- Review of the fire PSA methodology documents upon which the RP has based its revised fire PSA, and the implementation of these methods.

- Review of the preparatory work for the Fire PSA.  This includes the plant partitioning into fire compartments, the selection of fire initiators and fire initiating event frequencies, the fire accident sequences, components and failure modes to be modelled in the Fire PSA.

- Review of the cable analysis which identifies how fire-induced failure could affect equipment relevant to the fire PSA.

- Review the adequacy of the fire analysis used to support the Fire PSA.  The code CFAST is most likely to be used although other codes such as FDS or NRC Fire Dynamic Tools may be used.  This should be undertaken together with ONR’s internal hazards team.

- Review of the Main Control Room (MCR) analysis.  This will assess the risk from fires originating inside the control room, including abandonment and non-abandonment scenarios.

- Review the approach used to identify and include human failure events in the Fire PSA.  Any review of the human reliability analysis should be undertaken together with the GDA human factors team.

- The Fire PSA will be based on a staged approach in which the analysis will be progressively refined according to initial conservative results.  This approach is being used to identify the risk significant areas of the plant for which more detailed analysis will be undertaken.  This will enable the ALARP assessment to be focussed appropriately.  The TSC should work with ONR to advise upon the manner in which the Fire PSA should be progressively developed.

- Review of the adequacy of the UK AP1000 Level 1 and Level 2 fire induced risk models for internal events at power in coordination with ONR PSA team.  The review should be sufficient to provide technical comment on the following topics (see Resolution Plan for GI-AP1000-PSA-01):

  - The assumptions and limitations that apply.

  - The timelines and the links to the relevant procedures and appropriate clues for operator action.

  - The time windows for operator action and their documentation.

  - Sufficiency of the fire analysis to cover all the variety of accident sequences that may arise.

  - The incorporation of the cable analysis, human factors analysis and fire induced failure of components into the Fire PSA to derive minimum equipment requirements and performance standards for success.

  - The logic of the accident sequence modelling and the associated system analysis.

  - The adequacy of the reliability data analysis (given the influence of fires on equipment): data for initiating event frequencies (internal initiating events during operation at power), component failure probabilities and unavailabilities, common cause failure probabilities, probabilities of consequential events.

  - Any conservatisms in the analysis are presented and their impact is understood and justified.

  - The auditability and traceability of the analysis, and the standard of documentation provided.

- The TSC should plan for some in-depth spot checks of models and data to check how those methods and techniques have been applied by the RP in practice.

- The review work above should be developed to provide high level comments on the adequacy of the fire PSA to support the overall demonstration for the safety of the AP1000 plant:

  - Comment on the gap analysis which presents the PSA results from the revised success criteria work and compares this with the PSA results from the previous PCSR.

  - Comment on the impact of the risk significant design changes on the fire PSA.

  - Comment on the overall risk evaluation: quantification, sensitivity and uncertainty analyses, interpretation of the PSA results, significance of changes to the PSA with respect to ONR numerical targets 7, 8 and 9 of ONR’s Safety Assessment Principles (SAPs).

  - Comment on the fire PSA ALARP assessment and the adequacy of the updated PSA to support an ALARP assessment for the PCSR.

  - Comment on the Living PSA procedure which should permit the Fire PSA to be updated as further design information becomes available.

- The TSC should plan to support ONR inspectors at workshops and meetings with the RP in the UK and US.

- CONSTRAINTS

3.1	Constraints on guidance to be used by the TSC for the review of the UK AP1000 PSA:

- ONR’s Safety Assessment Principles (SAP)

(http://www.onr.org.uk/saps/saps2014.pdf).

- ONR’s Technical Assessment Guide (TAG) on PSA

(http://www.onr.org.uk/operational/tech_asst_guides/ns-tast-gd-030.pdf).

- IAEA’s specific safety guide (SSG) for Level 1 PSA, SSG-3;

- IAEA’s SSG for level 2 PSA, SSG-4; and

- Any additional relevant national and international PSA/PRA (Probabilistic Risk Assessment) standards and authoritative guidance as identified by the TSC, in agreement with ONR.  It should be noted that the RP is making use of the ASME PSA standard (ASME/ANS RA Sa 2009) and the fire PSA methodology (NUREG/CR-6850).

  - Constraints related to the TSC’s technical capabilities:

- The TSC should put forward a team with knowledge of the AP1000 (PWR) technology and safety analysis.

- The TSC should put forward a team with well-developed skills and experience of providing independent technical review.

- The TSC should put forward a team with detailed understanding of, and extensive experience in, light water reactor PSA (expert level) and an excellent working knowledge of current international PSA standards. Experience in regulatory reviews and/or IAEA IPSART missions would be desirable (but not essential).

- The TSC should have, or be able to obtain a licence for, and should have experience using, the relevant PSA computer code to be used by the RP, which will be CAFTA for PSA-01 (Success Criteria) and PSA-02 (Fire PSA).

- The TSC should ideally have a licence or experience of FRANX and FTREX for PSA-02 (Fire PSA).  However, this is desirable (but not essential).

- The TSC should have knowledge and experience of understanding and interpreting the output from the relevant performance analysis computer codes to be used by the RP, which will be MAAP for PSA-01 (Success Criteria), and CFAST, FDS or NRC Fire Dynamics Tools for PSA-02 (Fire PSA).

  - Scheduling constraints – RP’s schedule of PSA deliverables: The RP’s expected delivery programme for the PSA-01 (Success Criteria) and PSA-02 (Fire PSA) work is summarised in Appendix 1 and Appendix 2 respectively.  Either one or both of these programmes (but see paragraphs 7 and 8 above) should be reflected in the tender submissions and, ultimately, in the TSC’s overall project programme. However, the TSC’s programme of work may need to be adjusted later in the GDA close out phase to align it with the RP’s final PSA delivery schedule.  A pragmatic and flexible approach will need to be adopted by the TSC to deal with this, both technically and contractually.

  - Scheduling constraints – meetings with the RP: ONR anticipates that a number of meetings with the RP will require participation of TSC’s staff; for example:

- 20 teleconferences per year (2 hours).

- 2 technical workshops for the PSA-01 (Success Criteria) project.  One or both of these may be held in the US or the UK (5 days each).

- 2 technical workshops for the PSA-02 (Fire PSA) project.  One or both of these may be held in the US or the UK (5 days each).

3.5	A tentative schedule of Technical Workshops and meetings between ONR and the RP during the GDA close-out phase has been outlined.  Meetings will usually be scheduled on the 2nd week of the month.  The exact dates and locations of the meeting are still to be confirmed. TSC participation is likely to be needed in technical workshops potentially planned in June to September 2015 for the PSA-01 (Success Criteria) project and June 2015 to February 2016 for the Fire PSA (PSA-02) project.  These workshops will be held at either ONR Headquarters, Bootle UK or Westinghouse Offices, Cranberry, Pittsburgh US.  A pragmatic and flexible approach will need to be adopted by the TSC to deal with the project needs in terms of meeting dates, attendance and attendees.

  - Timing constraints – for both PSA-01 and PSA-02 projects:

- Kick-off meeting between ONR and TSC: within 10 working days of Contract Award.

- PSA-01 (Success Criteria) will be completed in six stages and PSA-02 (Fire PSA) will be completed by the RP in five stages.  These are:

  - Stage 0 (Task 1 only).  Focussed review of the base case PSA.  It is anticipated that the base case risk model will be provided to ONR in March 2015.  TSC review should be available within 2 months of contract award and before the workshops with WEC begin.

  - Stage 1.  The first stage is initial project technical work upon which the risk models will depend.  These deliverables will be provided to ONR between March to April 2015.

  - Stage 2.  A gap in formal deliverables to ONR of for the RP to work up the risk models and supporting work.  For PSA-01 (Success Criteria) this is anticipated to be June to September 2015.  For PSA-02 (Fire PSA) this is anticipated to be July 2015 to February 2016.  During this stage ONR anticipates that a number of workshops will be held with the RP to monitor technical progress and provide clarity on ONR expectations.

  - Stage 3.  This stage includes the delivery of the risk models, quantification, gap analysis and interpretation of the results.  For PSA-01 (Success Criteria) this is anticipated to be September 2015.  For PSA-02 (Fire PSA) this is anticipated to be March 2016.   A significant suite of documents will be provided as one “deliverable”.

  - Stage 3a.  Focussed and high level review of the application of AP1000 specific success criteria to two shutdown plant state initiating events.  The scope of this work will be agreed between ONR and WEC as the project proceeds.  The delivery of this work is currently anticipated as September 2015.  However, this is subject to negotiation.

  - Stage 4.  Presentation and discussion of ONR findings to the RP.  The RP will update a few key documents and resubmit these to ONR.  The TSC will be requested to provide a high level review of the revised RP documentation. This process is anticipated to take place between September 2015 and January 2016 for PSA-01 (Success Criteria) and April to August 2016 for PSA-02 (Fire PSA).

  - Stage 5.  Provision of TSC reports to ONR to complete the project.  TSC reports will be needed by February 2016 for PSA-01 (Success Criteria) and September 2016 for PSA-02 (Fire PSA).

  - Timing constraints for PSA-01 (Success Criteria) project (see Appendix 1):

- Stage 1 will include delivery to ONR of the Success Criteria/Accident Sequence Guidebook, the Initiating Event Analysis Notebook and the MAAP parameter file calculation note.  Last complete and quality assured TSC’s final report would be expected to ONR by June 2015 before the workshops with WEC begin.  This would enable transmission of ONR findings early in the RP’s work to construct the risk models.

- Stage 2 will include a number of workshops in the UK or US.  The dates and content of which will be determined as the project proceeds.  Technical advice notes to ONR to influence the agenda of the workshops are expected within 2 weeks of the workshop starting date.

- Stage 3 will include delivery to ONR from the RP of the Success Criteria, LOCA, Interfacing System LOCA, Steam Line Break, Steam Generator Tube Rupture, Anticipated Transient Without Scram risk models, the Quantification/results, gap analysis and qualitative assessment of design changes analysis.  The high level shutdown PSA work will also be delivered in Stage 3.  This work will be in separate deliverables but submitted to ONR together.  Working drafts of the TSC’s assessments should be shared with ONR periodically.  The complete and quality assured TSC’s draft report is required for the start of February 2016.

- Stage 4 will begin with the submittal of the revised deliverables to ONR.  The TSC will have 4 weeks to provide a complete and quality assured TSC draft report to ONR by the start of February 2016.

- Stage 5.  The complete and quality assured TSC’s draft report required before the start of January 2016.  The last complete and quality assured TSC’s final report required before the start of February 2016.

- End of the project: May 2016.

  - Timing constraints for PSA-02 (Fire PSA) (see Appendix 2):

- Stage 1 will include delivery to ONR of the fire PSA guidebook, plant partitioning and fire initiating event frequency analysis, the fire equipment selection analysis and the cable fire analysis deliverables.  Last complete and quality assured TSC’s final report would be expected to ONR by July 2015 before the workshops with WEC begin.  This would enable transmission of ONR findings early in the RP’s work to construct the risk models.

- Stage 2 will include a number of workshops in the UK or US.  The dates and content of which will be determined as the project proceeds.  Technical advice notes to ONR are expected within 2 weeks of the workshop completion date.

- Stage 3 will include delivery to ONR from the RP of the fire Human Reliability Analysis, Main Control Room fire analysis, fire risk models, the quantification and results, the fire ALARP analysis, the qualitative discussion of design changes on fire risk and the living PSA procedure for the fire risk model.  This work will be in separate deliverables but submitted to ONR together.  The complete and quality assured TSC’s draft report is required before the end of June 2016.

- Stage 4 will begin with the submittal of the revised deliverables to ONR.  The TSC will have 4 weeks to provide a complete and quality assured TSC draft report to ONR before the end of August 2016.

- Stage 5.  The complete and quality assured TSC’s draft report required before end of July 2016.  The last complete and quality assured TSC’s final report required before end of August 2016.

- End of the project: December 2016.

  - Security constraints:

- Much of the RP’s PSA material and, as a consequence, the TSC’s review reports will include information of a sensitive nature and attract the UK protective marking OFFICIAL – SENSITIVE. The received and produced data will therefore need to be handled appropriately.

- Work cannot commence until the required security clearances of individuals working on the project have been established and the TSC’s IT systems have been demonstrated to be suitable for the protective marking applied to the information.

  - Conflict of interest constraints: The TSC should not have previously supported the RP (directly or indirectly), in developing or reviewing the UK AP1000 PSA.  Any support to the RP or their suppliers must be declared. Tenderers must complete Schedule C of the ITT pack.

  - Constraints related to the performance of the TSC: at the end of Stage 2 a review will be conducted of the quality and timeliness of the TSC’s work and interactions with ONR and the RP to inform a decision of whether the contract should proceed to the next Stage 3 of the project the assessment of the suite of risk model deliverables.

  - Other constraints – distribution of the TSC’s reports and usage of the TSC’s information included in the UK AP1000 review reports:

- It is ONR’s intention to provide the TSC’s reports to the RP for confirmation of factual accuracy.

- Interim outcomes of the TSC’s review will be used by ONR, if appropriate, to inform the preparation of Regulatory Observations (and/or Regulatory Issues if serious shortfalls are identified which could prevent provision of a design acceptance confirmation, DAC) requesting the RP to make improvements to the UK AP1000 PSA during GDA. The final outcome of the TSC’s review will be used by ONR to raise, if appropriate, GDA Issues and/or GDA Findings at the end of the close-out phase.  In addition, ONR will report on the progress and outcome of this work in its status of assessment report at the end of the GDA process, in the close-out PSA Assessment Report, and, as appropriate, in the GDA quarterly reports, all expected to be published.

- OBJECTIVES

4.1	In summary, the overall objective of this work is to provide technical support to ONR, during the GDA close-out project, to review the UK AP1000 PSA. This will be done via:

- Review of the RP’s PSA submissions (documentation, models, databases and supporting analyses), against ONR’s SAPs, ONR’s TAG on PSA and international good practice.

- Report to ONR any shortfalls identified during the review of the UK AP1000 PSA and comment on their significance.  Evaluate the importance of the review findings and their potential impact on the PSA results.

- Determine the adequacy of the PSA to inform the understanding of risk from the generic plant and the further development of the design.  Assist in the clarification of the level of regulatory risk in passing the start of construction of the nuclear “island”.

- Support ONR (including any required preparation) during teleconferences, videoconferences and/or face-to-face meetings (in the UK and US) with the RP to discuss progress of the reviews of the various PSA tasks, findings from the reviews, emerging issues, etc., and/or to request additional information and/or analysis from the RP.

- Draft queries and/or observations to request additional information and/or analysis from the RP (to be formally submitted by ONR) and advise ONR on the adequacy of the RP’s responses.

- Define the scope of the assessment required by, or in coordination with, other GDA teams, and support ONR to coordinate these assessments.  This should cover technical topics for which the TSC does not provide expertise and/or topics that the TSC consider should be reviewed (for inputting into the overall PSA assessment) by other specialist teams in GDA to ensure consistency with their individual reviews.

  - The required output from this work is:

- Technical reports for the PSA review work for PSA-01 (Success Criteria) and/or PSA-02 (Fire PSA) depending on the scope of the contract agreed with the TSC.

- A draft and final report for PSA-01 and PSA-03.  Each of these reports may have two parts: part 1 will document the review of methodology, limitations and assumptions used by the RP.  Part 2 will document the reviews of models, data and, supporting analyses and results, as relevant.  However, the scope and content of the reports can be discussed with ONR to reflect the needs of the project.

- A summary report documenting the overall conclusions from the review of the UK AP1000 PSA.

- Technical review notes as agreed with ONR during Stages 1 and 2 of the PSA-01 (Success Criteria) and PSA-02 (Fire PSA) projects.

- Drafting of technical questions for ONR to send to the RP as the review progresses.

- Provide support to ONR for interactions with the RP as required.

- Notes and minutes of meetings as follows: project kick-off meeting, progress teleconferences and/or face-to-face meetings, and technical workshops between ONR, the RP and the TSC, as required.

- Project management – monthly progress reports giving an update on progress against the project plan and breakdown of spend against the budget.  This should include a short summary of progress and expenditure within month and cumulative, and per task and each team member.

5	TENDER SUBMISSIONS

5.1 	Tenderers proposals must clearly state which of the work stages stated in Paragraph 2.2 they are bidding for.  Tenderers must clearly define within their bid each individual work package (i.e. Stage 1, 2 and 3) and the proposed cost of each stage.  Tenders that do not comply with the above may be eliminated from the process.  Tenderers are also invited to offer any cost reductions available for award of all 3 work packages.

5.2	Tender submissions are required to provide all of the following:

- Clearly address all aspects of the specification (including objectives, scope and constraints).  It is noted that tenderers are invited to address either or both PSA-01 (Success Criteria) and PSA-02 (Fire PSA).

- Details of the project team members, including grades and rates and short curriculum vitae (CV).  Also:

- Experience of the project team relevant to each of the tasks. This should include a brief description of examples of the work undertaken by the individual that provides evidence of adequate experience to undertake the assigned task.

- Level of experience of the TSC using CAFTA and the fire PSA specific performance analysis and PSA codes CFAST, FDS, NRC Fire Dynamics Tools.

- Details regarding the experience of the project team on safety analysis for PWR technology (indicate if the project team has specific experience on the AP1000 design).

- Details of the project team with regards to undertaking independent technical reviews.

- Experience in regulatory reviews and/or IAEA IPSART missions would be desirable (but not essential).

- A licence or experience of FRANX and FTREX for PSA-02 (Fire PSA).  However, this is desirable (but not essential).

- Explain how the aims and scope of the work are to be addressed, and the proposed approach. This should include:

- Identification of the required tasks with the number of days required for each task and timescales, including details of who will undertake each of the tasks.

- Identify the anticipated engagement with ONR, including any progress meetings.

- Confirm that the TSC has, or will be able to obtain a licence for the relevant PSA computer code to be used by the RP, which is likely to be CAFTA for both PSA-01 (Success Criteria) and PSA-02 (Fire PSA).

- It would be advantageous if the TSC is also a user of the fire analysis codes CFAST, FDS, NRC Fire Dynamics Tools, although independent analysis by the TSC using these codes is not anticipated at this time.  Tenderers must confirm the above (desirable, not essential).

- Provide a detailed breakdown of all proposed costs associated with this work:

- total costs should be presented per financial year (ONR financial year starts in April);

- provide a schedule of invoices;

- costs should be broken down per month;

- provide an estimate of travel and subsistence costs;

- Provide a description of any other costs with an explanation.

6	CONTRACT MANAGEMENT

6.1	ONR will require to be kept updated about progress and delivery of the required work via monthly meetings, to include a contract start-up meeting at ONR’s offices at Bootle. Subsequent progress meeting should be arranged with the ONR Project Office and can be held at ONR’s office in Bootle, or the contractor’s premises.

- EVALUATION

7.1	Tenders will be evaluated across three stages of the procurement process, as detailed in the Instructions to Bidders document which accompanies this Statement of Service Requirements (Schedule A) and the Evaluation Criteria and scoring mechanism outlined in Schedule B.

Appendix 1: RP’s PSA-01 (Success Criteria) DELIVERY PROGRAMME

- The RP’s current expected delivery programme for the PSA-01 (Success Criteria) project is summarised below (only main milestones are listed):

| - Expected dates | - Main milestones | - Example of the information that will be submitted by the RP |
| --- | --- | --- |
| - March to April 2015 | - Stage 0 (Task 1 only) | - Focussed review of the base case PSA. The base case internal hazards at power risk model will be provided to ONR (CAFTA model plus documentation). |
| - March to June 2015 | - Stage 1 |  |
|  | - Initial project information supporting the UK AP1000 PSA for internal initiating events during operation at power. | Success Criteria/Accident Sequence Guidebook. This contains the methodologies to be used by WEC. - Initiating Event Analysis Notebook. Identification and grouping of initiating events. Initiating event quantification. Analysis of plant systems and support systems for their contribution to initiating events. The identification and frequency of interfacing systems LOCAs. - MAAP parameter file calculation note. Input data for the MAAP code. |
| - June to December 2015 | - Stage 2 |  |
|  | - Workshops in the UK and/or US. | - Gap in the delivery of work from the RP during which the RP will be producing the risk models and results. - The workshops will monitor technical progress, clarify ONR expectations and sample work produced by the RP. |
| - September 2015 | - Stage 3 |  |
|  | - Receipt of risk model work and results | - Completed risk model and documentation: at power Level 1 and Level 2 risk models: - LOCAs - Interfacing systems LOCAs - Transients - Steam Line Breaks - SG Tube Rupture - Anticipated Transients Without Scram - Supporting analysis: data justifications, HRA and systems analysis. - Success Criteria Analysis Notebook. Minimum top event requirements arising from performance analysis. - Quantification Notebook. Numerical evaluations and results. - Gap Analysis. Implications of the revised risk models on the CDF and LRF compared with the GDA Step 4 PSA results. - Qualitative assessment of Class 1 and Class 2 design changes. |
| - September 2015 | - Stage 3a |  |
|  | - Shutdown PSA submission (internal events) | - Updated high level analysis for 2 shutdown PSA initiating events using AP1000 specific performance analysis and success criteria for the shutdown plant states. The use of judgement to discuss the impact of the updated performance analysis on the remaining shutdown PSA initiating events. - The delivery date for Stage 3a is an estimate. The scope and delivery date for this work will be agreed between ONR and WEC as the project proceeds. |
| - September 2015 to - January 2016 | - Stage 4 |  |
|  | - Discussion with the RP and potential up-issue of RP reports | - Presentation of assessment results to the RP. - Potential for the RP to up-issue reports with subsequent RP high level review of the revised RP documents. |
| - February 2016 | - Stage 5 |  |
|  |  | Completion of the RP’s draft and final reports and their provision to ONR. |

Appendix 2: RP’s PSA-02 (Fire PSA) DELIVERY PROGRAMME

- The RP’s current expected delivery programme for the PSA-02 (Fire PSA) project is summarised below (only main milestones are listed):

| - Expected dates | - Main milestones | - Example of the information that will be submitted by the RP |
| --- | --- | --- |
| - April to July 2015 | - Stage 1 |  |
|  | - Review of initial project information supporting the UK AP1000 PSA for the fire PSA. | Fire PSA Guidebook. This contains the methodologies to be used by WEC. - Plant partitioning and fire equipment selection analysis. - Cable fire analysis. - Fire initiating event frequency analysis. |
| - July 2015 to February 2016 | - Stage 2 |  |
|  | - Workshops in the UK and/or US. | - Gap in the delivery of work from the RP during which the RP will be producing the risk models and results. - The workshops will monitor technical progress, clarify ONR expectations and sample work produced by the RP. |
| - March to June 2016 | - Stage 3 |  |
|  | - Receipt and review of risk model work and results | - Fire Human Reliability analysis. - Main Control Room fire analysis. - Completed fire risk model and documentation: at power Level 1 and Level 2 risk models: - Supporting analysis: Fire performance analysis (e.g. CFAST/FDS) fire PSA database, data justifications, HRA and systems analysis. - Fire ALARP analysis. - Quantification Notebook. Numerical evaluations and results. - Living fire PSA procedure. - Gap Analysis. Implications of the revised risk models on the CDF and LRF compared with the GDA Step 4 PSA results. - Qualitative assessment of Class 1 and Class 2 design changes. |
| - April to August 2016 | - Stage 4 |  |
|  | - Discussion with the RP and potential up-issue of RP reports | - Presentation of assessment results to the RP. - Potential for the RP to up-issue reports with subsequent RP high level review of the revised RP documents. |
| - September 2016 | - Stage 5 |  |
|  |  | Completion of the RP’s draft and final reports and their provision to ONR. |