Supply, delivery, installation & commissioning of goods lift to mezzanine floor & removal of conveyor & work to make good mezzanine.

General Specification

Supply of goods lift to mezzanine floor with the following dimensions;

Overall Dimensions: 2800mm(w) x 3042mm(l). Additional 50mm (minimum) all round for installation if within a mezzanine void

Platform Dimensions: 2450mm(w) x 2450mm(l)

Floor Height(s):  Up to maximum of 5.2m current figures based on 3000mm finished floor level

Lifting Capacity (SWL): 1500kg Uniformly Distributed Load (Goods lift only-no passengers) carrying 8 roll cages

Maximum no.floors/lift stops:  Ground+1

Gate Configurations:  Through Car

Lift Car Sides:  1100mm sides-ply lined

Outer Gates:  2100mm

Structural Build:Quality & Reliability

Inner Gates & Lift Car:  1100mm(h) sides and barn gates. Mechanical lock mechanism. Lift car & inner gates un-lined or ply-lined as standard

Outer Gates: 2100mm(h) clad in 10G 75mm x 10mm galvanised mesh. Electrical and mechanical interlocks. Key lockable

Steel Footplates: Anchor units into position-directly onto the warehouse floor, no specialist civil works required. M16 x 180mm through-bolts in each corner

Lift Platform: Steel box section frame with anti-slip flooring

Access Ramp: 2100mm(w) x 1000m(l) 6mm durbar plate, 70mm depth-for typical roll cages or manual hand pallet trucks

Lift Shaft: Superstructure clad in 10G 75mm x 10mm galvanised mesh

Hydraulics: Single hydraulic ram-mounted in overhead ram box, Safety valve fitted to ram and powerpack

Rope Failure Devices: 2 off-1 per lifting column

Finish & Colour: All steelwork prepared and paint finished. Lift superstructure, ram box, gates and columns Graphite Grey RAL 7024

Safety Signage: Hazard, warning, operational and safety signage

Power & Electrics

Operator Controls:  Dispatch and receive system-call/send lift at each landing

Power Requirements:  415V;5.5Kw;DOL;16A type D motor rated circuit breaker. Power supply to be in the immediate vicinity of the lift installation

Electrics:  IP65 rated

Duty Cycle:  Lift speed 90mm/s

Additional work required;

Removal of existing conveyor to mezzanine floor and make good space/hole left by removal of conveyor

A site visit is recommended to assess the work required and provide an accurate quotation if ITT documents are requested in due course

Electrical works to be provided by Trust contractor