## Opt1
Section (6)
Company Name:-
| Project:- Main Kitchen Refurbishment |  |  |  | Quoted Project Costs
| Scope of works | Photos | Qty | Rate | Costs
Back Ground
1 | The Main Kitchen prepares dinners for patients right across the Hospital site and also caters for the Staff Restaurant Servery 7 days a week. All the works below will be progress while maintaining activities in the Main Kitchen. Therefore careful planning is necessary with the Restaurant Manager so works and the cooking activity's run smoothly.
2 | The Tender should be prepared to work out of normal working hours. The plan is to complete the works in the Main Kitchen in sections, therefore allowance should be made to erect hoarding tightly sealed to prevent contaminates going from the working section in the food preparation area.
3 | Tenderers will be required to complete all the works before the end of March 2017 Tenderers who can completed the works sooner will be favoured. The Works will be undertaken under the JCT minor work contracts LAD will be set at £1000/day.
4 | Scope of works
5 | Preliminaries : Site set up cost, skips etc
6 | Hygienic Wall Cladding: Drawing A Ref:- Main Kitchen Refurb, rooms -1.11, -1.12, -1.14, -1.16 Floor to Ceiling (http://www.cleanclad.net/hygienic-wall-cladding ) 2.5mm Satin white 909 to be install to manufactures specification. Wall joints to be welded. Allow for coved flooring up the wall and sealing. Allow to cover duct riser doors / Panels, Allow to remove existing ventilation grills and install new PVC grills to suit. All exposed pipe work to be hidden behind wall cladding, Allow to remove and replace equipment fitted to walls fire extinguishers, notice boards clocks etc. | P1100540 P1100535 P1100586 P1100593 P1100592 P1100572 P1100573 P1100574 P1100590 P1100565 P1100531
7 | Install wall protection: Drawing A Ref: Main Kitchen Refurb, rooms -1.03, -1.04, -1.24 Allow to install :-Aluminium Chequer Plate 2500 x 1250 X3mm Five Bar Pattern 3mm Base Thickness . Install Aluminium corner protection to suit. Allow for secure fixing. As per installation in main kitchen corridor. Walls:- above Chequer Plate to be prepared for decoration and two coats of Dulux Trade Diamond High Performance (D598) YY34 Dulux 46YY 86/166, | P1100561
8 | Trims and interior joinery:- prepare and decorate 3 coats of white gloss Dulux Quick Dry (D1043) All areas
9 | Ceilings: Drawing B Ref: Main Kitchen Refurb, rooms -1.03, -1.04, -1.11, -1.12, -1.14, -1.16, -1.23, -1.24, -1.25 Prepare and install new suspended clean room grid system using Armstrong Parafon Hygien 9702M 600 x 600 x 18mm ceiling tile | P1100589 P1100580 P1100568
10 | Allowing to supply and install new ceiling ventilation Grills | P1100536
11 | Allowing to cut in Smoke Detectors, Light sensors switches
12 | Lighting : Drawing B Ref: Main Kitchen Refurb rooms -1.03,-1.04, -1.11,-1.12, -1.14. -1.16. -1.24. -1.25. -1.23 :- Allow to remove existing light system and install new LED lighting, Allow for light switching alteration and relocation, new wiring and install:- JCC LED Panel Light JC71276 in Cool White. Allow to install LED lighting with Emergency lighting at all Kitchen exit routes. | P1100589
13 | Electrical : Allow for the rewiring of power and lighting back to the consumer unit and the replacement of metal power socket outlets and metal light switches using MK fittings. throughout the Main Kitchen. | P1100532 P1050959 P1050954 P1100575
14 | Ventilation: Drawing A Ref:- Main Kitchen Refurb, rooms -1.11, -1.12, -1.14, Allow to upgrade ventilation panel. (Note RJ Heating to carry out ventilation repairs in main plant room.) when replacing ventilation grills use this opportunity to access the duct work and clean. | P1050903
15 | Flooring : Drawing C Ref:- Main Kitchen Refurb, Allow for Polysafe Verona Horizon Blue 5208 w/r 5208 in Rooms -1.02. -1.05, -1.13, -1.26. -1.25. -1.23. -1.21, -1.22 Allow for Polysafe Modena PUR Jetstone 4045 in Restaurant Servery rooms -1.16, -1.17 Allow for Polysafe Ultima Bluestone 4390 Main Kitchen and trolley bay and infront of counter in servery:- rooms -1.11, -1.12, -1.03, -1.04 Allow for the removal of the existing floor covering and prepare the floor to accept a New Heavy Duty Polyflor safety floor :Polysafe Ultima Colour Pattern to be confirmed (TBC).Particular attention should be made to the floor grating around the cooking area.as this in the past has come away. Tenderer to confirm method of jointing and laying coved upstands to be tappered off. | P1100543 P1100544
16 | Fat and Grease Traps :- Allow to install Fat Traps x 3 Allow to lift grill covers and clean out gullies Throughout Main kitchen, location TBC
17 | Sandwich Prep Area: Drawing Ref:- Main Kitchen Refurb, rooms: -1.12 Allow to install cold room in Sandwich prep area ( Quotes Attached )
18 | Wash Hand Basins : Drawing A Ref:- Main Kitchen Refurb, rooms: -1.12 . Allow to supply and install 2 no. Sammic LUP-450 Free standing Wash Hand Basin (5880012) 385mm Dia Basin made of ASA304 Stainless Steel 450w x450dx850m (mm) | P1100534 P1100547 P1100533
19 | Stainless Steel Boxing : Drawing A Ref:- Main Kitchen Refurb, rooms: -1.12 Allow for the manufacture of stainless steel boxing with access to control valves and maintenance. To cover all exposed pipe work in both cooking areas | P1100541 P1100542 P1100545 P1100546
20 | Walk in Fridges : Drawing A Ref:- Main Kitchen Refurb, rooms: -1.12 Allow to remove faulty door release and replace inner door release / escape mechanisms on two No. walk in fridges Allow to make good skirting, and decorate internally. | P1100555 P1100556 P1100557 P1100558
21 | Food Waste Disposal : Drawing Ref:- Main Kitchen Refurb, rooms: -1.01 Allow to Decorate throughout using an anti mould paint for ceiling and walls three coats of dulux egg shell, Floor Paint use battleship Grey three coats. Remove / supply and install New external wooden door with an Aluminium NHS blue coated door with mortise lock. Allow to supply and install an Extract ventilation fan in panel above door allow for electrical wiring to suit. Allow to box in exposed pipe work. Allow to redirect waste Pipe from waste disposal machines so the waste goes directly through the wall to outside drain. | P1100562 P1100563 P1100564 P1100567
22 | Restaurant Pot Wash : Drawing Ref:-Main Kitchen Refurb, rooms: -1.14, -1.16 Allow to removing all Cupboards and base units, shelving and any other equipment fix to walls and prepare walls for the wall cladding (as part of item 1 above). Allow to supply and install 2 No. 1000mmm new base units with work top to match existing cupboards, supply and install 2 No, 1000mm wall cabinets. Allow to replace the shelving with stainless steel racking. Allow to replace / supply and install both doors Ash Vanier 30 minute fire door with vision panels and mortise locks with thumb screw on the inside. Fit Kick and Push plates. Allow to remove and relocate items from existing ceiling to be fitted to new Suspended ceiling ( Fire smoke detector) | P1100587 P1100588P1100593 P1100594 P1100595
23 | Food Trolley Bay : Drawing Ref:- Main Kitchen Refurb, rooms: -1.03 Allow to replace supply and install external Aluminium coated fire exit door with vision panel in NHS blue with push bar opening, signage. For PUSH bar to open. plus new Exit sign above door. Fitted with Kick and push plates. Allow to infill missing duct covers at high level in corner of room next to waste disposal room. Allow to secure all fan light windows before new suspended ceiling is installed. Make allowance for sky lights when installing suspended ceiling. | P1100560 P1100566 P1100570 P1100569
24 | Staff Room: Drawing Ref:- Main Kitchen Refurb, rooms: -1.02 Decoration Walls:- Dulux Trade steralshield Diamond Eggshell (D320) 2 Coats Colour TDC Doors, Trim and Interior joinery Dulux Quick Dry (D1043) 3 coats Grey
25 | Female Changing and Toilets: Drawing Ref:-Main Kitchen Refurb, rooms: -1.25 Allow to remove existing cubicles and toilets suits, Form new cubicles out of Plaster board partition walls (100mm thickness) floor to ceiling allow for new suspended ceilings, Allow for 2 new Toilets and 2 new wash hand basins. Decoration Walls:- Dulux Trade steralshield Diamond Eggshell (D320) 2 Coats Colour TBC Trim and Interior joinery Dulux Quick Dry (D1043) 3 coats Allow for new LED lighting. Remove and supply and install new ventilation extraction unit. Allow to supply and install K2 Vanity Unit Laminated , semi-Countertop specification in appendix. Allow to supply and install Mirrors 600 x 600mm. Allow to install bathroom furniture ( toilet roll holder, soap dispensers, towel holders gel dispensers). Allow to remove and supply and install New staff lockers Z -cupboards Double unit with 4 compartments Zinc Yellow RAL1018 x 4 No. | P1050892
26 | Store Room : Drawing Ref:-Main Kitchen Refurb, rooms: -1.26 Allow to supply and install new Chrome Plated steel wire mesh shelving 5 shelves 2180mm H x 910mm W x 610mm D . Allow to Decoration Walls:- Dulux Trade steralshield Diamond Eggshell (D320) 2 Coats , Doors, Trim and Interior joinery Dulux Quick Dry (D1043) 3 coats Colour TDC . sourced from Kaiser+ Kraft | P1050891
27 | Male Toilet and Changing Room: Drawing Ref:- Main Kitchen Refurb, rooms: -1.23 Allow to remove old toilet, was hand basin urinal and cubicles. Form new cubicles out of Plaster board partition walls (100mm thickness) floor to ceiling allow for new suspended ceilings, Allow for 1 new Toilet and 1 new wash hand basins. Decoration Walls:- Dulux Trade steralshield Diamond Eggshell (D320) 2 Coats Colour TBC Door, Trim and Interior joinery Dulux Quick Dry (D1043) 3 coats Grey Allow for new LED lighting. Remove and supply and install new ventilation extraction unit. Allow to supply and install K1 Vanity Unit Laminated , semi-Countertop specification in appendix. Allow to supply and install Mirrors 600 x 600mm. Allow to install bathroom furniture ( toilet roll holder, soap dispensers, towel holders gel dispensers). Allow to remove and supply and install New staff lockers Z -cupboards Double unit with 4 compartments Gentian Blue Ral 5010 sourced from Kaiser+ Kraft | P1050894 P1050895
28 | Cleaners Cupboard: Drawing Ref:- Main Kitchen Refurb, rooms: -1.22 Allow to replace 1000mm x 450mm wall unit. Decoration Walls:- Dulux Trade steralshield Diamond Eggshell (D320) 2 Coats Colour TBC Door, Trim and Interior joinery Dulux Quick Dry (D1043) 3 coats Grey | P1050896
29 | Store Room : Drawing A Ref:- Main Kitchen Refurb, rooms: -1.21 Decoration Walls:- Dulux Trade steralshield Diamond Eggshell (D320) 2 Coats Colour TBC Door, Trim and Interior joinery Dulux Quick Dry (D1043) 3 coats Grey Allow for new LED lighting. | P1050893
30 | Wheels: Sourced from Kaiser+ Kraft or other Allow to remove / supply and install trollies wheels for Kitchen Oven pedestals, Stainless steel tables, Allow for 30 number of wheels. | P1050907 P1050928 P1050929 P1050930
31 | Restaurant Servery Area : Drawing C Ref:- Main Kitchen Refurb, rooms: -1.17 Allow to lift and relocate equipment to allow for flooring to be laid.
32 | Additions
33 | Grating in Main Kitchen : Allow to replace supply and install new grating around cooking hood for ovens including new grating in washing up area. The new grating to be stainleass steel and to meet Polyflor design where the vinly overlap the grating and the mesh grating sits on top creating the seal.
34
35
36
37
38 | Sub Total |  |  |  | 0
39 | Contingency |  |  |  | 0
40 | Estimated Cost of Building Works Only Total |  |  | 0 | 0
41 | Add VAT @ 20% |  |  | 0 | 0
42
43 | New Equipment supplier
44 | Total Estimated Project Cost |  |  |  | 0
Note :Admendments in Red
( Item 15)