## Instructions
1 | Title | C22116 - HMC Seeker - ILL + MSER
2 | Mandatory Questions
Any cell boarded in RED is mandatory and requires an answer. Any cells bordered in red that do not have an answer may render your bid non-compliant.
3 | Instructions
Bidders are requested to complete all lines with a cost in tabs Annex A to Annex E. Any line without a cost attributed to it will be considered as £0.00 and any further costs incurred in the facilitation of this line will be at the cost of the Supplier. Bidders are requested to select an entry from the drop down menus provided for every Note cells in Annex A to Annex E. Bidders are requested to fill in the Total Cost line for each Annex on the respective Annex tab. Bidders shall fill in the column I with a number value only.
4 | Additional Information
Where bidders can not provide a cost or wish to provide more detail than the cell allows, they are requested to fill in a line in the Additional Information tab for each item they wish to add information against.
5 | Communications
If, for any reason, you require assistance, please email: ian.mcdermott@homeoffice.gov.uk.
6 | Declaration
I have read and understood these instructions?

## Guidance
Guidance to Bidders
Line | Requirement
1 | All quotations are to be submitted in GBP.
2 | The Bidder offering the lowest compliant submission will be selected as the preferred Bidder for contract award.
3 | All submissions must contain the mandatory requirements as per Lines 4 to 15 (inclusive) of this Guidance.
4 | Mandatory requirements that qualify the submission as compliant are;
5 | Where requested, the Bidder has submitted costs for all work line-items listed in Annexes A, B, C, D and E of the Bidding Tool provided.
6 | Where applicable, the Bidder has acknowledged all note-items listed in Annexes A, B, C, D and E of the Bidding Tool provided.
7 | Written acknowledgement, by the Bidder, to the Standard UK Government Short Form Terms and Conditions for Goods and Services (attached to the tender advert at the Contracts Finder portal reference) must be stated by the Bidder upon submission.
8 | Written acknowledgement upon submission, by the Bidder, that they have the correct insurance levels as stated in §2.1.1, §2.1.2 and §2.1.3 of the SoR.
9 | The Supplier must submit a letter, alongside this completed Workbook, stating the total costs for;
10 | Annex A;
11 | Annex B;
12 | Annex C;
13 | Annex D;
14 | Annex E; and
15 | Grand Total.
16 | Failure, by the Bidder, to adhere to Lines 4 to 15 (inclusive) may result in the submission being considered non-compliant.
17 | Failure, by the Bidder, to electronically complete the Bidding Tool may result in the submission being considered non-compliant.
18 | Unless specified as Authority supplied, all spare parts required to complete this requirement, including paint and anodes, are to be provided by the Supplier.
19 | All clarifications regarding this competition should be submitted via email to ian.mcdermott@homeoffice.gov.uk no later than 12:00pm (midday), 08 December 2021. Any clarifications received after this date will not be actioned.
20 | All submissions should be submitted by 17:00hrs, 17 December 2021.
Declaration
I have read and understood this guidance.

## Annex A
Annex A: General Requirements of Work
Annex A |  | Description | Qty | DoQ | Description of Service | Acknowledgement / Unit Price | Total Firm Cost
1 | Berthing
Note |  |  |  |  | The Supplier is to include all costs associated with berthing, shore power, rubbish removal and movements in the submitted quotation and provide the following for the entirety of the contract period.
| 1.1 | Alongside Berthing | 1 | Day | The Supplier must provide appropriately sized, secure, alongside berthing, as required, during this period of works, with a minimum depth of 1m below Low Water Spring Tides at all times.
| 1.2 | Movements | As | Req. | The Supplier must arrange at their own cost, any movements of the vessel as required for the entirety of the contract period.
| 1.25 | Means of safe access | As | Req. | Suitable safe access is to be provided to the vessel at all times and at all states of the tide when in the water and a safe secured ladder or steps for access when out of the water. Note: it is normal to step straight from a pontoon onto a CPV.
| 1.4 | Electrical Power | 30000 | kW-h | The supplier must include all costs associated with providing unlimited electrical power to the vessel for the duration of the contract period. Vessel electrical system uses 400-volt, 50 Hz, 63-amp, three phase shore power.
|  |  | 1 | kW-h
| 1.5 | Electrical Connection | 1 | Ea. | Connection and Disconnection of shore power cable as required during the contract period
| 1.6 | Cleanliness | As | Req. | The Supplier will return the vessel to its original state of cleanliness on handover, removing and disposing of any arisings and cleaning all work areas on completion.
| 1.7 | Disposal of Waste | 1 | Ea. | All costs associated with the disposal of any waste during the life of this contract are to be born by the supplier to include approximately 100 ltrs of oily waste.
2 | Third-party Costs
| 2.1 | Use of third parties | 1 | Contract | Where a requirement stipulates the use of a third party, the Supplier is responsible for arranging the attendance of such suppliers. The Supplier is to include those costs in the section which stipulates their attendance.
3 | Insurance
| 3.1 | Cost of additional Insurance | As | Req. | If required, any additional costs that may be incurred by the Supplier due to the undertaking of a bespoke insurance arrangement are to be included in the quote and the Authority is to be notified and then provided with the appropriate documentary proof following contract award.
4 | General Provision
| 4.1 | Project Management | 1 | Contract | The Supplier will appoint a Project Manager, as a single point of contact for the BFOO, for the duration of this requirement. The Suppliers Project Manager is to be available as necessary for the duration of the period. The costs for the Supplier's Project manager should be included as part of the cost of each line-item.
| 4.2 | External Contractors | 1 | Contract | If required, the Supplier is to confirm they will provide support to the external contractors Border Force has engaged with. This will be the provision of manual labour, cranage, tools, removal and disposal of parts if required and costs incurred will be dealt with in the appropriate Annexes of this statement of requirement.
| 4.3 | Accommodation | 1 | Contract | During the contract period the Supplier shall provide reasonable office accommodation for use by the Authority at the site where the vessel is being worked on. All costs associated with this provision are to be at included in any quote/bid submitted by the Supplier to the Authority.
| 4.4 | Consumable Fixings | 1 | Contract | All minor consumable fixings, sealants etc. required to carry out this requirement are to be at the expense of the Supplier.
| 4.5 | Secure Storage | 1 | Contract | The Supplier is required to provide an appropriately secure storage area for any of the vessel’s equipment, should anything need to be removed.
Note |  |  |  |  | The storage area should not have a negative impact on the item(s) of the vessel’s equipment that has been removed for storage.
| 4.6 | Floor Protection | 1 | Contract | All flooring and bulkheads/partitions in all domestic areas, including the Wheelhouse, which will be accessed by the Supplier’s personnel or contractors, or Authority contractors, are to be provided with non-slip floor protection, up to ½ height of the partition, the use of brown paper or paper cardboard is not enough. Such protection will be replaced as necessary to ensure integrity throughout the project.
5 | Trials
| 5.1 | Trials | 1 | Contract | Any trials required shall be to prove that the executed work has been carried out satisfactorily and that the various systems can be checked and confirmed as fully and effectively re-commissioned. Other than fuel, all costs related to the operations of test and trials will be the responsibility of the Supplier. This includes the Suppliers personnel provided for sea trials.
Annex A Total Cost

## Annex B
Annex B: Inspection, Testing and Certification of Safety Equipment
Annex B |  | Description | Qty | DoQ | Description of Service | Acknowledgement / Unit Price | Total Firm Cost
1 | Requirements for Certification
Note |  |  |  |  | All line-items contained in this Annex shall be inspected and tested, where required, in accordance with relevant legislation and standards, as appropriate. All line-items shall be issued a separate certificate of inspection and testing. All tasks are to be carried out by an approved examination test house, unless otherwise stated. On completion of all work, the supplier shall provide inspection reports and certification for each separate task.
2 | Documentation
Note |  |  |  |  | Two copies of all certification required for regulatory compliance, or as requested by the Authority, shall be supplied enclosed in clear envelopes within two four-ring ring binders. Each binder shall be assembled using the ordering and numbering shown in the Authority’s document SOP 08 (SOP 08 will be issued to the successful Supplier). Additionally, an electronic copy of all certificates and test reports shall be forwarded by e-mail to the Authority in .pdf format. All certificates and reports specified and required are to be provided in hard copy folders to the Vessel before departure and electronically emailed to the Authority.
3 | Fire Fighting and Fire Detection
Note |  |  |  |  | These tasks are to be carried out by an approved Marine Fire and Safety Contractor. Supplier to arrange.
3.1 | - | Inspect, Clean and Test | - | - | Inspect, clean and function test the Tyco MX T2000 Fire Detection System Detector Heads
| 3.1.1 | Inspect, Clean and Test | 25 | Ea. | Smoke Detectors
| 3.1.2 | Inspect, Clean and Test | 1 | Ea. | Flame Detector
| 3.1.3 | Inspect, Clean and Test | 1 | Ea. | Heat Detector
3.2 | - | Test |  |  | Function Test the following:
| 3.2.1 | Test | 12 | Ea. | Call Points
| 3.2.2 | Test | 9 | Ea. | Audible Alarm Units
| 3.2.3 | Test | 2 | Ea. | Alarm Indicator beacons.
3.3 | - | Inspect and Clean | 1 | Ea. | Inspect the control panel Power Supply Unit (PSU), Batteries and connections: noting expiry dates. If batteries are within three months expiry date, they are to be replaced.
| 3.3.1 | Test | 1 | Ea. | Fully function test the system including secondary power mode.
| 3.3.2 | Record and Submit | 1 | Ea. | Update test tally and submit formal tabulation of reading results.
3.4 | - | Service, Survey and Certify | 1 | Ea. | Service, Survey and Certify the Unitor Engine Room, Emergency Generator Compartment and Bow Thruster Space Fixed CO2 Extinguishing System as follows:
| 3.4.1 | Disconnect | 1 | Ea. | Disconnect the Main CO2 cylinders from the system and insert blanks.
| 3.4.2 | Inspect | 1 | Ea. | Visually inspection the whole CO2 system.
| 3.4.3 | Blow through | 1 | Ea. | Blow through discharge pipe work system with clean air at a minimum pressure of at least 20 bar.
| 3.4.4 | Inspect and test | 3 | Ea. | Undertake the 10-year hydraulic test on the three main 45kg CO2 cylinders.
| 3.4.5 | Check | 4 | Ea. | Check the contents and levels of the 3 main 45kg CO2 cylinders and the operating cylinders.
| 3.4.6 | Check | 5 | Ea. | Check all flexible hoses for ageing.
| 3.4.7 | Check | 3 | Ea. | Check pilot bottle pressures are greater than 120 Bar and within 10% of one another.
| 3.4.8 | Check | 1 | Ea. | Function check of the pull handle to activate the cylinder valves, close valves, and check for leakage.
| 3.4.9 | Fill | 1 | Ea. | Fill CO2 manifold with (+/- 25 bar) from a CO2 test cylinder (Main valves closed, or sections sealed).
| 3.4.10 | Test | 1 | Ea. | Close and disconnect the CO2 test cylinder, check thread connections for leakage.
| 3.4.11 | Check | 1 | Ea. | Check operation of pressure gauge and blow through the CO2 pipe work with the CO2 gas in the manifold.
| 3.4.12 | Reconnect | 1 | Ea. | On completion, re-connect / re-commission the system.
| 3.4.13 | Recommission | 1 | Ea. | Present the re-commissioned system to the BFOO for acceptance.
4 | Fire Extinguishers
4.1 | - | Inspect | 1 | Ea. | Carry out annual inspection as per manufacturer’s instructions for each item listed and Inspect all fire extinguishers as listed.
| 4.1.1 | Inspect | 8 | Ea. | 5 kg CO2
| 4.1.2 | Inspect | 6 | Ea. | 6 kg Dry Powder
| 4.1.3 | Inspect | 2 | Ea. | 2 kg Dry Powder
| 4.1.4 | Inspect | 4 | Ea. | 9 litre Foam
| 4.1.5 | Inspect | 2 | Ea. | Fire Blanket
| 4.1.6 | Certify | 1 | Ea. | Issue certificate for all items.
5 | Fire Hoses and Nozzles
5.1 | - | Examine, Test and Certify | 1 | Ea. | The following fire hoses and nozzles are to be examined. On completion of examination they should be tested to 5.25 bar. A certificate of examination and testing shall be issued.
| 5.1.1 | Examine, Test and Certify | 1 | Ea. | 20 meter 1 ½ diam. fire hose and 1 nozzle (Bridge Deck Aft)
| 5.1.2 | Examine, Test and Certify | 1 | Ea. | 10 meter 1 ½ diam. fire hose and 1 nozzle (Boat Deck)
| 5.1.3 | Examine, Test and Certify | 2 | Ea. | 10 meter 1 ½ diam. fire hoses and 1 nozzle (Forward Main Deck)
| 5.1.4 | Examine, Test and Certify | 1 | Ea. | 15 meter 1 ½ diam. fire hose and 1 nozzle (Forward Machinery Space)
| 5.1.5 | Examine, Test and Certify | 1 | Ea. | 20 meter 1 ½ diam. fire hose (Forward Machinery Space)
| 5.1.6 | Examine, Test and Certify | 2 | Ea. | 10 meter 1 ½ diam. fire hoses and 1 nozzle (Engine Room)
6 | Breathing Apparatus Equipment
Note |  |  |  |  | These maintenance tasks are to be carried out by an approved Draeger service agent.
6.1 | - | Maintain, Survey & Test | As | Req. | Carryout required maintenance, survey and testing of Breathing Apparatus Equip, as indicated:
| 6.1.1 | Maintain, Survey & Test | 3 | Ea. | Drager PSS3000 plus (Annual survey and maintenance)
| 6.1.2 | Maintain, Survey & Test | 2 | Ea. | Draeger CF10 EEBD (Annual survey and maintenance)
| 6.1.3 | Maintain, Survey & Test | 9 | Ea. | 9 litre carbon fiber BA cylinders (Annual survey and maintenance)
| 6.1.4 | Test | 2 | Ea. | EEBD air cylinders (Annual survey and maintenance)
| 6.1.5 | Survey | 3 | Ea. | Sets Fireman’s Equipment (jackets, trousers, flash hoods, helmets, lifeline)
| 6.1.6 | Certify | As | Req. | Supply individual certificates for each item’s annual survey and maintenance.
7 | Life Jackets
Note |  |  |  |  | These tasks are to be carried out by an MCA/UK Flag State approved MRT service agent.
7.1 | - | Inspect and Test | 1 | Ea. | Inspect, service and test inflatable lifejackets:
| 7.1.1 | Inspect and Test | 10 | Ea. | Crewsaver Sea Crusader SOLAS approved inflatable lifejackets, complete with McMurdo locating beacons, are to be Inspected, serviced and tested.
| 7.1.2 | Inspect and Test | As | Req. | Replace CO2 inflation cylinders as necessary.
| 7.1.3 | Inspect and Test | 10 | Ea. | Issue individual certificates of inspection and test.
| 7.1.4 | Report | 1 | Ea. | Report all defects found to the BFOO.
8 | Immersion Suits
Note |  |  |  |  | These tasks are to be carried out by an MCA/ UK Flag State approved Crewsaver service agent.
8.1 | - | Inspect and Test | 1 | Ea. | Inspect, service and test inflatable immersion suits:
| 8.1.1 | Inspect and Test | 20 | Ea. | Crewsaver Immersion Suits are to be inspected, serviced, and tested.
| 8.1.2 | Inspect and Test | 20 | Ea. | Issue individual certificates of inspection and test.
| 8.1.3 | Report | 1 | Ea. | Report all defects to the BFOO.
9 | EPIRB
9.1 | - | Inspect and Test | 1 | Ea. | Inspect, service and test inflatable EPIRB SN: 20199 (UIN: 9D0D413B9C00379).
| 9.1.1 | Inspect and Test | 1 | Ea. | Survey and Service EPIRB by an approved service agent.
| 9.1.2 | Inspect and Test | 1 | Ea. | Inspect EPIRB Hydrostatic release expiry date and if less than 1 year remains, renew EPIRB hydrostatic release unit and plastic retaining bolt.
| 9.1.3 | Inspect and Test | 1 | Ea. | Check EPIRB, if less than one year remaining, renew batteries as required.
| 9.1.4 | Report | 1 | Ea. | Issue a service report with a list of the test results and maintenance performed.
10 | Safety and Rescue Equipment
10.1 | - | Inspect & Certify | 1 | Ea. | Inspect and Certify the ‘Helicopter Strop’ rescue sling.
10.2 | - | Inspect & Certify | As | Req. | Inspect and Certify the following personal Safety Harness equipment:
| 10.2.1 | Inspect & Certify | 2 | Ea. | KRATOS full body harnesses
| 10.2.2 | Inspect & Certify | 2 | Ea. | Seago safety lines.
| 10.2.3 | Inspect & Certify | 2 | Ea. | Waist Harnesses
| 10.2.4 | Inspect & Certify | 4 | Ea. | 2m restraint lanyards
| 10.2.5 | Inspect & Certify | 1 | Ea. | KRATOS two-point body harness
| 10.2.6 | Inspect & Certify | 1 | Ea. | Saviour Technical stretcher
Note |  |  |  |  | These tasks are to be carried out by a Soll approved GlideLoc / SALA Service Agent.
10.3 | - | Inspect & Certify | 1 | No. | All fixed components of the GlideLoc Mast Installation
| 10.3.1 | Inspect & Certify | 2 | Ea. | GlideLoc Fall Arrest Traveler
| 10.3.2 | Inspect & Certify | 1 | Ea. | Fall Arrest Block
| 10.3.3 | Inspect & Certify | 2 | Ea. | Work Positioning Strap
10.4 | - | Survey and Certify | As | Req. | Survey and Certify the following GlideLoc/SALA Mast Access Equipment personal safety equipment:
| 10.4.1 | Inspect & Certify | 2 | Ea. | Miller Full Body Harness to EN361 with back strap
| 10.4.2 | Inspect & Certify | 2 | Ea. | Petzl climbers Helmet
| 10.4.3 | Inspect & Certify | 1 | Ea. | AG 10 rescue kit including 30m rope and webbing straps
| 10.4.4 | Inspect & Certify | 2 | Ea. | Inertia Lanyard
10.5 | - | Inspect and Certify | 2 | Ea. | Carry out thorough inspection of the brow safety net and issue certificate.
10.6 | - | Inspect and Certify | 1 | Ea. | Carry out thorough survey of the scrambling net (including the securing arrangement) and issue certificate.
10.7 | - | Inspect and Certify | 1 | Ea. | Carry out thorough survey of the Jason’s Cradle, including captive slings and issue certificate.
10.8 | - | Inspect and Certify | 1 | Ea. | Carry out thorough survey of the Fiberlite frame and issue certificate.
11 | Deck Equipment
Note |  |  |  |  | All deck equipment to be tested/inspected under Lifting Operations and Lifting Equipment (LOLER) and MGN 332 regulations.
12 | Emergency Anchor Recovery Equipment
Note |  |  |  |  | The service is to be carried out by an approved test house whose details will be notified to the BFOO.
12.1 | - | Inspect, Certify and Test | As | Req. | The following anchor recovery equipment is to be inspected, certified and where appropriate tested:
| 12.1.1 | Inspect, Certify and Test | 1 | Ea. | Tractel Turffer tackle block and wire 3200kgs SWL.
| 12.1.2 | Inspect, Certify and Test | 1 | Ea. | GS Double fall manual chain block x 6metres HOL 3000kg SWL.
| 12.1.3 | Inspect, Certify and Test | 1 | Ea. | Duplex polyester web belt sling terminating in a captive eyed latch hook one end only EWL 840 mm 3000 kgs SWL.
| 12.1.4 | Inspect, Certify and Test | 1 | Ea. | Ace grade 8 alloy steel single leg chain, complete with 16/8 Bergok one end and 16/8 shortening clutches the other, EWL 400mm 3,500kgs SWL @ 90 degree.
| 12.1.5 | Inspect, Certify and Test | 1 | Ea. | 16 mm diam. single leg wire rope sling terminating in soft eyes EWL 850mm 3000 kgs SWL.
| 12.1.6 | Inspect, Certify and Test | 1 | Ea. | 1” Bow shackle 3750 kgs SWL.
| 12.1.7 | Inspect, Certify and Test | 8 | Ea. | Screw pin bow shackles.
13 | Emergency Towing Equipment
13.1 | - | Inspect & Certify | As | Req. | The following emergency towing equipment is to be examined, certified and where appropriate tested:
| 13.1.1 | Inspect & Certify | 1 | Ea. | 8 strand multi-plat Towing Line and shackles.
| 13.1.2 | Inspect & Certify | 4 | Ea. | 5.5 tonne D shackles.
| 13.1.3 | Inspect & Certify | 3 | Ea. | 12 tonne bow shackles.
| 13.1.4 | Report | As | Req. | Report all defects found, with work recommendations, to the BFOO.
14 | RHIB Recovery and Securing Equipment
14.1 | - | Inspect & Certify | As | Req. | Inspect and certify the RHIB recovery and securing equipment.
| 14.1.1 | Inspect & Certify | 1 | Ea. | RHIB screw pin “D” shackle
| 14.1.2 | Inspect & Certify | 1 | Ea. | RHIB wire rope sling
| 14.1.3 | Inspect & Certify | 1 | Ea. | RHIB turnbuckle
| 14.1.4 | Inspect & Certify | 1 | Ea. | RHIB quick release pin
| 14.1.5 | Inspect & Certify | 1 | Ea. | RHIB 10mm connector
14.2 | - | Inspect, Test and Certify | 1 | Ea. | Carry out a Dynamic Load Test of the anchor windlass using a horizontal load of 1.6 tonnes. On completion of successful test, update test tally and supply test certificate.
14.3 | - | Inspect, Test and Certify | 1 | Ea. | Carry out a Dynamic Load Test of the RHIB Recovery Capstan using a perpendicular load of 1.6 tonnes. On completion of successful test, update test tally and supply test certificate.
14.4 | - | Inspect, Test and Certify | 2 | Ea. | Carry out a Dynamic Load Test of the Port and Starboard After Mooring Capstans to 1.15 tonnes. On completion of successful test, update test tally and supply test certificate.
14.5 | - | Inspect, Test and Certify | 1 | Ea. | Survey and certify the RIB recovery equipment 12mm stainless steel rope, safety hook and swivel to a SWL of 1.6 tonnes. On completion of successful survey, update test tally and supply test certificate.
15 | Man Overboard Boat (MOB) System
Note |  |  |  |  | The following items are to be carried out by an approved Schat Harding service agent whose details will be notified to the Authority with the submission of the formal quotation. The normal practice from Messrs. Schat Harding is to use a service exchange QRH.
15.1 | - | Inspect and Maintain | 1 | Ea. | Carry out Annual Inspection and Maintenance of SEC MS2-7-40 MOB Davit.
15.2 | - | Inspect, Maintain and Certify | 1 | Ea. | Carry out Annual Inspection and Maintenance of Schat-Harding RRH15 MOB quick release hook.
16 | Zodiac 4.2m Man Overboard Boat (MOB)
Note |  |  |  |  | These tasks are to be carried out by an MCA or UK Flag State Zodiac approved service agent(s) whose details must be notified to the Authority with the submission of the formal quotation. Work on the Outboard Engine is to be conducted by an approved Yanmar service agent. On return the outboard is to be re-installed on the MoB.
16.1 | - | Service and Certify | 1 | Ea. | Remove MOB boat and send for service, survey and certification.
16.2 | - | Inspect & Certify | 1 | Ea. | Survey and Certify 4 leg lifting sling, shackles and links.
16.3 | - | Inspect & Certify | 4 | Ea. | Lifting points within the MOB.
16.3 | - | Service | 1 | Ea. | Remove MOB Boat 25hp Yamaha Long Shaft Outboard Engine and send for annual service as per manufacturer’s instructions. All parts are Supplier supply.
16.4 | - | Report and Certify |  |  | Issue service report, test, and survey certificates on successful completion of work.
17 | Miscellaneous
17.1 | - | Test | 2 | Ea. | Radiation leak test Microwave Ovens located in galley and mess deck.
17.2 | - | Service | 2 | Ea. | The onboard Oxygen therapy kits, including Oxygen cylinders, is to have its annual service carried out by an approved service agent.
17.3 | - | Inspect, Test, Survey and certify | 1 | Ea. | The gangway brow is to be inspected for weld/construction defects. If item is satisfactory, a load deflection test of 450 kgs is to be conducted. Test and survey certificates are to be supplied on successful completion.
17.4 | - | Inspect and Certify | 4 | Ea. | Steering Chain Blocks located in steering flat.
17.5 | - | Inspect and Certify | 1 | Ea. | Pilot Ladder: To be replaced by the Authority.
17.6 | - | Inspect and Certify | 1 | Ea. | Scrambling net: To be replaced by the Authority.
Annex B Total Cost

## Annex C
Annex C: Vessel Maintenance Tasks
Annex C |  | Description | Qty | DoQ | Description of Service | Acknowledgement / Unit Price | Total Quote Cost
Note |  |  |  |  | Where it is stipulated in this Requirement that approved engineers/agents are to be used, the Supplier shall submit details, to include business address and contact details, to the Authority, of these engineers/agents who will carry out the work alongside the formal quotation.
1.0 | Deck
1.1 | - | Overhaul | As | Req. | Overhaul Raised Coaming water-tight hatches and replace hatch seals.
| 1.1.1 | Replace | 1 | Ea. | Hatch Seals on Weather deck Fwd./Lower Deck Fwd. Accommodation.
| 1.1.2 | Replace | 1 | Ea. | Hatch Seals on Weather deck / Waist Main Engine Room Access.
| 1.1.3 | Replace | 1 | Ea. | Hatch Seals on Weather deck / Port Aft Peak Steering Compartment Access.
| 1.1.4 | Replace | 1 | Ea. | Hatch Seals on Weather deck / Stbd Aft Steering Compartment Access.
| 1.1.5 | Test | 1 | Ea. | On completion of all work, function test the hatches to prove security and water-tight integrity.
2 | Maine Engines: Caterpillar 3516B
Note |  |  |  |  | Main Engine lubrication oil capacity is 405 liters (Castrol Vectron 15/40), Oil and Filters will be supplied by Authority. In addition to the work detailed herein, both main engines will be subject to annual maintenance tasks contracted separately by the Authority. Work under this requirement must be chronologically arranged to coincide with both the Supplier and Authority scope of work.
2.1 | - | Change | As | Req. | Change oil and filters on both Port and Stbd Caterpillar 3516B main engines.
2.2 | - | Dispose | 1 | Ea. | Existing main engine lubrication oil charge is to be pumped out and disposed of in accordance with extant regulations.
2.3 | - | Renew | 1 | Ea. | Renew the lubrication oil filters.
2.4 | - | Replenish | 1 | Ea. | Replenish the lubrication oil charge.
2.5 | - | Change | 1 | Ea. | Change the main engine fuel filters (only change the 5x main filters).
2.6 | - | Dispose | 1 | Ea. | Cost for disposal of 1 cubic meter (m3) of lubricating oil in accordance with extant regulations.
3 | Main Engine Port and Starboard Reintjes WLS930 Reduction Gearboxes
Note |  |  |  |  | This service is to be completed by an approved Reintjes service agent.
Note |  |  |  |  | Main Gearbox lubrication oil capacity is 90 liters (Castrol MHP 153), Lube Oil to be Authority supply.
3.1 | - | Inspect | 1 | Ea. | Annual external inspection.
| 3.1.1 | Inspect | 1 | Ea. | Open the Inspection plates and carryout an internal inspection of the pinions and gearwheels in accordance with Reintjes WLS and WVS maintenance service routines.
| 3.1.2 | Test | As | Req. | Test all temperature and pressure shut down devices.
| 3.1.3 | Test | As | Req. | Test all sensors, inter-switches, and alarm systems for correct operation.
| 3.1.4 | Dispose | As | Req. | Existing gearbox lubricating oil charge is to be pumped out and disposed of in accordance with extant regulations.
| 3.1.5 | Renew | As | Req. | Renew the in-use lubricating oil filters (only change the in-use oil filter). To be supplied by approved Reintjes service agent.
| 3.1.6 | Change | As | Req. | Change the sinter filters. To be supplied by approved Reintjes service agent.
| 3.1.7 | Replenish | As | Req. | Replenish the lubricating oil charge.
| 3.1.8 | Report | 1 | Ea. | On completion, a Reintjes Service Report is to be provided to the BFOO in both hard and electronic copy formats.
4 | Steering Gear Installation
Note |  |  |  |  | There are two electronically linked Steering Gear installations each installation has two hydraulic pumps and consequently two starters.
4.1 | - | Inspect | 2 | Ea. | Carry out visual and physical inspection of the Port and Starboard steering gear installations.
| 4.1.1 | Check | As | Req. | Hydraulic leaks.
| 4.1.2 | Check | As | Req. | Cylinders and rams for leakage.
| 4.1.3 | Check | As | Req. | Tightness / security of linkages and connection.
| 4.1.4 | Inspect | As | Req. | Inspect tank anti-vibration mounts.
4.2 | - | Report | As | Req. | Inspection Report is to be provided to the BFOO in both hard and electronic copy formats.
5 | Bow Thruster
Note |  |  |  |  | Filters are Authority supplied.
5.1 | - | Survey and Report | 1 | Ea. | Survey the condition of the Bow Thruster flexible coupling element and the mounting bolts and report findings to BFOO.
5.2 | - | Survey and Report | As | Req. | The following Bow Thruster hydraulic power pack hydraulic oil filters are to be changed.
| 5.2.1 | Survey and Report | 1 | Ea. | Filter Element No E26N - Offline Filter.
| 5.2.2 | Survey and Report | 1 | Ea. | Tank Top Return Filter H33O R20N.
| 5.2.3 | Survey and Report | 1 | Ea. | Tank Top Return Filter H160 R20.
5.3 | - | Remove, Disassemble, Maintain and Inspect | 1 | Ea. | Hydraulic power pack oil heat exchanger.
| 5.3..1 | Remove, Disassemble, Maintain and Inspect | 1 | Ea. | Remove, clean, and inspect hydraulic power pack oil heat exchanger.
| 5.3..2 | Reassemble and Test | 1 | Ea. | Reassemble using new seals, end plates and conduct pressure test.
| 5.3..3 | Refit | 1 | Ea. | Refit heat exchanger.
6 | Emergency Fire Pump
6.1 | - | Service and Report | 1 | Ea. | 50hr service on Lombardini Diesel Firefighting Pump Engine as per manufacturer’s instructions for 250 hours.
6.2 | - | Service and Report | 1 | Ea. | Service Report is to be provided to the BFOO in both hard and electronic copy formats.
7 | Portable Salvage Pump
7.1 | - | Service | 1 | Ea. | Carry out 50 Hour service on the Yanmar L48 4.8HP diesel engine as per manufacturer’s instructions for 250 hours.
7.2 | - | Report | 1 | Ea. | Service Report is to be provided to the BFOO in both hard and electronic copy formats.
8 | Domestic Water System
Note |  |  |  |  | The Authority will supply any necessary replacements.
8.1 | - | Inspect, Maintain and Repair | 1 | Ea. | Hydrophore (BT) Fresh Water Hydrophore Unit.
| 8.1.1 | Disconnect | 1 | Ea. | Disconnect and drain the hydrophore.
| 8.1.2 | Inspect | 1 | Ea. | Inspect the hydrophore cylinder and rubber bladder.
| 8.1.3 | Maintain | 1 | Ea. | Remove the bladder, clean it with freshwater and sterilize it.
| 8.1.4 | Inspect | 1 | Ea. | Inspect the cylinder for excess corrosion, leaks, or damage.
| 8.1.5 | Inspect | 1 | Ea. | Inspect the bladder for damage, leaks, or signs of perishing: renew the bladder if necessary.
| 8.1.6 | Re-connect | 1 | Ea. | Re-pressurise the air space between the hydrophone cylinder and bladder to 0.2 bar.
| 8.1.7 | Test and Report | 1 | Ea. | On completion of all work re-commission the system and function test to the satisfaction of the BFOO and report details.
8.2 | - | Inspect and Test | 1 | Ea. | Domestic Hot FW System:
| 8.2.1 | Locate | 2 | Ea. | Daalder domestic fresh water calorifier Heaters (No.1 and No.2).
| 8.2.2 | Inspect and Test | As | Req. | Inspect and Pressure Test Calorifiers (carry out pressure test to 5 bar for 15 minutes).
| 8.2.3 | Inspect | As | Req. | Inspect for leaks and damage.
| 8.2.4 | Test | 2 | Ea. | Check pressure setting of PRVs.
| 8.2.5 | Record | 1 | Ea. | Supply local tallies to record the pressure and test date and issue ISO 9001 standard certificate of test for Calorifiers and PRVs.
| 8.2.6 | Test and Record | 1 | Ea. | Carry out and record insulation test on the 6 kW Heating elements in both calorifiers.
| 8.2.7 | Report | 1 | Ea. | Inspection Report is to be provided to the BFOO in both hard and electronic copy formats.
9 | Air Conditioning System
9.1 | - | Replace | 1 | Ea. | Replace the AC Compressor drier filling.
9.2 | - | Inspect | 1 | Ea. | Inspect the condition of the V- belts driving the ventilation fan.
9.3 | - | Measure and Adjust | 1 | Ea. | Measure the deflection/tension of the v-belts and adjust as required.
9.4 | - | Inspect | 1 | Ea. | Inspect refrigeration system pipework and system.
9.5 | - | Test and Report | 1 | Ea. | Carry out function test and provide Inspection Report to the BFOO.
10 | Electrical Distribution
Note |  |  |  |  | Tasks for 10.6.1 – 10.6.8 to include: Insulation testing Continuity testing of earth bonding Function test of current overload devices Function test of anti-condensation heaters Motor bearing condition checks Motor bearing condition checks
10.1 | - | Check and Record | 1 | Ea. | Check insulation readings on listed circuits.
10.2 | - | Check and Record | 1 | Ea. | Check and record insulation readings on all circuits from the following locations:
| 10.2.1 | Check and Record | 1 | Ea. | Main switchboard (Engine Room) 415/240V 50Hz.
| 10.2.2 | Check and Record | 1 | Ea. | P1 power/lighting distribution board (Engine Room) 415/240V 50Hz.
| 10.2.3 | Check and Record | 1 | Ea. | P2 power/lighting distribution board (Forward Machinery Space) 415/240V 50Hz.
| 10.2.4 | Check and Record | 1 | Ea. | L3 lighting distribution board (Main Deck Technical Room) 415/240V 50 Hz.
| 10.2.5 | Check and Record | 1 | Ea. | L4 lighting distribution board (Wheelhouse) 415/240V 50 Hz.
| 10.2.6 | Check and Record | 1 | Ea. | Central distribution board (Wheelhouse) 415/240V 50Hz.
| 10.2.7 | Check and Record | 1 | Ea. | AC plant distribution board (Forward Machinery Space) 415/240V 50 Hz.
| 10.2.8 | Check and Report | 1 | Ea. | Port and Starboard generator winnings resistance and insulation resistance.
| 10.2.9 | Report | 1 | Ea. | Submit formal tabulation of reading results in the format of the attached Annex P.
10.3 | - | Inspect and Test | 1 | Ea. | Shore Power Supply:
| 10.3.1 | Inspect and Test | 1 | Ea. | Inspect and Test Shore Power Connection Box and Cable.
| 10.3.2 | Report | 1 | Ea. | Submit formal tabulation of reading results.
10.4 | - | Check | 1 | Ea. | Earth Bonding:
| 10.4.1 | Check | 1 | Ea. | Check Earth Bonding of Shafts, Rudders and Stabilisers.
| 10.4.2 | Report | 1 | Ea. | Submit formal tabulation of reading results, in the format of the attached Annex P.
10.5 | - | Maintain and Test | 1 | Ea. | Clean, Inspect and Test Starters and Motors for the following:
| 10.5.1 | Maintain and Test | 1 | Ea. | Anchor Windlass.
| 10.5.2 | Maintain and Test | 1 | Ea. | Port and starboard capstans (2 in total).
| 10.5.3 | Maintain and Test | 1 | Ea. | MOB Boat Davit.
| 10.5.4 | Maintain and Test | 1 | Ea. | Steering gear system pumps (4 in total).
| 10.5.5 | Maintain and Test | 1 | Ea. | Bilge/general service pumps (2 in total).
| 10.5.6 | Maintain and Test | 1 | Ea. | FW hydrophore pumps (2 in total).
| 10.5.7 | Maintain and Test | 1 | Ea. | AC pump.
| 10.5.8 | Maintain and Test | 1 | Ea. | AC compressor.
10.6 | - | Test | 1 | Ea. | On completion of all work, restore power supply and function test to the satisfaction of the BFOO.
10.7 | - | Report | 1 | Ea. | Inspection Report is to be provided to the BFOO in both hard and electronic copy formats.
11 | 240v Portable Appliances
11.1 | - | Test | 180 | Ea. | Carryout and Document PAT on, approximately, 180 items of 240v Appliances.
11.2 | - | Test | As | Req. | On completion of satisfactory test, label each appliance with a suitable identification label indicating: Pass date of Test and Initials of Tester.
11.3 | - | Report | 1 | Ea. | Submit formal tabulation of reading results.
12 | Super Chlorination of the Domestic Fresh Water System
Note |  |  |  |  | Failure to achieve WHO test standards for both potable water and legionella will require re super-chlorination and re-testing at the Suppliers cost, until satisfactory test results, which meet WHO standards for potable water, are obtained.
12.1 | - | Maintain | 1 | Ea. | Super chlorinate the Fresh Water Holding Tank.
| 12.1.1 | Maintain | 1 | Ea. | Open the fresh water holding tank.
| 12.1.2 | Maintain | 1 | Ea. | Carry out visual survey of the tank coating in conjunction with International Paints representative/BFOO.
| 12.1.3 | Maintain | 1 | Ea. | Once the tank coating is acceptable, re-fit the holding tank lids, using new nitrile material gaskets.
| 12.1.4 | Maintain | 1 | Ea. | Press up the holding tank with treated super chlorination mixture.
| 12.1.5 | Maintain | 1 | Ea. | Run water through ALL taps, hoses, and shower heads: ensuring the super-chlorination concentrate levels are monitored and maintained.
| 12.1.6 | Maintain | 1 | Ea. | De-chlorinate the freshwater tank: run through ALL taps, hoses, and shower heads.
| 12.1.7 | Maintain | 1 | Ea. | Drain down the system and the holding tank.
| 12.1.8 | Maintain | 1 | Ea. | Super chlorinate the Fresh Water Holding Tank.
| 12.1.9 | Maintain | 1 | Ea. | Re-fill up Fresh Water tank, take water samples of the onboard system and shoreside.
| 12.1.10 | Analyse | 1 | Ea. | Submit samples for analysis of potability and legionary’s disease.
| 12.1.11 | Certify | 1 | Ea. | Provide a certificate of potability and no legionary present upon completion of satisfactory tests.
13 | Main and Emergency Batteries
13.1 | - | Inspect, Maintain and Test | 1 | Ea. | The following three 12-volt battery sets are to have work undertaken as per 13.2 – 13.6.
| 13.1.1 | Inspect, Maintain and Test | 1 | Ea. | Port and Stbd in Engine Room.
| 13.1.2 | Inspect, Maintain and Test | 1 | Ea. | Port side Weather deck (Emergency Set).
| 13.1.3 | Inspect, Maintain and Test | 1 | Ea. | Stbd Eng. Room general service bank.
13.2 | - | Inspect, Maintain | 1 | Ea. | Clean the Battery Sets and inspect for damage, corrosion and electrolyte leaks.
13.3 | - | Test | 1 | Ea. | Carry out capacity discharge test on each 12-volt battery.
13.4 | - | Maintain | 1 | Ea. | Clean connectors / terminals and coat with no-oxide grease (petroleum jelly).
13.5 | - | Check | 1 | Ea. | On completion of all approved work, ensure the Battery is fully charged and restored to the normal operational state.
13.6 | - | Report | 1 | Ea. | Pass inspect and test results to the BFOO.
14 | Engine Room Control Desk Cabinet
14.1 | - | Inspect, Survey, Repair | 1 | Ea. | The engine room engineers desk console panel is to be inspected and damaged repaired to include but not be limited to replacement of components, connectors and wires, removal of un-used old wires. This work will need to be undertaken in connection with SES who are the PRAXIS System OEM who the Authority will contract. Some indicative photographs of the wiring are included below. An allowance 40 hours to be made for an electrician.
15 | Starboard Fuel Tank Space
15.1 | - | Maintain, Empty | 1 | Ea. | The Stbd fuel tank is to be emptied, with the clean oil/fuel in the fuel retained in clean container and all such removed fuel and replaced onboard prior to Basin Trials and with the agreement of the BFOO. Assume up to 2m³ [The chief engineer will be transferring as much fuel as possible into the port fuel tank on or before arrival].
15.2 | - | Inspection, Repair | 1 | Ea. | The tank is to be opened at the aft end hatch, vented and gas free certificate issued to allow entry. Prior to sealing the tank space hatch, the BFOO is to witness the removal of all cleaning material and confirm the hatch maybe sealed, using new nitrile gaskets. A formal record of closing is to be issued.
16 | Anchor Cable and Locker
16.1 | - | Maintain, Inspect, Report | 1 | Ea. | Anchor cable locker to be opened and vented and gas free certificate issued.
16.2 | - | Maintain | 1 | Ea. | The anchor cable is to be removed from the Cutter and thoroughly cleaned.
16.3 | - | Inspect, Report | 1 | Ea. | Survey and measure the cable stud links against a Lloyds cable specification and report details to the BFOO.
16.4 | - | Maintain, Clean, Paint | 1 | Ea. | Reapply cable chain length markings, by paint and cable tie methods every ten meters as follows: The number of links painted for equivalent to the length in meters. The middle link to be wire moused. Links to be painted white except for the two outer end links which are painted red. The last ten-meter marker is to be painted all red.
16.5 | - | Maintain | 1 | Ea. | Re-stow the cable in the chain locker with rope tie and lock onto the anchor.
17 | Anchor Windlass Electrical Control Box
17.1 | - | Replace | 1 | Ea. | The anchor windlass control box is to be replaced including the corroded back plate and re-preserving the back mounting plate to international paint standards prior to refitting the new control box.
18 | Fore Peak Hatch
18.1 | - | Replace | 1 | Ea. | The seal on the fore peak hatch is to be replaced.
18.2 | - | Maintain, Repair | 1 | Ea. | The fore peak hatch drain is blocked and requires to be unblocked and the overboard discharge valve checked.
18.3 | - | Clean | 1 | Ea. | The floor of the fore peak is to be dried and cleaned from the incoming water.
19 | Starboard Aft Outdoor Shower
19.1 | - | Repair | 1 | Ea. | The supplier is to replace the rusting pipe fixing with like for like and make good the paintwork to International Paints standard, around the area as shown in the photograph below.
20 | Mechanical Fitting
20.2 | - | Provide | 1 | Ea. | The Supplier is to provide a quote for 40 hours of mechanical fitting labour to be used as needed by the BFOO.
21 | Electrical Labour
21.1 | - | Provide | 1 | Ea. | The Supplier is to provide a quote for 40 hours of electrical labour to be used as needed by the BFOO.
Annex C Total Cost

## Annex D
Annex D: Painting
Annex D |  | Description | Qty | DoQ | Description of Service | Acknowledgement / Unit Price | Total Quote Cost
Note |  |  |  |  | Painting and preparation to be completed in accordance with the attached International Paint Specification.
1 | General
1.1 | - | - | 100 | Hrs. | The Supplier is to provide a quote for 100 hours of painting work to be used as needed by the BFOO.
Note |  |  |  |  | The Authority will supply all International Paint as required.
1.2 | - | Wash Down | As | Req. | All the main deck, deck fittings, bulwarks / railings and superstructure are to be hot washed down to remove salt residue, oil, grease and soot from the areas, prior to starting the paint re-preservation.
2 | Anchor
2.1 | - | Paint | 1 | Ea. | The main anchor is to be cleaned, prepared and coated as follows: To patch repair areas by surface preparing areas of rust / coating breakdown back to bare metal and prepared in line with the International paint specification and feather in any areas of detachment, or damage including grazing or blistering. Recoating as per the international paint specification with one complete coat of boot topping.
3 | Spare Anchor
3.1 | - | Paint | 1 | Ea. | The spare anchor is to be removed cleaned, prepared and coated as follows and replaced: To patch repair areas by surface preparing areas of rust / coating breakdown back to bare metal and prepared in line with the International paint specification and feather in any areas of detachment, or damage including grazing or blistering. Recoating as per the international paint specification with one complete grey top coat.
4 | Main Deck
4.1 | - | Paint | 200 | m2 | Main deck has an area of 200 m2 is to be cleaned, prepared and coated as follows: To patch repair areas by surface preparing areas of rust / coating breakdown back to bare metal and prepared in line with the International paint specification and feather in any areas of detachment, or damage including grazing or blistering. Recoating as per the international paint specification (allow for up to 25% 50 m2). The main deck is to be recoated in one coat of “colour wash”.
5 | Bulwarks & Railings
5.1 | - | Paint | 90 | m2 | Bulwark & Railings has an area of 90 m2 is to be cleaned, prepared and coated as follows: To patch repair areas by surface preparing areas of rust / coating breakdown back to bare metal and prepared in line with the International paint specification and feather in any areas of detachment, or damage including grazing or blistering. Recoating as per the international paint specification 25% (22.5 m2). Areas shown in the photographs are to be included.
6 | Deck Fittings and Equipment
6.1 | - | Paint | 50 | m2 | Deck Fittings and equipment an area of 50 m2 is to be cleaned, prepared and coated as follows: To patch repair areas by surface preparing areas of rust / coating breakdown back to bare metal and prepared in line with the International paint specification and feather in any areas of detachment, or damage including grazing or blistering. Recoating as per the international paint specification (allow for up to 50% 25m2).
7 | Safety Signwriting around superstructure
7.1 | - | Paint | As | Req. | Survey all the “red” safety sign writing around the vessel and once surveyed re-sign write in red the one that require re-preservation to the office.
Annex D Total Cost

## Annex E
Annex E: Modifications and Defect Rectification
Annex D |  | Description | Qty | DoQ | Description of Service | Acknowledgement / Unit Price | Total Quote Cost
1 | AC Room Door Lock – Defect 26/21
1.1 | - | Replace | 1 | Ea | Replace the AC room door lock, supplying as a minimum three keys with the lock.
2 | AUX Hydraulic Pump - Defect 27/21
2.1 | - | Replace | 2 | Ea | Flex hoses end fittings are extremely rusty. Require new hoses; Hose 1: Feed from Tank to Pump. Hose 2: Discharge hose from pump.
3 | Air Conditioning Plant Sew Water Flow Check Valve - Defect 30/21
3.1 | - | Repair | 1 | Ea | No flow through valve. Unit details: Johnson Controls, PENN, V46BT-9301, Flange 2- 1/2" DIN 86021 Water Temp 90C Max Water Pressure 10 Bar Max
3.2 | - | Repair | 1 | Ea | New valve to be supplied and fitted.
4 | AC Seawater Pump Suction Gauge - Defect 32/21
4.1 | - | Repair | 1 | Ea | Glass on gauge is unreadable due to debris on inside of glass. Gauge requires replacement.
5 | G S Pumps - Defect 33/21
5.1 | - | Repair | 3 | Ea | Three gauges require replacement; 1. Discharge side pressure gauge on GS pump 1. Gauge looks fairly new however displays no indication of pressure when discharge line is charged. 2. Suction side pressure gauge on GS pump 1. Needle Broken. Requires replacement. 3. Suction side pressure gauge on GS pump 2. Needle Broken.
6 | GS Pumps O/B Discharge Valves - Defect 34/21
6.1 | - | Repair | 2 | Ea | GS Pup 2 overboard discharge valve stiff to operate. Please investigate and if required supply and fit replacement valves. GS pump 1 (right) - 3.9 turns to fully close GS pump 2 (left) - >2 turns to fully close Allow for 2 hours of a fitter plus spares
7 | External Door Operating Mechanicians - Defect 35/21
7.1 | - | Repair | As | Req. | Inspect all watertight door operating mechanisms for the presence of Nylon top hat sleeves/liners and washers. If any are missing, then allow to supply and fit the missing items on the watertight doors.
8 | Fridge Locks - Defect 40/21
8.1 | - | Repair | 2 | Ea | Arrange to source, supply and fit fridge locks on aft and fwd. fridges.
9 | Fuel Transfer Pump Y Strainer - Defect 41/21
9.1 | - | Repair | 2 | Ea | Arrange to source, supply and fit 1 new Y strainer and supply a second as a spare.
10 | Anchor Windlass - Defect 49/21
10.1 | - | Repair | 1 | Ea | Investigate an intermittent fault with the electric brake. Allow for 2 hours of mechanical fitter and two hours of electrician investigation time.
11 | AC Thermostat - Defect 48/21
11.1 | - | Repair | 1 | Ea | The air conditioning thermostat cabling conduit is not connected correctly. Please arrange to repair the conduit. Allow 2 hours of an electrician.
12 | Stern Door Stbd RAM Bearing Housing - Defect 51/21
12.1 | - | Repair | 1 | Ea | Arrange to investigate and repair the starboard RAM bearing housing on the stern door as the RAM is moving across the pin when the door is operated. Allow for 2 hours mechanical fitter to investigate and 6 hours of a fitter and welder to make the repair plus spares. Video of the RAM operating is available.
Annex D Total Cost

## Quote Total
Annex A Total Cost | 0
Annex B Total Cost | 0
Annex C Total Cost | 0
Annex D Total Cost | 0
Annex E Total Cost | 0
Quote Total Cost | 0

## Additional Information
Additional Information
Ser | Annex | Line | Description | Completed by: | Acknowledged by: | Complete
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32

## Acceptances
1 | Organisation Name
2 | Quote reference
3 | Terms and Conditions
My Organisation accepts the Authorities Terms and Conditions as set out in C22116 - HMC Seeker - MSER - T&Cs?
4 | Insurance
My Organisation has the required insurance as stated in Part 2 of C22116 - HMC Seeker - MSER - SOR - v1.0?
5 | Cardinal Date Plan
My Organisation has included my Cardinal Date Plan with my organisation's quote as per Part 4 of the SOR, §6.3?
6 | Quote Confirmation
My Organisation has included confirmation of the quote total on letter headed paper?
7 | Emergent Work
My Organisation shall ensure that the Supplier-assigned PM will inform the BFOO if any of the Suppliers employees or contractors have been approached by either; a) the Vessel commander, b) the Vessel’s crew or c) any member of the Authority’s staff to undertake work not specified in this Specification of Requirements or as part of a previously authorised EW task.
8 | Quote Confirmation
My Organisation acknowledges and agrees that the Authority reserves the right to withhold payment from the Supplier, in part or in full, should any, specified or otherwise, condition as expressed in this Specification of Requirements, not be successfully met by the Supplier and to the satisfaction of the BFOO within the specified timeframe?
9 | General
My Organisation accepts that the Authority reserves the right to withdraw this opportunity, for any reason, at any point, prior to contract award?
10 | Filled out by
11 | Position
12 | Date

## SDS (hidden)
Notes | Acknowledge
Acknowledge | Do not Acknowledge
Do not acknowledge
Complete
Yes
Pending
No
Yes
T&C | No
Yes
No
Yes
Pending
No