Medical Gas Pipeline Systems (MGPS) Maintenance Specification

All Gases:

- Quarterly Planned preventative Maintenance Check as detailed in HTM 02-01, part B – Operational Management

- Annual recalibration of  pressure switches

- 3-yearly alarm panel battery replacement

- 5-Yearly Pressure safety Valve (SRV) replacement

- 5-yearly Regulator Replacement

- 5-yearly Cylinder Tailpipe Replacement

Medical/Surgical Air:

- Annual maintenance of Oil/Water separator (including carbon filter)

- Annual compressor oil change

- Annual Compressor Intake Filter change

- 2-yearly line and dewpoint regulator overhaul

- 2-yearly dewpoint sensor replacement

- 2-yearly dryer inlet and line solenoid valve overhaul

- 2-yearly dryer shuttle ball replacement

- 2-yearly compressor and dryer filter replacement

- 2-yearly desiccant replacement

Medical Vacuum:

- Annual Pump oil change

- 2-yearly Bacterial Filter Replacement

AGSS:

- Annual recommission of systems (Re-balance/LEV Test)