## Sheet1
Notes
Pipe material | Mild Steel |  |  | Pipes and Tubes - Temperature Expansion
Expansion coefficient | 20.7 | m/m/K | Stainless steel pipe.
Pipe size | DN100 |  | Worst case, largest pipe size.
Pipe outer diameter | 114 | mm
Change of pipe temperature | 90 | °C
Length of pipe | 50 | m | Longest straight run.
Pipe expansion | 0.09315 | m
| 93.15 | mm | 50m of pipe would increase in length by less than 4".
Minimum offset | 10.3049 | m | 10m of pipe required perpendicular to straight run. Worst case offset recommendation for stainless steel.
Conclusion: | Due to the "L-shaped" arangement of the buildings and pipework and the changes in height, there is significantly more than the required offset length available to accommodate thermal expansion. It must be ensured that the pipes are supported to accommodate some longitudinal expansion, as well as lateral movement where required (such as the supports towards the main changes of direction). 4" would be worst case, but this would be shared by expansion in the other side of the pipe runs as well as the main perpendicular pipe run. The requirement to select appropriate supports and guides to accomodate thermal expansion will be included in the specification and verified in the detailed design approval process.
Pipework and Expansion Guide: Flexibility of a Pipe with an Offset ¦ DST Group

## Data
Expansion Coefficients
m/m/K
Mild Steel | 14.9
Stainless steel | 20.7