Report on Energy Centre - Chiller Structure Refurbishment Project

at

National Oceanography Centre, Southampton, Waterfront Campus, European Way SO13 3ZH

for

National Oceanography Centre, Southampton

Job No. 2206

October 2016

William Attwell & Associates

St Clement’s House, 27 Clement’s Lane, London EC4N 7AE

Tel: 020 3319 1725

www.williamattwell.co.uk

Registered in England and Wales, No. 4520800

REVISION SCHEDULE

| ISSUE | TITLE | DATE | PREPARED BY | CHECKED BY | APPROVED BY |
| --- | --- | --- | --- | --- | --- |
| 1.0 | Final | 26/10/17 | GA | WCA | WCA |

# INTRODUCTION

The scope of this survey is to check the condition of the protective enclosures and support structure for the three glycol chillers located on the roof of the Energy Centre of the Southampton site, and to give recommendations for repair or replacement as appropriate.  The survey was carried out by representatives of William Attwell & Associates on 2nd October 2017.

The three chillers and their enclosures and support structures were subject to a visual inspection only.

All parts of the chiller enclosures have been rated, using the following (RICS) Condition Rating:

NI – Not Inspected

1 – No repair is currently needed.  The property must be maintained in the normal way.

2 – Defects that need repairing or replacing but are not considered to be either serious or urgent.  The property must be maintained in the normal way.

3 – Defects that are serious and/or need to be repaired, replaced or investigated urgently.

Reference Plan:

# SURVEY RESULTS

| CHILLER | 01 | INSPECTION DATE |  | 02/10/2017 |
| --- | --- | --- | --- | --- |
| SCOPE | CHILLER ENCLOSURE INSPECTION |  |  |  |
| ELEVATION A |  | ELEVATION B |  |  |
| ELEVATION C |  | ELEVATION D |  |  |
| EXTERNAL CASE |  | WIRE GRILLES |  |  |
| SPRING ISOLATOR |  | SUPPORTING FRAME |  |  |
| CHILLER PARTS | EXTERNAL CASE | WIRE GRILLES | SPRINGS ISOLATORS | SUPPORTING FRAME |
| RICS CONDITION RATING | 2 | 3 | 3 | 1 |
| NOTE: External casing: The overall condition is generally satisfactory, but there are areas where the steel frame is delaminating due to corrosion. A number of the external fixings are corroded and some are missing. Wire grilles: The overall condition is very poor, with the plastic protection peeling off. 80% of the wire grilles are corroded and showing delamination. Spring isolators: Most of the spring isolators are corroded and showing delamination. Support frame: Mild steel galvanized support frame is in good condition, no signs of rust or delamination. |  |  |  |  |
| CHILLER | 02 | INSPECTION DATE |  | 02/10/2017 |
| SCOPE | CHILLER ENCLOSURE INSPECTION |  |  |  |
| ELEVATION A |  | ELEVATION B |  |  |
| ELEVATION C |  | ELEVATION D |  |  |
| EXTERNAL CASE |  | WIRE GRILLES |  |  |
| SPRING ISOLATOR |  | SUPPORTING FRAME |  |  |
| CHILLER PARTS | EXTERNAL CASE | WIRE GRILLES | SPRINGS ISOLATORS | SUPPORTING FRAME |
| RICS CONDITION RATING | 2 | 3 | 3 | 1 |
| NOTE: External casing: The overall condition is generally satisfactory, but there are areas where the steel frame is delaminating due to corrosion. A number of the external fixings are corroded and some are missing. Wire grilles: The overall condition is very poor, with the plastic protection peeling off. 80% of the wire grilles are corroded and showing delamination. Spring isolators: Most of the spring isolators are corroded and showing delamination. Support frame: Mild steel galvanized support frame is in good condition, no signs of rust or delamination. |  |  |  |  |

| CHILLER | 03 | INSPECTION DATE |  | 02/10/2017 |
| --- | --- | --- | --- | --- |
| SCOPE | CHILLER ENCLOSURE INSPECTION |  |  |  |
| ELEVATION A |  | ELEVATION B |  |  |
| ELEVATION C |  | ELEVATION D |  |  |
| EXTERNAL CASE |  | WIRE GRILLES |  |  |
| SPRING ISOLATOR |  | SUPPORTING FRAME |  |  |
| CHILLER PARTS | EXTERNAL CASE | WIRE GRILLES | SPRINGS ISOLATORS | SUPPORTING FRAME |
| RICS CONDITION RATING | 2 | 3 | 3 | 1 |
| NOTE: External casing: The overall condition is generally satisfactory, but there are areas where the steel frame is delaminating due to corrosion. A number of the external fixings are corroded and some are missing. Wire grilles: The overall condition is very poor, with the plastic protection peeling off. 80% of the wire grilles are corroded and showing delamination. Spring isolators: Most of the spring isolators are corroded and showing delamination. Support frame: Mild steel galvanized support frame is in good condition, no signs of rust or delamination. |  |  |  |  |