## Annex 1
Enclosure 1 |  |  |  | UP Use Only
Supplier name
Contact
Company Number
VAT Number
Confirm Copy of your company’s Terms and Conditions and Payment Plan as per section 6.3 has been included in our response
Conflict of Interest Statement. Please provide statement as per the options at section 8 in the ITT
Date of response
ITT Ref | REQUIREMENT | COMMENT | RESPONSE
3.2.1 | Required facility to be a combination spray booth / oven unit which can be used for both paint application and curing the paint work with a low bake stoving mode.
3.2.2 | Nominal Internal Dimensions: Length 10m, Width 5m, Height 3.5m
3.3.1. | The main structure to comprise of vertical double skin white steel panels which are fixed together on installation.
3.3.2. | The roof to be manufactured in single skin galvanised steel with an explosion relief area incorporated.
3.3.3. | Vertical panels to sit within floor channels which are screwed to the floor, the shell is then mechanically fixed to aid sealing and give the booth rigidity. Plenum area and lights to be fully sealed after erection to prevent ingress of dirty air.
3.3.4. | The spray booth must be a free standing enclosure independent of other buildings. The unit will be an internal unit fitted within an existing building.
3.4.1. | Nominal door opening to be 4.5m wide x 3.5m high electrically operated roller shutter door.
3.4.2. | The door must be able to gain a complete seal. Doors to be located at the front of the booth.
3.5.1. | 1 x off emergency escape door is to be fitted at the rear of the booth as the site location dictates.
3.5.2. | This door to be double skin, self-closing and fitted with a laminated glazing panel.
3.5.3. | The door must incorporate an easily replaceable seal, giving good seal.
3.6.1. | Light system to comprise multi-cluster LED's to required standards, units fitted at corner roof level.
3.6.2. | Average illumination level to be 1200 lux.
3.7 | This spray booth requires a down draught air movement with the following air flow characteristics:
a. | Nominal Air Capacity
b. | Spray temperature rise availability above ambient
c. | Bake temperature with recirculation
d. | Heater Output Capacity
3.8.1. | The spray booth requires an air handling plant to give air input into the top of the spray booth, to create a down draught air movement within the booth.
3.8.2. | The main input plant will incorporate a double inlet centrifugal fan unit.
3.8.3. | The fan unit has a 500mm impellor and is fitted with a 7.5 kW 3 phase motor.
3.8.4. | A direct gas fired heater is fitted into the duct system to give a temperature rise availability of 22°C above ambient in the spray cycle.
3.8.5. | In the bake cycle the air will recirculate through the heating system to optimize fuel costs and give a bake temperature of 80°C
3.8.6. | Automatic control dampers are fitted into the system for switching between spray and bake mode.
3.8.7. | Air from atmosphere will enter the duct system and be heated to the required temperature, it will then enter the booth via a ceiling plenum chamber. Air will diffuse into the booth through a EU5 fine filter media.
3.8.8. | The filters are fitted uniformly within the ceiling at the front of the booth into easily accessed hinged frames which trap the filter in position to ensure all air is filtered prior to booth entry.
3.8.9. | All the input and extract plant is mounted on the chest at the rear.
3.9.1. | Air to be extracted from the booth via a rear low level chest. The chest needs to be fitted with a two stage dry filtration system (EU3 and EU2 grades). These filters need to be easily accessible.
3.9.2. | The main extraction fan will be as the input unit.
3.9.3. | The installed package needs to come complete with the recirculation system, intake and exhaust ducts, including roof plates, skirts, water ingress damper and an accelerator cone. Ducting to be the DW144 standard and in galvanised steel.
3.10.1 | Comprehensive control panel to be supplied to control the booth giving all necessary functions, indications and readouts for all operations.
3.10.2 | The control panel must incorporate the following features:
a. | Operational mode switching
b. | Temperature readout on Spray mode
c. | Temperature readout on flash-off
d. | Temperature readout on Bake mode
e. | Light Switching
f. | Process cycle time control
g. | Total hours run indication
h. | Adjustment for bake and spray temperature setting, these would be preset and controlled to ensure set limits are not exceeded
i. | Cabin pressure readout by Magnahelic gauge
j. | Automatic shutdown and audible alarm if the booth becomes over pressurised in the spray cycle.
3.11 | Warranty Provision: 1-year parts and labour warranty as a minimum on installed and commissioned equipment.
3.12.1 | Electrical wiring must be in plastic conduit and cable trays in accordance with IEE Regulations.
3.12.2 | Plant to be commissioned and fully set up on completion and a test certificate of operation and conformity to be given to client together with instruction manual.
3.12.3 | Operational training to be given to clients nominated personnel.
Costs
£
£
Total (EX VAT) |  | £

## Compliance (hidden)
Supplier name | A | B | C | D
Contact
Company Number
VAT Number
Confirmation that you the supplier are able to meet the requirements outlined in the brief above.
2.1
2.1.1
2.1.2
2.2
2.2.1
2.2.2
2.2.3
2.2.4
2.2.5
3
Costs
Total (EX VAT)