Appendix C

SPECIFICATION FOR THE PROVISION OF

PLANNED PREVENTATIVE & REACTIVE MAINTENANCE AND MINOR WORKS

CONTRACT REF:  NHSBT0992/S/SP

Contract Requirements

Document

Provision of Planned Preventative Maintenance / Reactive Maintenance / Minor Works

- Tender reference: NHSBT0992/S/SP

- Specification for Mechanical, Electrical, Building Maintenance, Reactive Services & Minor Works Projects.

| Section | Title |
| --- | --- |
| 1.0 | Overview |
| 2.0 | Definitions |
| 3.0 | Variation of Conditions |
| 4.0 | Scope of Contract |
| 5.0 | Emergency Call Out & On Call Cover |
| 6.0 | Specification |
| 6.1 | Statutory Obligations |
| 6.2 | Specialist Testing |
| 6.3 | CAFM Management System |
| 6.4 | Mobilisation Period & Asset Condition Surveys |
| 6.5 | Building, Electrical, Mechanical & Catering Maintenance Tasks |
| 6.6 | Asset List |
| 6.7 | Maintenance of Assets |
| 6.8 | Manufacturers Instructions |
| 6.9 | Thermal Imaging |
| 6.10 | Fixed Wiring Inspection & Testing |
| 6.11 | Testing of Portable Appliances |
| 6.12 | Plant Shutdown & Disruption of Services |
| 6.13 | Spares & Consumables |
| 6.14 | Records Overview |
| 6.14.1 | Records General |
| 7.0 | Use of Specialist NHSBT Approved Contractors |
| 8.0 | Use of Specialist Approved Sub-Contractors |
| 9.0 | Liaison with Other Bodies – NHSBT Specialist Contractors NHS Trusts & Landlords |
| 10.0 | Equipment on loan |
| 11.0 | Contract Management and Client Team |
| 12.0 | Instructions to the Contractor |
| 13.0 | Site Visits |
| 14.0 | Contract Variations |
| 15.0 | Health & Safety |
| 16.0 | Permits to Work / Authority to Work |
| 16.1 | Fire Safety |
| 16.2 | Induction & Training |
| 16.3 | Staff |
| 17.0 | Price and payment |
| 18.0 | Defects Liability Period |
| 19.0 | General Information |
| 20.0 | Appendicies |

NHS Blood and Transplant (NHSBT)

- Specification for Mechanical, Electrical, Building Maintenance, Reactive Services & Minor Works Projects.

1.0	Overview

Contractors who provide goods or services to National Health Service Blood and Transplant must understand the critical nature of the work undertaken by NHSBT. Failure to meet the contract requirements can impact on the collection, testing and processing of Blood and Tissue Products. Stock levels are demand led and can reduce dramatically following an event, therefore the continuous flow of Blood and Tissue Product is critical.  Any failure in the provision of services may further adversely affect the operational requirements on which Transplant Services depend.

Good communication is a key component to the efficient running of any contract. To this end, the Contractor will be expected to liaise fully with NHSBT’s Facilities department.

By its nature, the work undertaken by NHSBT has a direct impact on Patient Lives and is often life saving in nature – the effective operational delivery of this Maintenance Contract plays an essential part in ensuring the continuity of services on which NHSBT rely.

The Contractor should be aware that a key element of the contract is ensuring that NHSBT remains compliant with statutory requirements and in working to Good Manufacturing Practice (GMP), the standard required by the licensing authority Medicines and Healthcare products Regulatory Agency and as noted in the paragraphs set out below

The purpose of this Specification is to give a clear understanding of the proposed requirements and the expected outcomes of the service. NHS Blood and Transplant (NHSBT) is a pharmaceutical manufacturer and distributor and it is obliged to adhere to European legislation relating to GMP and demonstrate stringent levels of control to satisfy the requirements of the Medicines and Healthcare products Regulatory Agency (MHRA).  This Specification highlights the important role that the appropriate level of maintenance and attendance to reactive works plays in the contribution towards this key NHSBT business commitment.

The standards identified in this Specification shall be read in conjunction with statutory requirements for all aspects of the Contract. It is the Contractor’s responsibility to ensure that they have a clear understanding of the complexity of the service and that required in its delivery.

Maintenance of the mechanical, electrical and related services within NHSBT’s premises supports in the provision of a suitable environment for Products and Services with regard to both MHRA and GMP requirements, together with the more general welfare requirements of both staff and the public. This results in the high degree of importance attached to ensuring all necessary environmental conditions, including temperature, humidity & air pressure, are controlled within set parameters.

The Contractor should be aware that compliance with these stringent requirements includes a high degree of regulation, conformance with procedures and the provision of a full audit trail.  This will include records of activities undertaken and associated documentation. Examples of such procedures will include prompt action in closing out Quality Incidents (QI’s), carrying out Corrective Actions within agreed timescales and, as necessary, contributing to a Root Cause Analysis.

All necessary measures in consideration of Security, Confidentiality and Data Protection will be expected in this contract.

The performance of the Contractor will be measured throughout the contract period via regular monthly reports against Key Performance Indicators (KPI’s).  Should the Contractor fail to respond within the KPI’s outlined in section 6.15, NHSBT reserve the right to engage with a third party contractor to undertake works recovering all costs from the PPM / Reactive Maintenance Contractor.

The Contractor will provide valid Insurance Documents indicating cover to the required amount during the course of the contract.

All the Contractor’s engineering staff will be required to undertake appropriate on-site training. The Contractor’s staff, and Subcontractors working on the contract, will require GMP Awareness training prior to commencing work on site. This training will be provided by Estates & Facilities (E&F) for all new staff and subcontractors throughout the length of the contract and will be renewed annually.  Records of attendance will be kept by Facilities; the induction applies for all NHSBT properties.

The Contractor shall not be limited in their ability to be innovative and to deliver a quality service with demonstrated value for money benefits.

The contract will be for Building, M&E and associated Specialist services as may be defined which will include reactive and Minor Works Projects. The contract will also include maintenance of associated catering equipment on certain sites.

The contract will be for 5 years, with the possibility of extending on a yearly basis for a further 2 years.

National/Regional Properties

The North West region comprises:

- Principal Sites – Birmingham, Liverpool and Manchester.

The North East region comprises:

- Principal Sites – Leeds, Newcastle and Sheffield.

Please note the direction of travel for our proposed estates plan is, subject to board approval the Main Centres at Leeds and Sheffield will close and a new Centre constructed in the Barnsley area during 2020/21.

The South West region comprises:

- Principal Sites – Filton, Oxford and Southampton.

The South East region comprises:

- Principal Sites – Colindale, Tooting and Cambridge.

There are a number of minor satellite sites and remote office locations within the regions comprising of Donor Suites, Warehouses and Team Base premises. (See attached Appendix 1).  Separate costs must be identified for all the various sites. Due to on going strategy reviews, NHSBT reserves the right to add or remove sites.

It should be noted that, for some larger manned sites, an extended day will be expected, with cover provided from 06:30hrs to 18:30hrs each working day.  Additional costs will not be created in this provision, site engineers to implement a rotation of duties to accommodate the longer day.  The successful Contractor will demonstrate the ability to help release maintenance savings that flow from any rationalisation of the estate.

2.0	Definitions

Definitions will be as laid out in section 1 of the JCT Measured Term Contract: key items are identified below.

NHSBT means the Health Authority placing the contract. Health Authority means a Health Authority, Special Health Authority or NHS Trusts, as the case may be.

The contract means the agreement concluded between NHSBT and the Contractor, including all specifications, plans, drawings and other documents incorporated or referred to therein.

The Contractor means the person who by the contract undertakes to supply the services to NHSBT as provided for in the contract. The Contractor also includes Sub-contractors working on behalf of the Contractor.

The contract price means the price exclusive of value added tax that is payable to the Contractor by NHSBT under the contract for the full and proper performance by the Contractor of its part of the contract.

The goods means all goods, materials or articles that the Contractor is required under the contract to supply in connection with the services.

The services means the services that the Contractor is required to supply under the contract.

The NHSBT representative means the person appointed by NHSBT and notified in writing to the Contractor to act as the representative of NHSBT for all purposes connected with the contract, or the authorised representative of such a person.

Personal data has the same meaning as in section 1(3) of the Data Protection Act 1998.

RCA - Root Cause Analysis - A systematic and structured investigation to identify the true underlying cause of an adverse event in order to determine effective corrective and preventive action.

Quality Incident (QI) – Anything which should not be happening and has, or has the potential to affect product quality, patient / donor safety or could significantly affect supply. This includes cumulative events that individually would not be reported.

- 3.0		Variation of conditions

NHSBT will require variations on the content of the contract, which will necessitate the provision of quotes for maintenance additions or for minor works.  When requested these quotations must be provided within a maximum 10 days from receipt of NHSBT request in writing.

4.0	Scope of Contract

The Contractor must ensure they have allowed sufficient management and supervision to meet the needs of this contract and NHSBT’s regulated environment.  NHSBT is made up of four regions each requiring a dedicated, competent and suitably experienced contract manager. Cover will be provided for any annual or extended sick leave.

Suitable qualified and experienced Site Engineers will be provided as a dedicated resource at all principal sites as defined under clause 1.0 above.  These engineers will be required to participate in an out of hours on call rota providing cover 365 days a year.  All planned leave events will be covered, with suitable resource made available.  Where sick absence exceeds 3 days, cover must be provided by the contractor.

A dedicated 24/7 on-call facility will be provided by the Contractor for the duration of the contract.  An out of hours escalation plan will be provided by the contractor detailing contingency measures should the primary contact be unavailable.

Mobile engineering services will be provided for the execution of planned preventative, reactive and statutory maintenance to all HV/LV electrical, mechanical and building services. This will include a range of building controls systems, heating, ventilation, plumbing, electrical and cooling equipment.

The contract will include the provision of personnel to carry out Authorised Persons (AP) and Competent Person (CP) duties in the various disciplines.

Contractors must demonstrate competency of both their own and subcontracted staff.Staff training records and relevant competency certificates are to be provided at the start of the contract and updated throughout the life of the contract.

Maintenance of M&E services & drainage systems external to buildings but within the site boundary are to be included within the contract.

The successful contractor will include for the provision of a general purpose operative.

The contract will also include an element of Minor Work Projects.

The Contractor will review the Asset Lists provided which detail plant at each location: maintenance tasks to be carried out in line with the relevant SFG20 schedule.

NHSBT reserves the right to approve all staff working on the contract. Any Contractor’s staff or Subcontractor’s staff who do not meet NHSBT requirements must be removed from site when requested.

The list of items below is indicative of the scope of works to be undertaken by the Contractor for this contract and is not exhaustive:-

- Heating Systems

- Ventilation & Air Conditioning installations

- Ventilation duct fire / smoke dampers

- Chilled water systems

- Building Management Systems

- Electrical HV & LV distribution

- Fire protection & alarm systems

- Fire Fighting Equipment

- Gas Suppressant installations

- Gas service and detection

- Public address and voice alarm systems

- Generators

- Loading bay doors, auto-doors and shutters

- Switchgear maintenance & LV Distribution up to and including local distribution boards.

- PAT & thermal imaging

- Mechanical services and Heating services: Including pumps, heating appliances, calorifiers, distribution systems including steam & condensate and controls

- Domestic Hot & Cold Water Systems:

- Lifts: Passenger / Goods. Includes release of trapped passengers

- Refrigeration plant

- Car parking barriers

- Lamp cleaning

- Attendance for Statutory Examinations

- External & Internal plumbing: Including sanitary ware, above and below ground drainage and guttering systems, gullies, interceptors

- Catering equipment.

- UPS’s

Planned Maintenance

The contract is to include all maintenance for assets in the building as defined in the Asset Register identified in Appendix 4. With the exception of specialist items, the Contractor shall be responsible for employing the necessary competent Engineers and Subcontractors as appropriate and shall be totally responsible for ensuring that they carry out the works in accordance with the terms of the contract and Specification.  Where access equipment will be required, the contractor must include this provision within the contract sum.

Reactive Works

In addition to PPM, the contract is to support the organisation with a Reactive Maintenance service working to service levels agreed with local E&F staff.  All requests for reactive work must be carried out in line with its priority code and the associated time frame.  Where necessary, the presence of the relevant AP will be required.  Quotes, when required for reactive work, are to be returned within 10 working days of request.

Where purchase orders are placed Risk Assesment and Method Statements (RAMS) will be provided by the contractor and agreed with NHSBT E&F staff no less than 10 working days prior to the commencement of the works.

Minor Works / Project Works

The Contractor may be requested to undertake Minor Works / Project Works on any NHSBT site.  These may typically range from the replacement of individual items of plant and equipment through to refurbishment of office areas and Laboratories including partitioning works, new flooring and ceilings, external works and fencing, and so on. The Contractor shall also be required to support capital / revenue projects when carried out by others where isolations of services, for example, may be needed.

Where a quotation / tender is requested, including those from nominated sub-contractors, a full and detailed breakdown of costs into the constituent elements of Labour / Plant / Materials / Subcontractors / Hired Items shall be provided. All associated ‘mark-ups’ shall be in accordance with the terms of this contract.

Minor works up to and not exceeding a value of £75k (per scheme) are to be included within the contract.  The Contractor will be responsible for all design / installation and compliance with current legislated requirements.  During 2016 / 2017 NHSBT expended £950k on Minor Works.

The cost of these works will be in accordance with the National Schedule of Rates and will be subject to audit by NHSBT’s nominated cost consultant at various times throughout the life of the contract.

Where required, the Contractor will comply with the requirements of the Construction (Design and Management) Regulations 2015, making appropriate notification to Health and Safety Executive. Evidence of training for operatives in CDM will be made available on request.

Risk Assessment and Method Statement (RAMS), Environmental Impact Assessment (EIA), Safe Systems of Works and a Programme of Works will be required on receipt of an order for minor/project work.

It will be the responsibility of the Contract Manager to ensure the works are co-ordinated with NHSBT and the site based Maintenance Engineers. Dependent on the scope of works, reports on progress will be given as a minimum as part of the routine Monthly Reports and any variations will be costed and agreed in writing with NHSBT.

A minimum 12 month Defects Maintenance Period will apply to these works.

NHS Trusts/Shared sites

Some sites are associated with other parties and services, such as water, heating or electricity, are provided by the associated Third Parties. The demarcation point for maintenance is to be considered as the isolation point (valves, switches, secondary circuits etc) where the service enters the area for which NHSBT has responsibility. When in doubt, liaise with NHSBT’s E&F department.

Specialist Subcontractors

NHSBT require the Contractor to employ specialist Subcontractors to carry out specific elements of work. The Contractor is to have ‘back to back’ contracts with their Subcontractors so that the Subcontractor is working to the same Specification and performance criteria as the Contractor - (See section 9.0).  Copies of these contracts must be presented to NHSBT within 2 months of the start of the contract.

The Contractor must visit the various sites at the time of tendering to establish the full extent of works. NHSBT will not accept any claim for lack of knowledge.

- 5.0	Emergency Call Out & On Call Cover

The Contractor will provide an emergency call-out service. The emergency service is to cover all sites listed within the four regions 24 hours per day, 365 days per year.

- The emergency response time shall not exceed the stipulated period from logged phone call to attendance on site. (The response times are as defined in clause 6.15). The Contractor must ensure, as far as is reasonably practicable, that the appropriately qualified Operative or Specialist is made available to respond to the initial call.  Access to sites will be afforded by the provision of access cards at sites with access control; for remote sites, sets of keys will be issued. The Contractor will be responsible for securing premises in the event of accessing a site outside normal working hours.

NHSBT staff availability outside normal working hours is limited and it is therefore essential that all staff employed by the Contractor for this service have reasonable site knowledge and are competent to attend any breakdown of the plant listed in the plant schedules.  They should be aware of site access requirements and the location of plant rooms, access points, location of all associated information on site, main service runs and isolation points.  The contractor will be responsible for creating and maintaining an emergency manual for each site.  This emergency manual is to be agreed and signed off by NHSBT E&F staff.  It will be the responsibility of the contractor to update this manual as and when changes are made but  no less than annually.

- If the out of hours call-out is not a matter which can be easily rectified, or made safe, without potentially adverse effects on the building or Products, the Contractor’s Representative is required to telephone an NHSBT Representative within one hour of arrival on site and inform them of the cause of the fault and, if known, its effect on the building, also its likely further effect and estimated time to rectify.

- The information provided may necessitate initiation of NHSBT Business Continuity Plans.

- The Contractor’s Representative will be required to leave a full report for the NHSBT Representative in all such incidents. The report should indicate the actions taken and any recommendations. Such reports apply to all works carried out for NHSBT and should be provided within the agreed period.

The Contractor shall identify separately costs for the out of hours management of critical alarms via remote monitoring where this will allow early rectification of faults.

6.0	Specification Overview

The Contractor shall provide Site Engineers for Maintenance & Minor Works for Main Blood Centres as outlined in Appendix 1.  The Contractor is reminded that Reactive Works are not necessarily restricted to mechanical and electrical works. Mobile Engineers will be required to serve sites other than the Main Blood Centre sites.

6.1		Statutory Obligations

The Contractor shall be responsible for ensuring that all plant and equipment is maintained in accordance with NHSBT Computer Aided Facilities Management System (CAFM) and SFG20 tasks.  In addition all statutes, by-laws, other laws and regulations will be complied with. These shall include, but not be limited to, Healthcare Technical Memoranda (HTM’s), Health Building Notes (HBN’s), NHS Advice Notes, NHS Guidance Notes, Health & Safety legislation encompassing COSHH, Electricity at Work Regulations, IET Regulations BS7671, LOLER, PUWER, ‘F’ Gas Regulations and other relevant legislation, as applicable.

In addition, should the Contractor be of the opinion that any of the installations, systems, equipment, plant or materials in use do not comply with such statutes, by-laws, laws and regulations, the Contractor shall inform NHSBT’s Representative immediately of its views and shall then comply with any instruction or decision given. In this respect, the Contractor will be working on behalf of the ‘duty holder’ in compliance with, for example, the Electricity at Work Regulations.

The Contractor shall be responsible for an element of programming and partnership, ensuring timely attendance to all Statutory Inspections, liaising with relevant representatives and/or insurance inspectors who will be nominated by NHSBT on matters concerning any Building Services installations. The Contractor shall be responsible for ensuring that all their employees and Subcontractors carry out works strictly in accordance with Health and Safety, COSSH, Electricity at Work regulations and other pertinent legislation. The Contractor shall be in attendance at all such events to strip down any and all plant associated with an inspection (for the provision of insurance purposes etc) and shall restore any and all plant back to operational conditions upon completion. In executing this service, the Contractor must ensure that NHSBT is compliant, at all times, with statutory obligations, including during emergency shut down events. Any comments or recommendations passed by the Inspectorate shall be noted by the Contractor and passed on immediately to the NHSBT Representative. Findings must be resolved within any stipulated timescale required either by the Inspector or NHSBT.

- The Contractor shall be responsible for ensuring that all their employees and Subcontractors carry out any work strictly in accordance with Health & Safety, COSHH, Electricity at Work, Asbestos Regulations and all other legislation, by-laws and amendments and demonstrate capability / competency of all personnel.

- The Contractor shall submit a copy of their Health & Safety procedures, Risk Assessments and Method Statements (RAMS) before undertaking any activities within a building or its boundary.

- The Contractor shall provide valid, in date calibration certificates for all test equipment that is being used prior to use, safe to use certification on harnesses or other safety equipment, daily check records for lifting equipment if used over longer periods, and any other relevant documentation in association with test records. Training records must also be made available for staff in the use of such equipment.

6.2		Specialist Testing

Any statutory or specialist testing shall be undertaken by the Contractor or their Subcontractors. Test certification for specific buildings and tasks, including the next test date where known, should be made available to the E&F Representative for each main site or satellite building for review.

The test shall cover all the requirements of the appropriate Statutory Instruments and Regulations. The following list outlines the type of test required. The Contractor shall determine the extent of tests required as this list shall not to be treated as comprehensive.  The list of certification expected includes but is not limited to:

- 5 yearly IET Fixed Wiring Testing and Inspections

- 2 yearly IET Fixed Wiring Testing and Inspections (liquid nitrogen compounds)

- Fire Safety

- Chlorination certificates

- Lightning Protection

- Portable Appliance Testing

- Ventilation duct smoke / fire damper testing

NHSBT shall utilise specialist Contractors or Consultants to provide independent inspection services on installations and services including but not limited to the following:-

- Water services installations in respect of L8 / HTM04-01 risk assessment

- Statutory inspection of equipment and installations falling under the Pressure Systems Safety Regulations

- Internal Ductwork  inspection

- Statutory inspection of lifting equipment

- Fire Safety Specialist

- Asbestos

These specialists are not responsible for the maintenance of equipment, system or material: this is the responsibility of the Contractor and the Contractor will liaise, as necessary, with these specialists to allow such independent inspections to be carried out. This may include but not be limited to demonstrating and preparing equipment/vessels for inspection and restoring to full operation after inspection, also ensuring compliance at all times.

The Contractor will also be responsible for completing as necessary any data entries or documentation which may be provided by others, e.g. water or fire logbook or entry onto a personal digital assistant (PDA).

A logbook or suitable alternative will be provided by the Facilities department for all sites at which maintenance is carried out, allowing records of PPM activities to be kept on site. Water logbooks will also be provided by NHSBT and will be located at a suitable and agreed location on each NHSBT site. The Contractor will be responsible for ensuring that all relevant entries and certificates are provided within these logbooks. This will provide a full audit trail of works/tests carried out on such systems and will be inspected by the relevant Facilities Manager.

6.3		CAFM Management Systems

- The NHSBT Computer Aided Facilities Management (CAFM) software package is used to manage the maintenance of all properties within the organisation’s portfolio. The Contractor and NHSBT’s administrators will be expected to explore areas which can improve the management of the contract to the mutual benefit of both parties.

- The Contractor is to use the NHSBT CAFM system for all PPM and Reactive Works.

- The Contractor’s own CAFM system shall not be used to monitor NHSBT PPM activities.

- All original service documentation is to be provided back to the site E&F staff within 10 working days of task completion.  Contractors are to comply with GMP Good Documentation Standards.

The Contractor must confirm in writing that they are prepared to use the CAFM system as the primary source of information/data relating to the performance of the contract.

- The Contractor’s staff will be expected to use NHSBT IT infrastructure to manage and utilise NHSBT CAFM system for the planning, management and close out of Planned and Reactive tasks.  Tasks cannot be closed until all service documentation has been provided to E&F staff.  All original service documentation is to be provided to the appropriate Facilities staff within 10 working days of task completion.

6.4	Mobilisation Period & Asset Condition Surveys

The Contractor must access all sites, other than a Main Blood Centre site, through the E&F Office associated with that satellite site as not all remote sites are manned during normal working hours and access is therefore restricted.

The Contractor shall, within the mobilisation period, review all assets and provide a dilapidation report complete with photographic evidence for all major equipment and plant. This will detail the condition and future life expectancy, complete with any other relevant comments.

The costs for carrying out the condition surveys is to be included within the tender. Within 90 days of contract commencement, the Contractor is to visit all of the NHSBT properties included within the contract and carry out the initial maintenance visits.  At the same time, the Contractor will carry out an accurate and detailed survey of the properties to establish the accuracy of the Asset Schedules and fully detail the condition of the assets. The Contractor will then issue the dilapidation report, costings for any remedial works shall be included. The dilapidation report, detailing the condition of the assets and costs for remedial works, is to be submitted prior to the end of this mobilisation period. It will be updated and submitted annually from the commencement of the contract.  A condition survey report identifying building fabric & major plant falling below condition ‘B’- based on guidance within NHS Estatecode and CIBSE guide M- will be submitted by the contractor.

During the mobilisation period, assets requiring Planned Preventive Maintenance outside normal working hours should be identified agreed with the local NHSBT E&F Manager and costed accordingly.

Major plant will include but not necessarily limited to switchgear, generators, air handling units, fan systems, boiler plant, chillers, split system chillers/heat pump units, pumps, tanks, controls, lifting equipment, hot water generation plant, automatic doors, fire alarms, emergency lighting & specialist equipment.

NHSBT have a Critical Plant list which must be prioritised to ensure we can continue to produce in support of the core operational demands. Critical Plant will be identified by the NHSBT representative and relates mainly to installations supporting GMP operations and the core activities of NHSBT.

No Critical Plant PPM plant inspection shall be missed; all inspections shall be undertaken as scheduled.

6.5	Building, Mechanical, Electrical & Catering Maintenance Tasks

Maintenance is to be undertaken in line with SFG20 tasks schedules.

6.6	Asset List

- The PPM schedule has been produced using existing plant and equipment Asset Lists which, by their nature, are subject to change when Project Work is undertaken on the sites or items of plant and equipment are replaced due to failure or life cycle renewal.

- The Asset Lists indicate the overall extent of plant, equipment and systems within NHSBT premises. The Contractor shall review these and provide accurate and comprehensive Asset schedules of all equipment within the premises appertaining to this Specification. This will be provided within three months of appointment with a formal requirement for the asset register to then be reviewed and updated on a regular basis with NHSBT. PPM Asset Lists can be inspected at the time of tendering.

- All equipment and plant has been individually identified and labelled in a manner to suit NHSBT requirements. It will be the Contractor’s responsibility to ensure all equipment continues to be identifiable and advise where any additional labelling may be required.

6.7	Maintenance of Assets

The Contractor shall include within their tender the maintenance of all such ancillary equipment as may be associated with an entire heating and ventilation system. This includes, but is not limited to, all Building Management Systems (BMS) as provided in Appendix 1. The Contractor will allow for all specialist Subcontractor costs and maintenance visits for such equipment. The Contractor must maintain each BMS at each site as recommended by the manufacturer.

Various assets identified on the Asset Lists are detailed in groups, including but not limited to, pipe work and ductwork which may themselves include pipeline valves, strainers, volume control dampers, etc.  A site visit will be required to evaluate such items.  It is the Contractor's responsibility to satisfy themselves in respect of the above matters and it should be noted that no subsequent claim based upon lack of knowledge of a site will be accepted.  The Contractor shall also note that some equipment is identified without any reference to interconnecting or ancillary components, including but not limited to:-

- Remote/External Controllers associated with plant and equipment

- Integral Controls within plant and equipment

Where Maintenance Tasks relate to pipe work, valves and insulation for items of plant and equipment, it is deemed that the related distribution and interconnection systems items, both internal and external to the sites, are included in the tasks.

This includes but is not limited to:-

- Safety Valves

- Pressure gauges

- Temperature gauges

- Expansion loops/bellows

- Auto/manual air vents

The above is not exhaustive and used for indicative purposes only.

Where the Maintenance Tasks refer in general to check; examine; inspect; the Contractor is to report any remedial works that may be required or, in other situations, report abnormalities. The Contractor shall report any concerns without delay raising a helpdesk request on the NHSBT CAFM system.

The Contractor will not be held responsible for repairs to plant and equipment that can be demonstrated to be as a result of vandalism or misuse.  NHSBT will reimburse the Contractor for repairs carried out in such cases.

It is the sole responsibility of the Contractor to undertake analysis, replenish chemicals, ensure correct dosage and adjust dosage controls of water systems.  The Contractor shall note that NHSBT will engage an independent Consultant to audit the water systems but this will not absolve the Contractor of their responsibilities.  The cost of chemical replacement will be paid for in addition to the contract value.

Works undertaken on Domestic Hot and Cold Water Systems will be only be undertaken by trained Competent Persons.

6.8	Manufacturers Instructions

The Contractor shall check and bring to the attention of the NHSBT representative any requirements of the relevant equipment manufacturers instructions where the maintenance tasks or intervals are different to those set out in the SFG20 schedules.

In situations where manufacturer’s instructions/recommendations exceed the task frequencies as stated in the tender document, these recommendations shall be brought to the attention of the NHSBT Representative.

6.9	Thermal Imaging

The Contractor shall provide within the schedules accompanying the Form of Tender a cost for undertaking annual thermal imaging, and provision of a related comprehensive report, for all properties.  The assets to which thermal imaging will apply are main electrical switchgear LV and HV, electrical distribution board, electrical sub distribution, electrical control panels and heating, ventilating and air conditioning control panels and produce a report.

6.10	Fixed Wiring Inspection & Testing

A list of properties requiring a 5 year Electrical testing is attached in Appendix 1. The Contractor shall provide, within the schedules accompanying the tender, a cost for the undertaking of fixed wiring inspection and testing in accordance with the requirements set out by the NICEIC and the provision of a comprehensive report and test certificate for all properties.  The Contractor must be conversant with the specific requirements of NHSBT in so much that there can be no disruption to Main Blood Centre  activities or any impact with regard to Good Manufacturing Practice.

The majority of testing will be completed out of hours and will be subject to detailed planning. Method statements and risk assessments must be signed off by NHSBT’s E&F representative

6.11	Testing of Portable Appliances

The testing of portable appliances shall be carried out at each of the properties in accordance with NHSBT MPD for Electrical Safety. Appendix 2 includes the total number of tests per site previously undertaken. The equipment at team bases are to be tested six monthly the remainder annually. The Contractor shall include costs in their tender for testing but the actual remuneration to the Contractor will be on a unit cost/cost per number of appliances actually tested basis.  The test results are to be provided in both hard and electronic copy.

6.12	Plant Shutdowns & Disruption of Services

The PPM should be costed on the basis of being undertaken during normal working hours.  Following negotiation with the local E&F staff and where PPM activity is required to be undertaken outside of normal working hours, payment will be additional to the contract value.  These costs should be established as outlined in section 6.4.

It is the responsibility of the Contractor during the tender process to identify and understand these activities.  It should be noted that liaison with site E&F staff may be required as not all sites operate in the same way.

Out of hours shutdowns will relate to critical equipment/operations and would include but not necessarily be limited to: -

- Electrical and mechanical services serving critical plant and equipment or GMP areas

- Chlorination of water systems

- Clean room activities

- Relevant drainage maintenance

Due to the interconnections of various items of plant and the sensitivity of inoperability, no plant shall be shut down, asset isolated or disconnected without prior approval of the E&F Representative responsible for that site or location. The E&F Representative should be provided with prior notice of such shutdowns: RAMS must be provided for any such isolation.

The Contractor is advised that NHSBT has specific change control procedures which must be adhered to in effecting change. There are also Management Process Descriptions (MPD) and Standard Operating Procedures (SOP) to control and manage any planned shutdowns or outages for the purposes of maintenance, repair or project which can impact on NHSBT operations or processes. This is not limited to areas under the control of GMP. Copies of this documentation will be made available to the Contractor on request.

Isolation of plant or equipment is not permitted without the express agreement of the NHSBT Representative. This will include activities such as the isolation of plant, equipment or air handling units. Any such agreement will take into consideration availability of standby plant and site operational status/requirements and will usually be determined following a change control exercise. This change control will be informed by Method Statement/Risk Assessment and require suitable and sufficient liaison with departments which may be affected by such an isolation.

No system outages attributable to inadequate maintenance or operational errors on behalf of the Contractor or its Subcontractors will be accepted.  Should the Contractor fail to respond within the time frames, outlined in section 6.15, NHSBT reserve the right to engage with a third party contractor to undertake works recovering all costs from the PPM/Reactive Maintenance Contractor.  Should the Contractors failings result in the loss of Product provided by NHSBT, NHSBT reserve the right to claim such costs from the Contractor.

6.13	Spares & Consumables

The Contractor shall, during the mobilisation period, collect details of all spares required to ensure that NHSBT sites can be maintained with minimum disruption to service. The Contractor shall also make NHSBT aware of any equipment where spares could be difficult to obtain. In addition, NHSBT will make the contractor aware of any spares identified as specific to the organisation. A complete and current list of such spares shall be maintained by the Contractor, a copy to be made available to NHSBT on request. Replacement spares shall be ordered as soon as possible, when such spares are used.  E&F are to agree manufacturers and suppliers of spares to be held on site.

The Contractor will be aware that the main Blood Centres and other specific premises are critical to the operation of NHSBT and that all practical means must be in place, including provision of spares, to ensure any disruption is kept to a minimum.  The Contractor must advise NHSBT on how their supply chain operates throughout their organisation, its carbon footprint and its ability to satisfy any demand on these essential parts.

The Contractor will make adequate provision for the supply and utilisation of consumable materials and equipment to ensure the optimum efficiency and effectiveness of the assets at all times. Consumables will include:

- Oils and grease

- Cleaning materials and equipment

The Contractor will make provision within the tender cost for all service consumable materials, equipment and tools in accordance with the maintenance specification.

For clarification the following are not classed as consumables and will be subject to reimbursement from NHSBT:-

- filters

- lamps

The Contractor is to manage the areas in which spares and consumables are stored and will ensure these areas are kept in a clean and tidy condition, items that may be required in emergencies must be easily accessible. Disposal of any waste created in this regard will be the responsibility of the Contractor and must be carried out in line with current legislation.

  - Records:  Overview

It is a requirement for demonstrating activities have been done and completed by completing records that allow decision making as to whether an asset is fit for use.  The provision of records enables an audit trail of activity and decision making to be seen.  Therefore, records are a vital part of the process and must be clearly made, stored, reconciled and be available for retrieval for set periods of time.  All records made must be retained in the NHSBT Estates & Facilities office and be provided for inspections and audits etc.

All PPM and recording documentation are the property of NHSBT and are to be available at all times.

Contractor’s records will be required to inform a number of separate audits, which will include audits by NHSBT’s Quality Assurance Department, the MHRA and E&F Management. Please note this is indicative and may include other accrediting/auditing authorities as required. The Contractor will be expected to self-audit and provide reports on a monthly basis.  These will be reviewed by the E&F site based staff.

The Contractor will be required to complete and maintain documentation issued by NHSBT which will enable records to be kept up to date. The Contractor shall also provide NHSBT with such reports as are required by this specification, including the Monthly Report and an annual condition survey, while also making NHSBT aware of any necessary changes to the Asset List. It is emphasised that these Monthly Reports are important to NHSBT and will be expected to be made available in a timely and regular manner and a minimum of three working days in advance of scheduled monthly meetings.

A quarterly review will be undertaken by the Regional Estates & Facilities Manager (REFM) and the Contractor to discuss contract performance and KPIs .  Contract reviews will be held at a six-monthly frequency with the REFM, the Procurement Management Team and the Contractor.

The six monthly reviews will include but not be limited to the following section headings:-

- Production of overview report

- Office audit

- H&S

- QA

- Complaints

- Performance

- Finance

- Innovation

    - Records: General

All records, data & information will remain the property of NHSBT during and after the contract period.   All such information will remain confidential and can only be shared with third parties with the permission of NHSBT.

Drawings, Manuals & PPM Records:

All available Building Services Record Documentation, including drawings and manuals in NHSBT’s possession, shall be made freely available to the Contractor for use in maintaining the property, with the proviso that it remains on site at all times as the property of NHSBT.

The Contractor shall provide NHSBT with updates and information on a monthly basis to allow for the update of all drawings and manuals. In this respect, the update shall comprise of amendments to the documentation highlighted in a clear and accurate manner, reflecting the requirements of BS7671, for example.  All such records shall be kept on site and remain the property of NHSBT.

The Contractor should utilise a Management/Quality system that ensures the efficient and smooth running of the contract together with a full audit trail of all activities.

The CAFM system will produce a 53 week planner, indicating on a weekly basis for the full Contract Period the service intervals of all plant, will be utilised. This will enable all concerned to assess the labour and/or materials requirements of site, identify the tasks to be performed and dates of planned site visits. Where these include the attendance of an inspector or relevant third party, it will be the responsibility of NHSBT to arrange their attendance.

Site log books shall be maintained in a suitable agreed location and must be completed by the Service Engineer.  The logbook is to include all Specialist Sub-Contractor’s maintenance visits and the Contractors Risk Assessments, Permits-to-Work and COSHH details etc.  (NHSBT reserves the right to update our current paper based system to electronic data capture systems).

The Contractor will also be responsible for the completion of the site’s fire and water hygiene log-books, also any other relevant records which may be required to ensure NHSBT remains compliant with both Statutory and GMP requirements.

A copy of a typical logbook is available for inspection.  Log books will be provided by NHSBT.

The Contractor shall be responsible for ensuring all electronic and Engineer’s paper worksheets are completed to the requirements of Good Manufacturing Practice and Good Documentation Practice. All records must be clearly legible and fully describe any actions taken and the status of the plant and equipment as it has been left.  The Contractor will also be responsible for the provision, management and correct completion of all site log books.

Tippex or other correction fluid must not be used to change any records or documentation - All worksheets must be completed using blue or black ink, any amendments must be initialled and dated.

All documentation will require version/date control and be provided in line with Good Documentation Practice.

6.15	Performance monitoring (SLA & KPI’s)

NHSBT will undertake site inspections to review the performance of the Contractor/Contract.  Key Performance Indicators will be used to measure performance on the contract, a copy of these are in Appendix 5.  NHSBT reserves the right to revise these measures at any time within the contract following negotiation with the Contractor.

- With regard to attendance on reactive calls the Contractor will make due allowance for ensuring timely close out of calls in accordance with NHSBT requirements.

- IT provision and an email link will be made available for the Site Engineers to access to NHSBT IT system to facilitate prompt closure of tasks on the CAFM system.  This will be the primary reporting tool.  Suitable and sufficient information should be entered in this to allow for follow-up action.

- All monthly reporting is to be in an agreed electronic format.

All KPI’s will be measured against the performance of the Contractor on a Region by Region basis.

The Service Level Agreement for responses to Reactive maintenance calls will be as follows:-

| Priority Classification Response Time Help Desk Requests / PPM | Response Time |
| --- | --- |
| 1 | Investigate and make safe within 1 hour of notification by telephone, call. Restore/repair or provide temporary alternative to E&F within 3 hours of making safe. This priority is used for Emergency call outs where operational conditions may be impacted on. |
| 2 | Investigate and restore/repair or provide temporary alternative to E&F, within 24 hours / 1 working day of notification of telephone call. |
| 3 | Investigate and restore/repair or provide temporary alternative to E&F, within 72 hours / 3 working days of notification of telephone call. |
| 4 | Investigate and restore/repair or provide temporary alternative to E&F within 5 working days. PPM - 5 Working Days (Main Sites only) |
| 5 | 20 Working Days (Remote Sites: Start Date 1st Month) PPM only. |
| 6 | Investigate & respond to complaints 10 working days. |

NHSBT, as part of its normal operating procedures, will undertake performance measuring which includes audits of the properties within the contract. These will be carried out at such times as deemed necessary, with or without notice to the Contractor, to ensure satisfactory performance by the Contractor.  Where the Contractor is given notice of the audits, the Contractor is to make available their Operatives to open up plant as required for NHSBT’s inspection.

PPM tasks for main sites are to be completed within 5 working days of the task start date.  PPM tasks for all other sites are to be completed within 20 working days of the task start date.  Service documentation must be provided within 10 working days of completion of the task.  Scheduled PPM tasks for premises other than main sites are to be agreed in writing with the associated Main site EFM or Deputy EFM.

Information will be drawn from NHSBT’s CAFM system to inform performance on PPM and Reactive activities and compliance with Priorities. The provision of information and the performance of sub-contractors will also be considered in this measure.

- Use of NHSBT Specialist / Approved Contractors

Some items of plant are key to the operation of the site and will continue to be maintained by Specialist Contractors who are directly appointed by NHSBT. There will be occasions when the Specialist Contractor will require support from the Maintenance Contractor. See section 9 for details.  This Specialist Contractor may be used in the installation of new systems or equipment.

The Contractor will be made aware that on specific buildings / installations / equipment, warranties may exist. These must be taken into consideration when attending to repairs.  NHSBT will make the Contractor aware of such warranties and will agree the processes relevant to carrying out planned maintenance, reactive repairs and emergency repairs. The Contractor shall ensure that all relevant staff are aware that such arrangements may be in place. Such warranties may include specific equipment, complete installations and building fabric/roofing. The Contractor should be aware that to comply with the warranty arrangements, they may be requested to engage a Specialist Contractor to undertake maintenance for the duration of the Warranty or Defects Maintenance Period.

8.0	Use of Sub Contractors by the Main Contractor

For certain items of plant or equipment the Contractor may choose to employ Specialist Subcontractors (to be approved by NHSBT) to carry out specific elements of work. The Contractor must have ‘back to back’ contracts with these Subcontractors so that the Subcontractor is working to the same performance criteria as the Contractor.  This will include but not be limited to the following:

- Thermal imaging

- Roller shutter doors

- Lifts

- Generators

- Chillers Main Plant (not DX systems)

- Car Park Barriers

- BMS controls - The on-site operator will be allowed day to day access to the system but the servicing is expected to be carried out by specialist contractor

- Water Purification

- Fire Alarms installation

- Catering equipment

- CCTV

When attending remote sites, it is a key criterion of the contract that the Subcontractors visit is scheduled to coincide with that of the Contractor’s engineer.  This will prevent any issues over access to unmanned sites.

Any Subcontractor within this contract, appointed by the Contractor, is to fully comply with NHSBT requirements in respect of Health & Safety, GMP and other stipulations.

A comprehensive list of any proposed subcontracted works and Subcontractors to be used must be provided with the tender return. Any changes to the Subcontractors must be agreed with NHSBT during the life of the contract. The Subcontractors must not in turn sub-let their works without the express agreement of NHSBT.

9.0                  Liaison with Other Parties – NHSBT Specialist Contractor & NHS

Trusts and Landlord bodies

The Contractor must work in partnership with NHSBT appointed Contractors and other parties when carrying out certain maintenance tasks. These include but are not limited to:

- Mobile generator supply connection – Aggreko- SPEC

- Security – G4S

- Water Hygiene – Hydrop, Water Scientific

- Fire Safety - Tenos

- Asbestos – Safer Spaces

- Pressure Vessels – Zurich Insurance

- Lifting Equipment – Zurich Insurance

- Liquid Nitrogen Systems – Air Products

- LEV testing / maintenance – Jasun Envirocare PLC

It should be noted that on a number of sites, services, such as mains water, are provided by the landlord or host NHS Trust. The Contractor must allow for liaison and agreement where maintenance or minor works may affect these services.

10.0	Equipment on loan

If the Contractor agrees to provide replacement equipment on temporary basis while the services are being carried out on NHSBT’s own equipment, such provision shall be deemed to be a contract for the hire of goods as defined by section 6 of the Supply of Goods and Services Act.

11.0	Contract Management and Client Team

This contract will be administered by NHSBT Estates and Facilities Department. This is structured regionally as Appendix 3.

- Instructions to the Contractor

It will be the Contractor’s responsibility to establish if TUPE applies to any of the Engineers working for the current maintenance provider on allocation of contract.

Where requested by the E&F Representative to attend site for reasons other than Planned Preventative Maintenance, for example a breakdown or fault, the Contractor shall accept and act upon the verbal request which will be followed by written confirmation or purchase order in due course.

The Contractor shall not take instructions from any other NHSBT department.

13.0                 Site Visits

It is the Contractor’s responsibility to visit all the main blood Centres and a representative sample of other sites during the tender period.  Specific dates will be agreed with NHSBT to ensure all site visits are accommodated.

Contractors should ensure they are aware of the details of the site/demise and any site-specific access requirements.

14.0	Contract Variations

NHSBT may wish to vary the frequency or number of inspections for particular plant and may add to or remove from the issued asset list items. The contract will allow for NBSBT to make any relevant plant/equipment changes within sites.

NHSBT will apply in writing for these variations: the Contractor will respond to NHSBT within five working days, with the cost adjustments that will be added to the basic price of the Contract.

All variations to the basic price of the Contract will be charged pro-rata on a monthly basis by the number of complete months that have passed since the last anniversary of the Contract. A variation will only be introduced when the variation procedure has been completed in full.

The Contractor shall within the tender return propose a pricing mechanism to detail how variations to assets will be calculated.

Where new assets are to be added to the contract, the Contractor must ensure that the assets are maintained and inspected at the correct frequency, in line with manufacturer’s recommendations and the SFG 20 schedule.

15.0	Health & Safety

NHSBT operates in a strict risk-based health and safety environment and in carrying out the contract works the Contractor shall be responsible for, and strictly comply with, all safety, health and welfare measures.  The Contractor shall provide as part of the contract Risk Assessments, Method Statements and COSHH data sheets/registers relating for all maintenance tasks with due consideration for environmental impact. This will be provided no later than one month from the commencement of the contract and for each site. These will also be provided for minor works extra to contract prior to project commencement.

The Contractor will ensure that all doors, ducts, cupboards giving access to electrical, mechanical or other equipment are kept locked unless work is being carried out. The Contractor will carry out periodic inspections, as part of the PPM schedule, to ensure that all such areas are free of waste materials, chemicals and other goods which should not be stored there.

All Contractors and sub Contractors will comply with NHSBT Health & Safety Policies and Procedures. Contractor H&S audits are to be undertaken and reported to the E&F Operational Development Group.

The Contractor shall include within the contract sum for the removal and disposal of all redundant equipment and consumable materials, including lamps, filters, oils, etc. in line with current legislation.

16.0		Permits to Work / Authority to Work

NHSBT operates a Permit to Work / Authority to Work system. The Contractor, however, is to produce their own Permit to Work/Authority to work system for use at the properties within the Contractor’s area of responsibility. The format and operation of which shall be agreed with NHSBT. The permits are to include but not be limited to:-

- Restricted Areas

- Confined Spaces

- Roof Access

- Fire Alarm / Extinguishment Isolation

- HV/LV Working

- Hot Working

- Pressure Vessels

The Contractor’s Operatives and Subcontractors will comply strictly with the conditions imposed by Permits to Work. Hot works will only be allowed with the specific agreement of the NHSBT Representative and where appropriate precautions have been taken to avoid activation of fire alarm systems.

  - Fire Safety

The Contractor shall ensure that Employees or Subcontractors comply with NHSBT Fire Safety Management Plan (FSMP) given in MPD 705. Training in this will be provided through the local E&F office.

All combustible refuse shall be collected and removed from the site as soon as is practicable.

If at any time the Contractor, their Employees and Subcontractors notice

anything they consider could be a potential fire risk, it must be reported immediately to an NHSBT Representative.

The Contractor shall strictly comply with any regulations which govern the storage

of explosive, or other high risk materials brought on to the site.

The Contractor’s Employees and Subcontractors must familiarise themselves with the procedures to be followed in the event of a fire alarm being raised on the Site and if required must attend training lectures.

The Contractor will be required to liaise with NHSBT’s nominated Fire Specialist.

Contractor’s staff, working permanently on a site, must complete NHSBT Fire Training to ensure awareness of the dangers of fire, the precautionary measures to be taken and the action to be followed in the event of fire.

16.2	Induction & Training

The tenderer shall allow within their tender costs the time and travel for the Employees involved in the Contract to attend NHSBT Patient Safety & Quality and GMP inductions in the week prior to contract commencement (approximately a one hour training session).  All Contractors and Subcontractors must attend PSQ/GMP training before working on a NHSBT site. The Contractor will not be allowed to work on site without this: training must be refreshed on an annual basis. Records of the date training was issued and the date for its renewal will be held on a NHSBT database, contractors will be asked to attend training prior to commencing work if training is not current.  Contractor’s site engineers will be required to be included within the E&F training matrix held centrally within NHSBT.  As and when NHSBT procedures are updated, update training of the Contractor will be required.

All key staff working on behalf of the Contractor and related to the contract must attend NHSBT’s ‘Blood Centre Tour’ during the first three months of the contract.

16.3                 Staff

The Contractor will be required to include in their return for the provision of Site Engineers based on all Main Blood Centres as noted in Section 6.  Normal working day cover, for each centre is identified in the table below.

- The Site Engineers are to be employed as site specific and to work normal hours; this will usually comprise of a five day week and be capable of undertaking all PPM activities. When not employed on PPM work the Engineer is to be employed by the E&F Manager on Reactive tasks as required.

- The Site Engineer must not be employed by the Contractor on any work other than PPM and relevant Reactive works.

- Minor Works and Projects are to be carried out by other staff.

- The Contractor is to provide sickness cover, when over three days, cover for training leave and holiday cover for the Site Engineer, such costs will be included in the Tender Return. The Site Engineer must be able to demonstrate effective and full use of their working day and be able to show a proactive approach. If a Handyman requires assistance the Site Engineer is to assist as required by the E&F representative.

The Contractor is to include for any “two man” PPM tasks within their tender price.

Space will be made available by E&F which will include a desk, chair, filing cabinet and IT facilities for the Engineer allowing good communication on the contract.

The Site Engineer must also be capable and trained in the co-ordinating visits from colleagues and Subcontractors.  They will also receive training in updating records and supplying certification to NHSBT administrators, allowing updates the CAFM system.  A mobile smart phone is to be provided by the Contractor for the exclusive use of the Site Engineer.

The Contractor’s Employees, Visitors and Subcontractors can use the toilets, showers and restaurant while working at NHSBT by arrangement with the E&F Representative. Dirty work clothing will not be allowed in the restaurant at any time. Any abuse of the building’s facilities will result in the person’s withdrawal from site. The Contractor will then have to make alternative welfare arrangements.

While on NHSBT premises the Contractor shall comply, and shall ensure that its staff comply, with the requirements of the Health and Safety at Work Act 1974 and other relevant legislation, including current regulations and codes of practice, and with NHSBT’s policies and procedures.

All visiting Contractor’s and/or Subcontractor’s staff shall report to the E&F Office or agreed Authorised Representative on arrival and departure from the premises. Contractors must ensure that they sign in as required at NHSBT premises and that E&F are aware of their presence on site.

The Contractor shall cause as little interference as possible with other activities on the premises.

The Contractor shall instruct their staff about fire risks.  Smoking is not permitted on NHSBT premises.

NHSBT acknowledges its responsibilities to the Contractor and its staff under the Health and Safety at Work Act 1974 and COSHH (Chemicals or Other Substances Hazardous to Health) 1994.

The Contractor must satisfy the requirements of the Rehabilitation of Offenders Act 1974.

The Contractor will be required to provide NHSBT with a current list of Engineers and their competence to work on specific plant. Certificates of competence for each Engineer will be required to be presented before the contract commences.

NHSBT reserves the right to refuse access to the site for any person and to remove the Individual, or subcontractor, from the Contract.  In this event, the Contractor shall be obliged to make a replacement with a suitably qualified person or Subcontractor meeting with the approval of E&F.

The Contractor will be responsible for immediately notifying E&F of any incident which requires the attention of any emergency service.  In the event of E&F not being immediately available, the Contractor shall contact the relevant service without delay and notify of the incident. The contractor will then contact the duty Critical Incident Manager (CIM) for which contact details will be provided. Steps shall be taken to alleviate the effect of the incident to NHSBT without delay.  A report shall be provided within 24 hours to E&F which shall include a statement by each of the Contractor’s personnel involved detailing the incident and actions taken.

In the interests of security, all Contractors’ personnel shall display an identity card or proof of identity, ideally incorporating a recent photograph and will produce it on reasonable demand.  NHSBT will also provide security passes for permanent based staff and mobile staff who are working permanently on the contract. This will allow movement within buildings having access control.

The Contractor and their employees will comply with all reasonable security requirements, including searches of bags and packages, which might be imposed.  This may also include personal body searches.

The Contractor shall ensure full compliance with current Rules, Regulations and Edicts relating to Safety of Personnel, Safety of Work Practices and Single Working/Lone working.

The Contractor will ensure that all Contractor’s and Subcontractor’s personnel are provided with clean and tidy protective clothing, including safety equipment, overalls will bear the Contractor’s name. All costs to be included within the Contract Price.

When on site, the Contractor’s staff will comply with NHSBT’s emergency procedures.  They will attend at the agreed assembly point on hearing the fire alarm and will assist NHSBT’s staff in directing the emergency services on matters such as isolation points etc.

The Contractor’s Operatives shall not bring children, or others who are not employed by the Contractor, on to NHSBT properties.

Dispute resolution will follow that outlined in the contract documentation.

Details of current Site Engineer Posts:

| Main Site | No. Contractor Operatives (Centre normal working hours) |
| --- | --- |
| Filton | 3 (06:30 hrs – 18:30hrs) |
| Oxford/Southampton | 1 (shared) (08:00hrs – 17:00hrs) |

| Main Site | No. Contractor Operatives (Centre normal working hours) |
| --- | --- |
| Tooting | 1 (08:00hrs – 17:00hrs) |
| Colindale | 1 (08:00hrs – 17:00hrs) |
| Cambridge | 1 (08:00hrs – 17:00hrs) |

| Main Site | No. Contractor Operatives (Centre normal working hours) |
| --- | --- |
| Leeds | 1 (1 shared engineer with Sheffield) (07:00hrs – 16:00hrs) |
| Newcastle | 1 (07:00hrs – 16:00hrs) |
| Sheffield | 2 (1 shared engineer with Leeds) (08:00hrs – 17:00hrs) |

During 2020/21 it is expected the number of operatives will need to be reviewed with the successful contractor for sites at Leeds and Sheffield.  This will be the result of the strategic decision to move to a single site in the Barnsley area which will necessitate decommissioning of the existing Leeds and Sheffield Centres.  Please note the Leeds / Sheffield areas include crucial stand-alone Donation Centre properties at Leicester, Nottingham, Bradford, Sheffield and Leeds which will not be affected by the closures. In addition, the strategy will require two new team bases to be leased, one in Leeds, and one in Sheffield.

| Main Site | No. Contractor Operatives (Centre normal working hours) |
| --- | --- |
| Liverpool | 2 (07:00hrs – 17:00hrs) |
| Manchester | 2 (07:00hrs – 16:00hrs) |
| Birmingham | 1 (08:00hrs – 17:00hrs) |

17.0 	Price and payment

Pricing schedules are included separately and required to be costed separately for all sites.

The tender return will need to include all costs, and be split to show:-

- PPM costs per asset (as per priced asset sheets – Appendix 4 )

- Costs for PPM tasks which occur at periods in excess of one year (e.g. 2 Yearly and 3 Yearly). Please note that the cost for 5 Yearly electrical fixed wire testing & periodic chlorinations are to be provided separately.  NHSBT will confirm if such works are to be carried out by the Contractor.

- Hourly Rate Schedules, which include Labour rates for normal working hours and overtime rates and subcontract on-cost, call out rates, etc, will be provided. Travel time is deemed to be included within any call outs.

NB: Abortive costs, where relevant and in respect of site visits, shall be agreed with the NHSBT representative. These shall only be chargeable in situations where the contractor is not at fault

The contract price for the services shall be final, inclusive and without prejudice to the generality of the foregoing. It will include all labour charges, travelling, other costs and expenses incurred by the Contractor unless otherwise stated. Consumables/Materials will be charged at trade prices including all Contractors’ immediate and cumulative / retrospective discounts plus the Contractor’s on cost.

Any invoice shall be rendered on the Contractor’s own invoice form to NHSBT, clearly marked with NHSBT’s order number and to an agreed format.

NHSBT may choose to pay the contract price to the Contractor by BACS (Bank Account Clearing System). This will be by monthly instalments in arrears (unless otherwise stated) provided that the invoice specified in condition 24 has been received and approved.

Additional works above the contract price will be paid within one month of NHSBT agreeing the invoices and on the basis that the works are complete and relevant completion certificates have been received.

When, under the terms of this or any other contract, any sum of money shall be deemed recoverable or payable by the Contractor, the same may be deducted from any sum then due. This may be deducted from the next monthly instalment or from any payment which at any time thereafter may become due to the Contractor.

| The following shall apply to the Key Performance Indicator measures for the contract. The table indicates the minimum acceptable limits and shall be measured on a ‘calendar month’ basis. |  |
| --- | --- |
| For all GMP/ Critical Plant PPM | KPI 100% |
| Overall Performance | KPI 85% and above |
| Any single failure to meet either of the criteria noted above will result in a deduction of 5% of the total monthly contract value for the month in which the failure was noted. |  |
| Additionally, should the KPI overall performance fall below 70%, the full value of the total monthly contract value will be withheld until all the works are completed or the overall contract performance exceeds the minimum acceptable level – the value of any non recoverable tasks will be deducted. |  |

18.0 		Defects Liability Period

All new items of plant and equipment, extra to the provided equipment schedule, put into operation before the completion of the Contract must be maintained as directed by NHSBT’s Representative. The Contractor shall be fully conversant with items of plant and equipment which are under manufacturer’s warranties and, to retain any warranties, items of plant requiring maintenance shall be strictly in accordance with manufacturer’s recommendations.

Should the Contractor find, during their routine maintenance, an item of plant is considered defective, NHSBT should be notified in writing. Where relevant, the defects liability period is typically 12 months from commencing the applicable Contract or date of purchase, however this is subject to individual contract conditions.

Should the Contractor replace any item of plant or equipment, the defects liability period is typically 12 months commencing from practical completion of those works. This is subject to warranties and the provision of the required level of maintenance, also any prevailing or specific contract conditions.

Major servicing on new equipment will be carried out as recommended by the manufacturer for the length of the warranty period, or the first year of the Contract. This may be carried out by the manufacturer or his approved agent. This will be done with the approval of NHSBT’s representative. The Contractor will usually be required to carry out routine maintenance on any and all plant. Additions to plant to be maintained will follow the agreed variation process.

19.0 General Information

Payment

Planned Maintenance

The Contractor will submit monthly invoices for each main blood centre and their associated satellite sites within 10 working days of the end of the month being invoiced. This will be equivalent to 1/12th of the lump sum.  NHSBT will make payment within 30 working days. However, payment of this sum in full may be subject to auditing of the provision of the PPM programme, as detailed within the tender documentation and this specification.

Reactive and Minor works

The Contractor will submit invoices for reactive work carried out at each main blood centre, and its associated premises, within 4 weeks of the reactive work being completed.  The Contractor must demonstrate in each case that they have taken full provision of the inclusive elements, where appropriate, of the contract terms and conditions.  NHSBT will reject any invoices for reactive and minor works that are received over 8 weeks from the completion date.

Information

The following information can be viewed during the site visits in the tender period:-

- Contractor monthly report

- H&S policies and procedures

- GMP Induction training modules,1 to 3

- Relevant MPD’s and SOP’s

- Computer Aided Facilities Management information system

20.0 Appendices

Appendix 1

Appendix 2

Number of portable appliances by region

Appendix 3

Management Structure of NHSBT Estates and Facilities Department

Appendix 4

Appendix 5

KPI’s