## Tab 1 - Instructions
Instructions
Please see below instructions for the various tabs in this spread sheet.
Tab 2 - Basket
1. Enter a price for each individual filter (Colum M)
2. If the product you are pricing for varies the spec in Colum's B to K please detail variations in column L.
3. Enter your product code in column K
Tab 3 - Discounts
1. A discount structure for related products in required
2. Enter the highest discount available for category in Tab 3 - Discounts
Tab 4 - Fitting and Removal
1. The cost for fitting and removal mist be interred in Tab 4 Fitting and Removal. Note that the prices for fitting and removal are based on a real room exercise, the details are in Tabs 5 to 6.
2. The price should be based on the assumption that only one person is required to do the job.
3. You will not require to carry out any maintenance work during the fitting, however should you encounter / come across any faults or elements that may need maintenance or replacement you will be asked to provide a written report to contact person.
4. Please note that the AHU is in an accessible plant room location, which will require no special access equipment e.g. ladders etc. and service work can be carried out during normal working hours, in this case 8:00 am to 5:00pm. Parking is available on site
Pricing
Prices will be required to be entered as a single figure in the required tabs
If a range is enter either clarification will be requested or the highest value in the range quoted will be used for the purpose of scoring.
If clarification is requested and is not provided within the timescale given the highest value in the range quoted will be used for the purpose
If no price is provided the average price of all suppliers will be used in the purpose of scoring
All prices should be net of any discount offered
All discounts provided must be the highest discount available
All prices submitted must be in Sterling and exclude VAT
Scores will be calculated using the following formula:
Lowest Total Price Received / Total Price to be Scored x 50 % = Total Score
All marks and weightings will be calculated to two decimal places.

## Tab 2 - Basket
Air Filter Basket of Goods
Bag Filters
Item Number | Media Area (m2) | Dimensions (w x h x d) (mm) | Filter Classification EN779:2012 or Equivalent | Maximum Airflow (m³/h) | Initial Pressure drop (Pa) | Final Pressure Drop (Pa) | Case Material | Media Material | Header Size (mm) | Number of Pockets | Product Code | Price | Comments / Variations from Details
1 | 2.6 | 592 x 287 x 535 | F8 | 1350 | 147 | 250 | Galvanised Steel | Micro Glass | 25 | 4
2 | 6.4 | 592 x 592 x 635 | F9 | 3400 | 170 | 250 | Galvanised Steel | Micro Glass | 25 | 8
3 | 11.4 | 490 x 892 x 640 | M6 | 4100 | 50 | 450 | Galvanised Steel | Glass Fibre | 25 | 10
4 | 13.7 | 592 x 892 x 640 | F7 | 5000 | 85 | 450 | Galvanised Steel | Glass Fibre | 20 | 12
5 | 3.7 | 592 x 592 x 520 | G4 | 3400 | 30 | 250 | Plastic | Polyester Fibre | 25 | 6
6 | 7.5 | 592 x 592 x 640 | F7 | 3400 | 85 | 250 | Plastic | Fibreglass and carbon | 32 | 10
7 | 6.2 | 592 x 592 x 520 | F7 | 3400 | 105 | 450 | Galvanised Steel | Glass Fibre | 20 | 10
8 | 4.9 | 490 x 592 x 520 | F7 | 2700 | 110 | 250 | Plastic | Fibreglass and carbon | 20 | 8
9 | 9.1 | 592 x 592 x 640 | F7 | 3400 | 85 | 450 | Galvanised Steel | Glass Fibre | 32 | 12
10 | 13.7 | 592 x 892 x 640 | F7 | 5000 | 85 | 450 | Galvanised Steel | Glass Fibre | 32 | 12
Pleated Panel Filter
| Media Area (m2) | Dimensions (w x h x d) (mm) | Filter Classification EN779:2012 or Equivalent | Maximum Airflow (m³/h) | Initial Pressure drop (Pa) | Final Pressure Drop (Pa) | Case Material | Media Material |  | Number of Pleats | Product Code | Price | Comments / Variations from Details
1 | 2.56 | 594 x 594 x 98 | G4 | 4140 | 90 | 250 | Water Resistant Cardboard | Cotton and Synthetic Fibre
2 | 0.83 | 594 x 594 x 23 | G4 | 2600 | 65 | 250 | Water Resistant Cardboard | Cotton and Synthetic Fibre
3 | 1.12 | 495 x 495 x 48 | G4 | 2340 | 70 | 250 | Water Resistant Cardboard | Cotton and Synthetic Fibre
4 | 1.2 | 610 x 610 x 48 | G4 | 3600 | 48 | 250 | Galvanized steel | Cotton and Synthetic Fibre
5 | 2.4 | 610 x 610 x 96 | G4 | 3600 | 45 | 250 | Plastic | Cotton and Synthetic Fibre
6 | 0.53 | 305 x 610 x 50 | G4 | 1620 | 70 | 250 | Water Resistant Cardboard | Cotton and Synthetic Fibre
7 | 0.63 | 406 x 508 x 50 | G4 | 1830 | 70 | 250 | Water Resistant Cardboard | Cotton and Synthetic Fibre
8 | 0.91 | 508 x 610 x 50 | G4 | 2750 | 70 | 250 | Water Resistant Cardboard | Cotton and Synthetic Fibre
9 | 0.6 | 287 x 592 x 48 | G4 | 1700 | 55 | 250 | Plastic | Cotton and Synthetic Fibre
10 | 2.3 | 592 x 592 x 96 | G4 | 3400 | 45 | 250 | Plastic | Cotton and Synthetic Fibre
Panel Filter
| Media Area (m2) | Dimensions (w x h x d) (mm) | Filter Classification EN779:2012 or Equivalent | Maximum Airflow (m³/h) | Initial Pressure drop (Pa) | Final Pressure Drop (Pa) | Case Material | Media Material |  |  | Product Code | Price | Comments / Variations from Details
1 | 0.19 | 305 x 610 x 25 | G2 | 1200 | 45 | 250 | Water Resistant Cardboard | Glass Fibre
2 | 0.21 | 406 x 508 x 50 | G3 | 1400 | 50 | 250 | Water Resistant Cardboard | Glass Fibre
3 | 0.32 | 508 x 635 x 50 | G3 | 2100 | 50 | 250 | Water Resistant Cardboard | Glass Fibre
End Of Document

## Tab 3 - Discount
Discounts
Provide the discounts available under the appropriate category headings below.
Product Category | Discount Percentage
Primary Filters
Secondary Filters
Final Filters
Carbon and Chemical Filters
Bags for changing the Filters
Self-cleaning air filter cartridges
Housings / Frames
Air Purifier
The discount should be a single figure (i.e. not a range of figures) and expressed as a percentage to two decimal places

## Tab 4 - Fitting and Removal
Price list
Price
Air Filters
Man Power 1 Hour
Man Power 2 Hours
Man Power 3 Hours
Man Power 4 Hours
Man Power 5 Hours
Man Power 6 Hours
Man Power 7 Hours
Man Power 8 Hours
Removal and Disposal

## Tab 6 - AHU Requirements
Requirements of the AHU Unit
Requirements
Supply Air :- |  | Exhaust Air :-
Filter Location No.1 | Filter Location No. 2 | Filter Location No. 3
Size: 063 | Size: 063 | Size: 063
Filter length: pleated filter | Filter length: Long bag (vertical pockets only) | Filter length: pleated filter
Filter class: G4 | Filter class: F7 | Filter class: G4
Filter type: synthetic, cleanable | Filter type: glass fibre, standard | Filter type: synthetic, cleanable
Drain tray: without | Filter frame : plastic | Drain tray: without
Material: galvanized sheet steel | Inspection side: inlet in end wall | Material: galvanized sheet steel
Inspection side: left | Location: negative pressure | Inspection side: right
Number of filters 6x592x592, 2x287x592 | Prefilter: without | Number of filters 6x592x592, 2x287x592
Pressure drop, start 54 Pa | Drain tray: without | Pressure drop, start 51 Pa
Pressure drop, dimensioning 89 Pa | Material: galvanized sheet steel | Pressure drop, dimensioning 86 Pa
Pressure drop, end 124 Pa | Inspection side: left | Pressure drop, end 121 Pa
Face area 2.5 m² | Number of filters 6x592x592, 2x287x592 | Face area 2.5 m²
Face velocity 2.5 m/s | Pressure drop, start 69 Pa | Face velocity 2.3 m/s
Pressure drop, dimensioning 119 Pa
Pressure drop, end 169 Pa
Face area 2.5 m²
Face velocity 2.4 m/s