| 375767 |  | 002 | D |  |
| --- | --- | --- | --- | --- |
|  | Mott MacDonald |  |  |  |

Mott MacDonald 22 Station Road Cambridge CB1 2JD United Kingdom

T +44 (0)1223 463500

F +44 (0)1223 461007

mottmac.com

Defence Infrastructure Organisation Bazalgette Pavilion RAF Wyton Huntingdon PE28 2EA

RAF Lakenheath Repair Protective Aircraft Shelters (PAS)

DIOCB2/078 Works Information

12 November 2018

Mott MacDonald Limited. Registered in England and Wales no. 1243967. Registered office: Mott MacDonald House, 8-10 Sydenham Road, Croydon CR0 2EE, United Kingdom

Defence Infrastructure Organisation

Issue and Revision Record

| Revision | Date | Originator | Checker | Approver | Description |
| --- | --- | --- | --- | --- | --- |
| A | 24 May 2018 | N Griffith | R McMenamin | J Hunter | First Issue (Design Brief) |
| B | 29 June 2018 | N Griffith | R McMenamin | J Hunter | Second Issue |
| C | 18 Sept 2018 | N Griffith | R McMenamin | J Hunter | Draft to Tenderers |
| D | 12 Nov 2018 | N Griffith | R McMenamin | J Hunter | Issue for ITT |

| Document reference: | 375767 ¦ 002 ¦ D |
| --- | --- |

| Information class: | Standard |
| --- | --- |

This document is issued for the party which commissioned it and for specific purposes connected with the above-captioned project only. It should not be relied upon by any other party or used for any other purpose. We accept no responsibility for the consequences of this document being relied upon by any other party, or being used for any other purpose, or containing any error or omission which is due to an error or omission in data supplied to us by other parties. This document contains confidential information and proprietary intellectual property. It should not be shown to other parties without consent from us and from the party which commissioned it.

This Report has been prepared solely for use by the party which commissioned it (the 'Client') in connection with the captioned project. It should not be used for any other purpose. No person other than the Client or any party who has expressly agreed terms of reliance with us (the 'Recipient(s)') may rely on the content, information or any views expressed in the Report. This Report is confidential and contains proprietary intellectual property and we accept no duty of care, responsibility or liability to any other recipient of this Report. No representation, warranty or undertaking, express or implied, is made and no responsibility or liability is accepted by us to any party other than the Client or any Recipient(s), as to the accuracy or completeness of the information contained in this Report. For the avoidance of doubt this Report does not in any way purport to include any legal, insurance or financial advice or opinion. We disclaim all and any liability whether arising in tort, contract or otherwise which we might otherwise have to any party other than the Client or the Recipient(s), in respect of this Report, or any information contained in it. We accept no responsibility for any error or omission in the Report which is due to an error or omission in data, information or statements supplied to us by other parties including the Client (the 'Data'). We have not independently verified the Data or otherwise examined it to determine the accuracy, completeness, sufficiency for any purpose or feasibility for any particular outcome including financial. Forecasts presented in this document were prepared using the Data and the Report is dependent or based on the Data. Inevitably, some of the assumptions used to develop the forecasts will not be realised and unanticipated events and circumstances may occur. Consequently, we do not guarantee or warrant the conclusions contained in the Report as there are likely to be differences between the forecasts and the actual results and those differences may be material. While we consider that the information and opinions given in this Report are sound all parties must rely on their own skill and judgement when making use of it. Information and opinions are current only as of the date of the Report and we accept no responsibility for updating such information or opinion. It should, therefore, not be assumed that any such information or opinion continues to be accurate subsequent to the date of the Report. Under no circumstances may this Report or any extract or summary thereof be used in connection with any public or private securities offering including any related memorandum or prospectus for any securities offering or stock exchange listing or announcement. By acceptance of this Report you agree to be bound by this disclaimer. This disclaimer and any issues, disputes or claims arising out of or in connection with it (whether contractual or non-contractual in nature such as claims in tort, from breach of statute or regulation or otherwise) shall be governed by, and construed in accordance with, the laws of England and Wales to the exclusion of all conflict of laws principles and rules. All disputes or claims arising out of or relating to this disclaimer shall be subject to the exclusive jurisdiction of the English and Welsh courts to which the parties irrevocably submit.

Contents

1 WI 100 Description of the Works 1 1.1 General description of the works 1 1.1.1 Existing buildings on the Site 2 1.1.2 Existing mains/services/Ground Conditions 2 1.1.3 Contractor’s responsibilities 2 2 WI 200 General constraints on how the Contractor provides the works 4 2.1 Constraints on how the Contractor Provides the Works 4 2.2 Access to the Site 5 2.2.1 General 5 2.2.3 Access for deliveries 6 2.2.4 Access to the works by Others 7 2.2.5 Driving 7 2.2.6 Working hours 7 2.2.7 Parking 8 2.3 Protection of existing services 8 2.3.1 Commencement condition survey 8 2.3.2 Existing services 8 2.3.3 Taxiways, Hardstandings, Roads and footpaths 9 2.3.4 Trees / hedges / shrubs / lawns 9 2.3.5 Existing features 10 2.3.6 Existing works 10 2.3.7 Building interiors 10 2.3.8 Existing structures 10 2.4 Environmental Constraints 10 2.5 Use of Peat 10 2.6 Security Escorting Requirements 11 2.6.1 Escorting Within Airfield Perimeter 11 2.6.2 Escorting Between Main Gate and Airside Boundary 11 2.7 Site Permits 11 2.8 Considerations of Others 11 2.9 Industrial Relations 12 2.10 Control of Site Personnel 12 2.11 Waste Materials 12 2.12 Deleterious and Hazardous Materials 12 3 WI 300 Contractor’s design 13 3.1 Parts of the works to be designed by the Contractor 13 3.2 Particulars of the Contractor’s design 14 3.2.1 Design generally 14 3.3 General Items 15 3.3.1 Asbestos Survey 15 3.3.2 Building Condition and Land Use 16 3.3.3 Accommodation Considerations and Constraints 16 3.3.4 DREAM requirements 16 3.3.5 Design excellence evaluation process 16 3.3.6 Building Information Modelling 16 3.3.7 Soft landings 16 3.3.8 Force protection measures 17 3.3.9 Definition of “percentage design” 17 3.3.10 Design Review and Acceptance 17 3.4 35% Design 18 3.4.1 General 19 3.4.2 Architectural 19 3.4.3 Civil/Structural 19 3.4.4 Electrical and Mechanical 19 3.5 65% Design Documents 19 3.5.1 General 19 3.5.2 Architectural (Appendix A) 20 3.5.3 Structural and Civil (see Appendix B) 20 3.5.4 Electrical and mechanical (see Appendix C and Appendix D) 20 3.6 95% Design 21 3.6.1 General 22 3.6.2 Architectural (see Appendix A) 22 3.6.3 Electrical and Mechanical (see Appendix C and Appendix D) 22 3.6.4 Civil and Structural (see Appendix B) 25 3.7 100% Design 25 3.8 Design Calculations 25 3.8.1 Maximum Demand calculations 26 3.8.2 Cable calculations 26 3.8.3 Lighting calculations 26 3.8.4 Cable containment 27 3.9 Fire strategy documents 27 3.10 Other construction documents 27 3.11 Waste Management 27 3.12 Working Methods, Method Statements and Permits 28 3.12.1 Existing infrastructure, permit to dig, permit to work 29 3.12.2 Cranes and Construction Equipment 30 3.12.3 Electromagnetic Interference 30 3.12.4 Laser Equipment 30 3.12.5 Powder Actuated Fixing Systems 30 3.13 Behaviour on Site 30 3.13.1 Smoking 30 3.13.2 Burning on site 30 3.13.3 Plant and Machinery 30 3.13.4 Planning/siting approval 31 3.14 Working drawings 31 3.15 Technical literature 31 3.15.1 Building Regulations 31 4 WI 400 Completion 32 4.1 Works to have been finished by the Completion Date 32 4.2 Take over 32 4.2.1 Asset register 32 4.2.2 Transfer and acceptance of property 33 4.2.3 Provisional information on services 33 4.2.4 Training of Employer’s staff 33 4.2.5 Spare parts 33 4.2.6 Tools 33 4.2.7 Deep clean 33 4.3 Operation and Management Manual 34 4.4 Notice of Completion 34 5 WI 500 Programme 35 5.1 Sequencing of the Works 35 5.2 Programme 35 5.2.1 Requirements of the programme 35 5.2.2 Phasing 36 5.2.3 Programme/progress 36 6 WI 600 Quality management 37 6.1 Workmanship 37 6.1.1 General quality of installed Plant and Materials 37 6.1.2 Protection of products 38 6.1.3 General quality of workmanship 38 6.1.4 Samples 38 6.1.5 Samples of finished work 39 6.2 Photographs 39 7 WI 700 Tests and inspection 40 7.1 Tests required 40 7.1.1 Testing, pre-commissioning and commissioning 40 7.1.2 Defects in existing construction 41 7.1.3 Timing of tests and inspections 41 7.1.4 Test certificates 41 7.1.5 Proposals for rectification of defective Plant and Materials 41 7.1.6 Measures to establish acceptability 41 7.1.7 Quality control 42 7.1.8 Work at Completion 42 7.1.9 Security at completion 42 7.1.10 Making good Defects 42 7.2 Notices for Witnessing 43 7.3 Notice of Completion 43 8 WI 800 Management of the works 44 8.1 Site organisation 44 8.1.1 Changes to proposed key works staff 44 8.1.2 Coordination of the works 44 8.1.3 Status and experience of Contractor’s key staff 44 8.2 Site Progress Meetings 46 8.2.1 Reporting Requirements 46 8.2.2 Information Requirements / Electronic Systems and Communications 46 8.3 Aircraft Operations 47 8.4 Foreign Object Damage (FOD) 47 8.5 Climatic Conditions 47 9 WI 900 Working with the Employer and Others 48 9.1 Working with the Employer and Others 48 9.1.1 Liaison with agencies acting for the Employer 48 9.1.2 Furniture, Fittings and Equipment 48 10 WI 1000 Services and Other Things to be Provided 49 10.1 Site accommodation 49 10.1.1 Office, storage and workshop accommodation 49 10.1.2 Room for meetings 49 10.1.3 Site offices for the Project Manager and Employer 49 10.1.4 Sanitary facilities 50 10.1.5 Site security 50 10.1.6 Signage 50 10.2 Services and facilities 51 10.2.1 Lighting and power 51 10.2.2 Water and drainage 51 10.2.3 Communications 51 10.2.4 Use of permanent installations 52 10.2.5 Meter readings 52 10.2.6 Thermometers 52 10.3 Use of the Site 52 10.3.1 Access restriction and use of the Site 52 10.3.2 Site compound and laydown area 52 11 WI 1100 Health and safety 54 11.1 Health and safety 54 11.1.1 Risks to health and safety 54 11.2 Safety Equipment 54 12 WI 1200 Subcontracting 56 12.1 Restrictions or requirements for subcontracting 56 13 WI 1300 Title 57 13.1 Marking 57 13.2 Materials from Strip Out and Demolition 57 Appendices 58 A. General Specification 59 A.1 General Description 59 A.2 General Requirements 59 B. Civil and Structural Engineering Specification 63 B.1 General Requirements 63 B.2 Building Form 63 B.3 Scope of Proposed Structural Works 65 B.4 Detailed Scope of Proposed Structural Works 66 B.5 Design Standards 73 B.6 Design Life 74 B.7 Health and Safety 74 B.8 Deflections 74 B.9 Coordination with services 74 B.10 Exposure conditions 74 B.11 Fire Engineering 74 B.12 Construction Tolerances 75 B.13 Loading 75 B.14 Stability 75 B.15 Substructure 75 C. Mechanical Specification 76 C.1 General 76 C.2 Scope of Works 77 C.3 Mechanical Services Installations to PAS 79 D. Electrical Specification 82 D.1 Building Usage and Design Parameters 82 D.2 Electrical Services Infrastructure Connections 87 D.3 Internal Electrical Installations 89 D.4 Lighting 95 D.5 External Lighting 98 D.6 Emergency Lighting 99 D.7 General (Utility) Power 100 D.8 Aircraft Doors 100 D.9 Aircraft Winches 102 D.10 Mechanical Services 102 D.11 Communications 103 D.12 Fire Alarms 104 D.13 Closed Circuit Television (CCTV) System 104 D.14 Intruder Detection System. 104 D.15 Mass Notification System 105 D.16 Lightning Protection System (LPS) 105 D.17 Earthing (Grounding) 106 D.18 Building Management System 106 E. Fire Precautions 107 E.1 General 107 E.2 Fire Strategy Report 107 E.3 Employer Reviews 108 E.4 Roll of the DSA Fire Safety Inspector 108 E.5 Applicable Fire Regulations 109 E.6 Fire Systems Requirements 109

# WI 100 Description of the Works

## General description of the works

The extent of the Site is shown on drawing: 375767_MMD_00_XX_GIS_GEN_0001_PAS Locations.

The site address is RAF Lakenheath, Brandon, Suffolk IP27 9PP, with the protective Aircraft Shelters (PAS) being located across the Airfield area of the Base.

The PASs at RAF Lakenheath are currently used for housing the F-15 Aircraft. They were originally built in the early 1980’s.

Each Protective Aircraft Shelter (PAS) primarily consists of a single storey, cast in-situ, reinforced concrete, curved barrel vault roof structure approximately 36m long by 22m wide and 9 m high. The shelter has motorised bi-parting, reinforced concrete doors to the front elevation, with a counter-weighted external steel support framework. There are large steel manually opened “blast” doors to the rear elevation serving the efflux chamber. The jet exhaust efflux chamber structure at the rear of each shelter is constructed of reinforced concrete, there is a reinforced concrete generator room to the rear of the efflux chamber accessed by a separate steel external door. There is a single steel personnel door on one side elevation with a reinforced concrete porch.

Inside the shelter there is ventilation, lighting, communications equipment and controls for the front door motors.

The dimensions of the building are approximate.

The principal objectives to repair the PASs for the 48th Fighter Squadron are:

Replacement of the front door motors, roller system,  track and I beam

Repair and replacement, where required, of the rear doors, tracks and rollers

Internal walls/ceiling to be coated with an anti-corrosion and anti-condensation material

Repairs to the rear wall spall plates to remove areas of corroded material, and recoating

Existing floor coverings are to be removed and replaced with anti-slip fuel resistant surfacing and relined

Existing shelter drains are to be blocked up to avoid fuel contamination incidents

Remove the existing winch system

Provide suitable repairs to the Efflux chamber, which have spalled due to jet engine run-up within the shelter

All mechanical and electrical services shall be investigated and systems replaced/upgraded to comply with modern standards. Electrical support beyond shelter operational requirements is to be provided for USVF security system, communications systems and in-shelter floor vaults controls shall be retained and reconnected

Repairs to external concrete walls/roof

Limited works are required to the generator room to the rear of the Efflux chamber

Design Life to first major maintenance:

New concrete base for door tracks 				50 years

Design Life to first major maintenance for equipment		25 years

Coatings to floor and walls					15 years

Repairs to Efflux Chamber					5 years

Single PAS Efflux Chamber trial repair (Option)			25 years

The shelters are to be designed for the F-15E aircraft

DREAM is NOT required.

BIM is NOT required.

- Options subject to funding are as follows:

It is proposed to seal the external walls with a coating to preclude moisture penetration

Under aircraft lighting

A one-off trial for a longer term repair to the Efflux Chamber wall

### Existing buildings on the Site

The 58 No. PASs are located across the airfield of RAF Lakenheath within the flightline restricted area. Each individual PAS is generally surrounded by grass to three sides with concrete hardstanding to the front for aircraft access, and a concrete pad where Aircraft Ground Equipment (AGE) used to be kept externally by the personnel door.

### Existing mains/services/Ground Conditions

Existing mains and/or services shall be as indicated on drawings included within the Site Information. This information shall be indicative only. No assurance can be given for the accuracy of this information. Positions of existing services must be confirmed by the Contractor on Site. Unknown and/or uncharted services may also be present on Site.

The Contractor shall undertake all surveys and testing they deem necessary to satisfy themselves of the capacity and condition of ground conditions and existing services at the Site.

The Works will require the use of utilities from Base-maintained infrastructure, as set out in electrical (Appendix D) sections of this Works Information and drawings.

The Contractor shall carry out a ground penetrating radar survey of the site, including all areas affected by the Works.  The survey shall confirm the exact location of services indicated on the Site Information.  Where the radar locates services below ground the Contractor shall trace these cables to the site boundary.  Where these services are not shown on the Site Information, the Contractor shall provide drawings detailing their exact position and depth, and identifying the type of services to the Project Manager who shall advise what works are to be carried out.

### Contractor’s responsibilities

The Contractor shall be responsible for the design, correct operation and full co-ordination of all services, modification, removal, supply, installation, testing, commissioning, proving, demonstrating and handing over in full working order ready for immediate use of the Works and further detailed requirements as described in the documents included and referred to in this Works Information.

The installation shall be complete in every respect, including all ancillary elements, whether specifically mentioned in the documents or not, necessary for the systems to be tested, balanced, commissioned and perform correctly.

The Contractor shall be responsible for liaising with all relevant public, local and statutory authorities, as necessary and as required by the Works Information.

The Contractor shall liaise with and gain the required approvals from the Employer’s Authorised Persons (APs) throughout the works.  Where AP involvement is known to be required, e.g. for electrical and mechanical works to services, the Contractor shall ensure that liaison with the AP commences at least 4 weeks in advance of the required attendance by the AP.  In addition, the Contractor shall have contingency plans and pre-agreed method statements in place to reduce the “development” of the requirements if unplanned attendance is required.

The Contractor shall provide a design such that all equipment or materials with a common purpose are selected from a single manufacturer’s range of products and, in order to ensure compatibility with existing systems, they should be the same manufacturer and range as used on the existing building where these are retained.

# WI 200 General constraints on how the Contractor provides the works

## Constraints on how the Contractor Provides the Works

The Contractor is to work in accordance with requirements as specified in this Works Information. The Contractor is to adopt and develop the construction phase health & safety plan sufficiently to the agreement of the Project Manager prior to commencement of the works on site.

The project is being delivered through Contractor design. Following award of contract, there will be a period of design.

The Contractor shall agree work areas for different sections of the works with the Project Manager, prior to the commencement of each section. No work shall be undertaken outside the Site at any time without prior authorisation from the lead person at RAF Lakenheath Base and the Project Manager.

All personnel shall require a current Base security pass at all times whilst on Site. An allowance within the programme shall be made for pass applications by the Contractor, as detailed in section 2.2.2. Non-pass holders who have been allowed temporary passes for deliveries shall need to be escorted by the Contractor’s own staff that have previously been cleared.

RAF Lakenheath has a requirement to maintain flight operations that support real world missions and military operations.  Any closure of taxiways or the impediment of air traffic to the runway would have detrimental impact on mission accomplishment.  It is the intent of the USAF to maintain mission operations throughout the entire period of all construction projects.  Any required airfield closures, which includes impediments to aircraft movements either under self-power or towed on taxiways or ramps, shall be pre-planned and coordinated with the 48th FW no later than 60-working days (12 weeks) in advance.  Additionally, if real world mission operations dictate, the Contractor shall cease construction operations and clear closures within 24 hours of any notice. This time frame allows the USAF to consider appropriate arrangements to account for both military operations and works progression.  The Contractor shall ensure strict adherence to these agreements.

RAF Lakenheath shall continue as an operational USAFE Base throughout the period of the works. The roads to the Site and all facilities on the Base shall be in constant use throughout the contract. The Contractor must familiarise themselves with all constraints, confirm all permitted access routes are acceptable and obtain security clearances for all personnel and vehicles entering the Base.

Access to all areas of the Base by Base personnel and emergency vehicles shall not be impeded by the Contractor at any time during the works. The works shall be carried out in a manner to minimise disruption and nuisance to the operational requirements of the Base in particular, and to the life of the Base in general.

## Access to the Site

### General

The main access gate to RAF Lakenheath is to the north east of the Base. Access to the Site shall be from the main entrance, signposted Gate 8, located off the A1065 Brandon Road.

Construction vehicles are to proceed directly to the Site compound. The Contractor is to provide directional signage as agreed with the Employer to the Site compound.

All construction traffic reversing within or outside of the Site compound must be supervised by a Site representative (CSCS qualified/competent banksman).

Mobilisation to Site will be permissible from contract award with access to the Site for mobilisation/enabling and early works to be agreed following project mobilisation meeting. Access will not be allowed to site for construction works until the 100% design package is reviewed and accepted by the Employer and the Contractor shall ensure that sufficient plant and personnel are present for construction to commence in accordance with the programme.

    - Baseline Personnel Security Standard (BPSS) clearance and Site access passes

Each passholder will be entitled to escort privileges for 4 adults holding temporary base passes, which shall not extend to the Air-side section of the base.

The Contractor shall ensure that all personnel mobilised to undertake the works, including all Subcontractors obtain security clearance in accordance with the procedures stated within. The Contractor’s staff and all Subcontractors shall obtain a base pass if they are on site for longer than five (5) days consecutively, with the exception of delivery drivers (see section 2.1.1). These passes shall be specific to the site the staff are required to attend.

For non-List X companies, the Contractor shall confirm if they have SC/CTC cleared (Counter Terrorism Check as a minimum) staff who are approved and trained by the DIO Personal Security Department (PSD) to undertake the BPSS (Baseline Personnel Security Screening) and initiate any required security clearances through the DIO PSD, if not the Contractor shall employ/nominate staff to be SC/CTC cleared and undertake this role on behalf of their company and in either case that they submit to security audit by the PSyAs team.

The Contractor’s main / essential site established staff & all Subcontractors are required to apply for unescorted base passes for the duration of the works. These unescorted passes shall be issued by the site security (48SF) at their discretion.

In order to obtain a pass all personnel shall submit a completed BPSS Form (Form 79 created and accredited by on-site DIO personnel). The Baseline Personnel Security Standard (BPSS) Form shall to be submitted to a nominated point of contact on Base (name to be confirmed on award by the Employer), who shall process the pass application via the base security organisation (48SF).

Following approval of an application, the site security officer will return the paperwork to the nominated point of contact. The Contractor’s staff will be informed when this paperwork has been processed and will be required to attend to collect the paperwork with formal photographic ID. Paperwork shall then be taken by the staff to the Pass & ID office adjacent to the main gate for pass issue.

The Contractor is required to give sixty (60) days’ notice of all members of staff, including Subcontractors, working at or due to be working at the Base. The first submittal of names of staff shall be required with the Contractor’s 65% design-stage submission.

The Contractor shall allow a minimum of two (2) months prior to mobilisation for personnel to obtain BPSS security clearance and shall take account of the requirement to obtain security clearances for all personnel when developing the Program. Typically, the period for obtaining the base pass should be ten (10) working days, however, for the initial batch of Contractor passes to be produced, an allowance of two (2) months shall be included within the Contractor’s programme.

At the Employer’s discretion, the Contractor’s workforce or his representatives may be issued with temporary passes. However, the issue of temporary passes shall not be relied upon and the processes outlined above shall be implemented.

The Contractor shall be responsible for all passes issued to his employees and Subcontractors. The Contractor shall be required to submit a fortnightly report to the security pass issuing authority in order to confirm that each and every pass has been accounted for and seen by a member of the Contractor’s management staff. The Contractor shall be responsible for the recovery and return to the issuing authority of all passes issued to the Contractor’s employees or its Subcontractors who leave his employment.

Passes which are no longer required / valid must be returned to the issuing authority.

The Contractor shall note that admittance to the construction sites is not normally granted to persons under 17 years of age or trainees unless apprentices under full time supervision of qualified and certified tradesperson.

The Contractor’s personnel will not be admitted to the Base if they do not possess a pass, issued in accordance with the above procedures.

Car passes are not required at RAF Lakenheath.

### Access for deliveries

Site passes will also be required for those making deliveries or visiting the Site. Each driver will be required to carry valid documentation requesting access to the Site to enable passes to be issued. The documentation shall include information regarding materials and location of building for which the materials are intended. The following is essential or the delivery lorry will be turned away from the gate:

“Bill of Loading” / delivery notice: this must be a formal commercial invoice, to be presented by the driver, which should state the exact location of the delivery by building number, which is being delivered and the Contractor’s point of contact on the Site, and the telephone number.

When using Base escort facility (alongside Contractor’s escort) for deliveries, pre-announcement by the Contractor to the gate, giving notice of delivery personnel and vehicle details, including the information in the delivery notice.

The Contractor shall ensure that all personnel entering any MOD facilities are in possession of valid photographic identification (i.e. passport or photographic driving licence). Personnel/Deliveries attending site less than 14 times will need to provide photographic ID etc. and be escorted on to site, this will be Contractors responsibility.

The Contractor shall restrict his deliveries such that they do not arrive at the main gate between 7.30-9.00am as this is a busy period for USAF personnel arriving on Base.

The Contractor shall notify the Base through the Project Manager of access required for abnormally large loads to the Base to make any necessary arrangements to ensure adequate and appropriate access. Such notification shall be required a minimum of seven working days in advance.

The Contractor shall be responsible for escorting deliveries from the main gate to the site/site compound. A Base representative may also escort the vehicles, but this shall be in addition to the Contractor’s escort and not instead of. There may be a vehicle search procedure at the main gate and Base military police have the right to search vehicles anywhere on the Base at any time. On arrival at the site, the Contractor’s escort will observe the delivery and vehicle off-loading procedure. Base military police may witness and inspect the material if they require.

The Employer will not accept responsibility for delays incurred as a result of failure to have relevant documentation to access facilities or the failure of the Contractor to provide adequate documentation for the mobilisation of Equipment as described elsewhere in this documentation.

### Access to the works by Others

The Contractor shall coordinate and provide access for Others prior to contract completion. All Contractors (e.g. BT, maintainers, etc.) requiring access to the works shall be confirmed by the Employer at the bidders’ conference.

### Driving

The Contractor shall ensure that all personnel driving within RAF Lakenheath have all relevant documentation including appropriate driver licences and insurance for the vehicle/driver.  All vehicles entering RAF Lakenheath must be registered and compliant with current UK vehicles legislation regarding insurance, MOT and vehicle excise licence.

The speed limit around RAF Lakenheath generally is 20mph, although this does vary in local areas.  Speed limits are vigorously enforced for the purpose of safety by the MOD Police and 48SF. Airside driving will require an airside driving permit to confirm competency to drive a vehicle within a restricted area. Contractor’s vehicles should be sign written and identifiable, with a flashing amber beacon on the roof. No POV's (standard road vehicles), shall be permitted airside.

### Working hours

Working hours shall be Monday to Friday 0700 to 1800 hours. Working hours within the defined “Airfield Perimeter” shall be 0800 to 1600 hours.

Each evening, a flag lowering ceremony will be held on the Base. During this time the national anthems of the US and of the UK will be played. While this is happening the Contractor and any person employed or working on the Site shall be required to observe the restrictions on movement imposed. No movement on or around the site of vehicles or personnel will be allowed during the flag lowering ceremony.

In addition to the UK public and bank holidays, the following US public holidays are observed on the Base:

Columbus Day

Independence Day

Labor Day

Martin Luther King Day

Memorial Day

Presidents’ Day

Thanksgiving

Veterans’ Day

Additionally, there are a number of Goal days throughout the year which will be a holiday for the Base personnel.

The Contractor shall be aware that access, movement around the Base and escort availability may be restricted on these days.

The Contractor’s attention is drawn to the requirement to liaise, and gain acceptance from, the Employer’s Approved Persons (APs) throughout the Works. It should be noted that APs’ availability is generally limited to 08.00 to 16.00 hours, Monday to Friday.

#### Working outside normal hours

The Contractor shall:

Obtain prior permission from the Project Manager to carry out overtime or work outside the normal working hours, which shall also be subject to any establishment regulations, special restrictions etc.;

Bear all costs of any and all overtime, shift and night work allowances;

The following minimum periods of notice for working outside of normal hours are required:

Weekday working: 72 hours’ notice

Weekend working: 96 hours’ notice

The Employer reserves the right to refuse any request for working outside normal hours.

### Parking

Parking of the Contractor’s and Employer’s vehicles will be restricted to the Contractor’s site compound area.

## Protection of existing services

### Commencement condition survey

Prior to the start of the works, the Contractor shall carry out a survey, including photographic records (Following obtaining a photographic authorisation permit), of the Site and adjacent features.  The Contractor shall agree survey records with the Project Manager. The condition survey of the next Phase of PAS’s will need to be completed and Works agreed prior to completion of the previous Phase.

### Existing services

The Contractor shall:

Notify, via the Project Manager’s representative, all service authorities, the DIO Base APs and, if applicable, adjacent owners of the proposed works, not less than 15 working days before commencing works at Site.

Before starting work, confirm positions of existing services. Where positions are not shown on drawings, obtain relevant details from service authorities, Base APs or other owners.

Unrecorded services found during the works shall be identified and their location traced (if necessary) and accurately recorded. If diversions are deemed necessary, these shall be recorded and all information to be provided to the Base.

Provide method statements for all works to existing services.

Follow the Employer's and/or Base APs recommendations for work adjacent to existing services.

Adequately protect, and prevent damage to all services and not interfere with the operation of the services without consent of the service authorities or other owners.

If any damage to services results from the execution of the works, notify the Project Manager and appropriate service authority/AP without delay and make arrangements for the work to be made good without delay, to the satisfaction of the service authority, AP or other owner as appropriate. Any measures taken by the Project Manager to deal with an emergency shall not affect the extent of the Contractor's liability.

Replace any marker tapes or protective covers disturbed during Site operations to the service authority/AP’s recommendations.

Service diversions shall only be carried out after agreement with the Base authorities (in particular Base APs) and the Project Manager. In some cases, it may be necessary due to operational reasons to carry out this type of work at weekends.

Prior to carrying out any work in connection with service diversions, a method statement shall be prepared and submitted to the Project Manager for his information and for the agreement of the Base authorities.

The Authorised Person (electrical) shall be consulted if any uncharted or unknown cable is found, to agree the strategy for moving or diverting the cable.  In addition, the Authorised Person (POL) shall be present in the event that isolation is required.  The attendance of an AP will require 28 calendar days’ notice. Therefore, the Contractor shall provide at least 4 weeks’ notice of the requirement for the relevant AP to attend a specific part of works. It should be noted that APs’ availability is generally limited to 08.00 to 16.00 hours, Monday to Friday.

### Taxiways, Hardstandings, Roads and footpaths

The Contractor shall adequately maintain taxiways, hardstandings, roads and footpaths within and adjacent to the Site and keep clear of mud and debris. This may include but not be limited to providing road sweepers, wheel washers and dust suppression. Any damage to roads and footpaths caused by Site traffic or otherwise consequent upon the works shall be made good to the satisfaction of the Project Manager, local authority or other owner.

The Contractor shall bear any costs arising from damage to taxiways, hardstandings, roads and footpaths.  Road closure applications shall be made at least four (4) weeks in advance of any works which obstructs the road network for the Base. Taxiway closures would be subject to a twelve (12) week notification period.

### Trees / hedges / shrubs / lawns

The Contractor shall adequately protect and preserve all flora at the site, except any which are to be removed. The Contractor shall replace to approval or treat as instructed any species or areas damaged or removed without approval. Mature trees and shrubs which, due to the Contractor’s negligence, are uprooted, destroyed or damaged beyond reasonable chance of survival in their original shape, shall be replaced on a 1:3 ratio with those of a similar type and age at the Contractor’s expense.

### Existing features

The Contractor shall prevent damage to existing buildings, fences, gates, walls, roads, paved areas and other site features which are to remain in position during the execution of the works.

### Existing works

The Contractor shall:

Prevent damage to existing property undergoing alteration or extension and make good to match existing any defects so caused

Minimise the removal of the existing work and, with care, reduce the amount of making good to a minimum.

### Building interiors

The Contractor shall protect building interiors exposed to the weather during the course of the works with temporary enclosures of sufficient size to permit execution of the works and which shall remain weather tight in severe weather. The building is to be fully sealed and cleaned prior to the activation of any HVAC systems.

### Existing structures

The Contractor shall:

Provide and maintain during the execution of the works all incidental shoring, strutting, needling and other supports as may be necessary to preserve the stability of existing structures on or adjoining the site that may be endangered or affected by the works.

Support existing structures as necessary during the cutting of new openings or replacement of structural parts.

Not remove supports until the works are strong enough to support the existing structure.

Prevent overstressing of completed work when removing supports

## Environmental Constraints

The site is on a drinking water aquifer therefore the Contractor shall develop a suitable Environmental Management Plan; this is expected to include good construction practices to prevent pollution; and should include:

Dedicated, bunded re-fuelling areas

An agreed spill response plan

Control of “wash-out” water (or other methods) to clean the PAS floor and walls

## Use of Peat

The MOD is committed to eradicate the use of peat on the Defence Estate. All use of peat should be substituted with organic wastes such as compost, manure, leaf mould, bark chippings and coir wherever possible.

## Security Escorting Requirements

### Escorting Within Airfield Perimeter

All works within the identified “Airfield Perimeter” will be subject to military escorting.  The required escorts will be provided by the base. Specific constraints on this are:

For PAS works the number of escorts will be determined by the escort office and is dependent on the number of contractors on site, with a maximum of 50m between escorts and line of sight required from at least one escort to each worker

An escort is required for all deliveries from the Contractor’s compound to work areas, a restricted area escort must oversee deliveries to agreed storage locations within the restricted access zone. The restricted area escort will handover escorting responsibility at the boundary to the restricted area and will not oversee operations outside the boundary to the restricted area.

The Contractor shall adequately plan the works and inform the base of work locations two (2) weeks in advance.

### Escorting Between Main Gate and Airside Boundary

The base requires all personnel on site to either have an installation pass or be escorted by a person who holds a base security pass. To allow for ease of working, it has been agreed that construction areas can be fenced to create a zone. The zone will be defined based on the number of PAS’s being released, where they are located and a working area around them. It shall be the responsibility of the Contractor to ensure that all operatives working on this project are escorted at all times.

One (1) cleared person with escorting rights shall escort a maximum of four (4) non-pass holders at any time within the Base.

The Contractor shall make special consideration of how personnel with be transported to and from the fenced site area while complying with escorting rules.

## Site Permits

The Contractor shall submit a request form for a Site Permit to Base. The application shall be submitted three weeks prior to the start of Works and is valid for 30 days. Two weeks prior to the expiry date, the Contractor shall be required to reapply for another 30-day permit. This arrangement will continue for the duration of the Works.

## Considerations of Others

The Contractor shall provide facilities to ensure that dust created by the works is kept to a minimum. This shall include but not be limited to spraying and wheel washes. Working times shall be set out as in accordance with Section 2.2.6. Light pollution shall be kept to a minimum with only security lighting being left on during the hours of darkness. All other lights shall be on timers to ensure they are switched off once the sites have closed. Activities that may cause vibrations above and beyond the movement of plant shall be reported to the Project Manager at least two (2) weeks prior to commencement. Traffic shall be managed to avoid stacking at the Base access gate, with details provided within the Contractor’s Site Traffic Management Plan. 48CES may provide guidance regarding traffic management on Base.

## Industrial Relations

The Contractor will be required to work alongside other contractors present on the Base. The Contractor shall hold regular meetings with the other contractors on Base to ensure works are coordinated and any challenges can be managed effectively. These meetings shall be chaired by the Employer, his representative or the Principal Contractor of the respective sites.

## Control of Site Personnel

The Contractor is required to control all personnel including Subcontractors to ensure they abide by the restrictions imposed by the Base.

## Waste Materials

The Contractor shall ensure that waste streams are separated and where possible materials reused or recycled in line with best guidance. The Contractor is responsible for the safe disposal / recycling of all waste materials generated by the works.  The Contractor shall complete the DIO Waste Report on a monthly basis.

## Deleterious and Hazardous Materials

The Contractor is responsible for the safe containment and disposal of all deleterious and hazardous materials.

The Contractor shall undertake a full refurbishment asbestos and hazardous material survey for each building that is to be refurbished. This shall satisfy the Contractor of the presence or absence of asbestos containing materials and any other deleterious and hazardous materials.

# WI 300 Contractor’s design

## Parts of the works to be designed by the Contractor

The Contractor will design the whole of the works and will be solely responsible for the design development of the works to a final acceptable design solution as agreed with the Project Manager and Employer.

The Contractor shall apply good working practices and guidelines and any statutory requirements normally required for facilities of this type and should be fully reflected in his design.

Any proprietary items specified shall be suitable for their intended use and fit for their purpose. Manufacturers' recommendations on the use and fixings appropriate to the intended use shall be deemed to have been allowed for in the design detailing and therefore in the pricing.

The Contractor is required to provide, whenever appropriate, products made by companies belonging to approved third party quality assurance schemes, such as the BSI Kitemark, agreement certification.

It is to be noted that materials and products are to comply with specification and standards noted throughout the Works Information, and the materials and products identified in this document are extracted from these standards.

The minimum design input required by the Contractor is as follows:

to design the scheme for construction, including working drawings as per the requirements of the specifications, standards and design submission requirements;

to meet fully the requirements of the Works Information;

to meet fully the requirements of the relevant statutory regulations and restrictions, including those imposed by the Employer and RAF Lakenheath;

to design and have received design acceptance of any differences (or changes in regulations) identified in the next Phase of PAS’s prior to completion of the previous Phase of PAS’s.

The detailed requirements for the project are as detailed within the project drawings and this Works Information.

The Contractor shall prepare a specification incorporating specific requirements of this Works Information. In particular, the Contractor shall include in his specification clauses pertaining to the testing and standards of workmanship. The National Building Specifications (NBS) and National Engineering Specifications (NES) standard specification shall be taken as a minimum standard for materials and workmanship. Particular attention is drawn to the third party quality assurance schemes. The Contractor shall inform the Employer of all Plant and Materials that are required to be tested by third parties, in order for them to achieve compliance.

The Contractor is required to comply with the current building regulations (Fire Regulations) as a minimum standard. Higher Standards may be required by NBS/NES or this Works Information or Base standards, in which case they are to be priced designed and constructed accordingly, the most onerous and mandatory will always apply.

## Particulars of the Contractor’s design

### Design generally

The Contractor shall, in all cases, be responsible for the development and detailing of the design set out in, or implicit from, the Works Information to whatever level is necessary to enable the works to be carried out.

The Contractor shall prepare full working drawings and specifications for all aspects of the works as the design proceeds. All such drawings and specifications are to be submitted to the Project Manager at key stages as noted below.

Electronic copies of all documents and drawings shall also be submitted in both their native format (e.g. AutoCAD) and in Adobe© PDF format. Where issued as part of a hard copy, soft copies shall be issued on CD or DVD (as appropriate).

The use of other types of electronic information transmission shall be proposed by the Contractor, (see Section 8.2.2) but shall not be used without the written consent of the Employer and Project Manager. Consent should not be assumed. The Employer may decide that some hard copies are not required due to the use of an electronic information transmission system.

| 65% Design Stage | Four (4) hard and Six (6) soft copies of all full size drawings, calculations, specifications and reports as information listed in Section 3.5 |
| --- | --- |
| 95% Stage | Four (4) hard and Six (6) soft of all full size drawings, calculations, specifications and reports as information listed in Section 3.6 Schedule of details of all finishes in all areas including external materials 2 copies of supporting information for building regulation submission including calculations & Life cycle costing analysis |
| 100% Stage | Four (4) hard and Six (6) soft of 100% acceptance documents as information listed in Section 3.7 |
| Post 100% | Four (4) hard and Six (6) soft of any full size drawing or specification revised or issued after 100% design acceptance |

The Contractor shall complete the design and detailing of the works as specified and provide complete production information (including, as appropriate, fabrication/installation drawings, all design calculations, specifications and other documentation) based on this Works Information, liaising with the Project Manager and others as necessary to help ensure co-ordination of the work with related building elements and services.

The Contractor shall be required to make presentations of the 35%, 65%, 95% and 100% design packages to the end-user, Employer and the Project Manager following completion of each stage.  The 100% design presentation shall be a formal presentation and sign off meeting with the end-user and Employer. The 95% design shall be a design complete in all respects. The subsequent 100% submission is only required to allow any 95% review comments to be incorporated and for acceptance by the Employer and his representatives.

Throughout the design period, the Contractor shall inform the Project Manager, user and Employer of the progress of the design through the Contractor’s regular design team meetings, which shall be held monthly as a minimum. These shall be used as a design aid by the Contractor in which he shall gain regular feedback on any design issues arising which might have an impact on the design.

The Contractor shall ensure that any necessary amendments are made to the design within a maximum of 10 working days from notification to the Project Manager of the required amendment. Unless and until the Project Manager confirms his satisfaction, submit the required number of copies of amended drawings etc, to the Project Manager, and ensure incorporation of necessary amendments all as before.

The design drawings shall be fully co-ordinated with all disciplines and shall fully detail the design intent of the scheme.  All drawings issued shall be signed as checked and suitable for submission by the Contractor’s nominated design co-ordinator prior to issue to the Project Manager.  The Contractor shall provide drawings appropriate to the stage of work throughout the design, installation and completion of the project.  The Contractor shall indicate, at all stages of design, on all schematic drawings all settings of all adjustable protective devices including circuit breakers. This information shall also be included on the as installed drawings.

Design submissions that fail to demonstrate compliance will be rejected by the Employer. Such submissions will not be comprehensively reviewed by the Employer and the Contractor shall re-submit the designs having undertaken a full design review, check and co-ordination exercise that designs are compliant with the Works Information and suitable for submission.

The design shall consider in detail ease of accessibility for maintenance and replacement of all elements of the building and its services.

The form of the title block for all drawings and schedules shall be to Employer’s standard and agreed with the Project Manager.

The project design and construction shall be developed in compliance with the latest RAF Lakenheath Base Standards and USAFE standards.

Where any deviations from these standards are proposed, they shall be to the satisfaction of the Employer

## General Items

### Asbestos Survey

The Employer has removed asbestos containing material (ACM) from the door seals of Phase 1 of the PAS and will issue clearance certificates in Site Information. The Employer will arrange to remove ACM door seals from future Phases of PAS and issue the clearance certificates.

The Contractor shall undertake a refurbishment asbestos survey prior to undertaking any works on site. The cost of removal of any asbestos not identified in the Employers asbestos register and survey shall be undertaken by the Contractor as a Compensation Event.

The Base shall require method statements for asbestos removal prior to permits being issued for undertaking surveys or removal of asbestos containing material in accordance with the Base Standards. A Risk Assessment Method Statement (RAMS) for both asbestos survey and removal must be forwarded to the Employer, allowing suitable notice for review. The Employer will liaise with the Base Asbestos Program Officer (The Duty Holder) for approval. Work should only commence once the Duty Holder has issued a permit.

The asbestos survey shall be undertaken upon all areas being fully vacated by users to ensure that any asbestos can be removed without a delay to the critical path. Asbestos removal may be undertaken as an enabling package, prior to 100% design acceptance in agreement with the Project Manager.

The removal of any further Asbestos Containing Material to that previously identified shall be an Employer Risk.

### Building Condition and Land Use

Visual building condition surveys have been undertaken for this project and are included in the  supporting information. The Contractor shall undertake two video and photo dilapidation surveys; one prior to the commencement of the asbestos survey and one prior to the Works. The Contractor shall undertake any intrusive surveys he requires to satisfy his design and construction of the works the scope and specification of any intrusive surveys must be agreed with the Project Manager and Employer.

### Accommodation Considerations and Constraints

Accommodation within the building will be arranged in accordance with the accommodation schedule, which is co-ordinated with the reference design contained within the Works Information.

Any decommissioning of ordinance and military equipment is the responsibility of the Employer. The Contractor shall not be responsible for decant of users into the building. All furniture and equipment shall be installed by the Employer.

### DREAM requirements

- A Defence Related Environmental Assessment Methodology (DREAM) assessment is NOT required.

### Design excellence evaluation process

Design Excellence Evaluation Process (DEEP) is NOT required.

### Building Information Modelling

Building Information Modelling (BIM) is NOT required. A Revit model of a single PAS shall be provided in the supporting information the Contractor shall satisfy himself of its accuracy and bears all responsibility for the Contractors intended use in their design.

### Soft landings

In addition to the requirements of Tech12 and Red Zone, the Contractor shall ensure that the design, construction, handover and aftercare of the facility apply the principles of the BSRIA Soft Landings and Government Soft Landings. The process applies to all new build, alteration and refurbishment works and shall reference the Soft Landings Framework (BSRIA BG4/2009), Government Soft Landings guidance and abide by the Soft Landings Core Principles (BSRIA BG38/2012).

The Employer has set up a soft landings steering group and the Contractor shall ensure this group is kept fully informed of progress throughout the contract.

The Contractor shall develop the design for the works, taking into account the understanding of how the facilities will be used and managed.

Alongside the design and construction process, the Contractor shall review performance expectations as the design solutions become more fixed and plan for commissioning handover and aftercare. This shall include but not be limited to the tasks below.

#### Soft Landings Stage 2: design stage

- Discussing and reviewing progress on environmental and other performance targets

- Ensuring feedback from occupiers and stakeholders is obtained and agreement is reached over incorporation (through the Employer) as the design is developed

- Passing on requirements to Subcontractors

- Confirm acceptance of control strategy, metering strategy and monitoring strategy

- Ensure a commissionability review is carried out during design stage

- Prepare a handover plan, to be reviewed in the same manner as other design deliverables, which is compliant/consistent with the Contractor’s proposed facilities management strategy. ensuring that it is consistent with the transition plan

- Take account and comply with the facilities management strategy in terms of the selection of Plant and Materials

- Initiate and apply the CIBSE TM22 Energy Assessment Tool, with a metering and monitoring strategy to suit.

#### Soft Landings Stage 3: pre-handover to handover

- Put a commissioning manager in place (Noting Comp-Ex requirements)

- Initiate environmental and energy logging review

- Set up a building readiness programme for issue in its final form at least 1 month prior to commencement of commissioning

- Submit commissioning records

- Provide training and demonstrations as required for the Employer’s nominated personnel.

- Provide operations and maintenance manuals and operations guides, along with any required support in accordance with Tech 12

- Implement the handover plan

- migration of equipment, personnel and operations into the facility

### Force protection measures

As no works are being undertaken to change the external envelope or structural frame, Force Protection measures are not required.

### Definition of “percentage design”

The definitions of the “percentage design submission” requirements noted in this document are to follow the definitions stated in the United States Air Force Project Managers’ Guide for Design and Construction as well as the requirements of this document, whichever is the more onerous. The USAF PM Guide defines the ‘submission’ of a design as n0% (e.g. 60%) and the ‘approval’ as n5% (e.g. 65%). Under this contract, no documents are “approved” but may be “accepted” by key persons or roles defined in the contract. For clarity, the terms “n0% design” and “n5% submission” are broadly interchangeable in this WISI, as the former is the status of the design at the end of a design stage and the latter refers to the design package submitted for review at the end of a design stage.

### Design Review and Acceptance

During the works the Contractor shall submit to the Project Manager the required number of copies of design/production information.  The Project Manager will note his comments on Review Sheets and return to the Contractor.

The Contractor shall confirm to the Project Manager the date for each design submission ten (10) working days prior. If the design is submitted on that date the Project Manager will require twenty (20) working days following receipt to review the Contractor’s design submission and issue comments at the 65% and 95% stages (i.e. 20 working days for each stage).  If the design is not issued on the date advised by the Contactor, the Project Manager will require up to thirty (30) working days following receipt to review the Contractor’s design from the date of receipt. The Contractor shall be responsible for recovering the programme delay at his own expense.

It shall be the responsibility of the Contractor to issue documents to each of the interested parties (DIO, MM, End User, and 48CES) through the approved electronic document management system.  Hard copy documentation if required, including CDs/DVDs, must be sent via a courier service with details agreed with the Project Manager.

The Contractor shall ensure that any necessary amendments are made to the design within a maximum of twenty (20) working days following receipt of review comments from the Project Manager.

The Contractor shall ensure incorporation of necessary amendments and re-submit the required number of copies of amended drawings etc, to the Project Manager for a repeated review as before.

The Project Manager shall confirm his satisfaction with the 65% stage submission when all comments have been addressed sufficiently. At that point the Contractor shall commence work on the 95% design stage.  If the Contractor chooses to progress design work past 65% prior to the Project Manager confirming his satisfaction with the 65% design, any abortive 95% design work by the Contractor will be at his own risk.

The design drawings shall be fully coordinated with all disciplines and shall fully detail the design intent. All drawings issued shall be signed as checked and suitable for submission by the Contractor’s nominated design coordinator prior to issue to the Project Manager.

Design submissions that fail to demonstrate compliance shall be rejected by the Employer. Such submissions will not be comprehensively reviewed by the Employer. The Contractor shall re-submit the designs having undertaken a full design review, check and coordination exercise. The Contractor is to ensure that their designs are compliant with the Works Information and suitable for submission. The Contractor shall be responsible for recovering any programme delay caused by a such a re-submission.

The Project Manager shall confirm his satisfaction with the 95% stage submission when all comments have been addressed sufficiently. At that point the Contractor shall amend the revision numbers on documents and re-submit as the 100% design. If any changes have been made to any documentation other than revision numbering, the 100% design package will be treated as a resubmission of the 95% design until the Project Manager confirms his satisfaction with the design.

When the Project Manager confirms his satisfaction with the 95% design, a 100% Design Sign-off meeting shall be arranged. At this meeting the 100% Design documents shall be signed as being accepted by the Project Manager for use in construction. Other End Users may also sign their acceptance at this meeting.

At no time will the review or sign-off processes affect the design liabilities of the Contractor under this contract, including any comments issued or acceptance of any documentation

## 35% Design

The Contractor shall provide an on-board presentation of his 35% design submission to the Project Manager the Employer and their Client to ensure the design is heading in the right direction. The items listed below are for guidance only and represent the minimum acceptable for this design presentation.  This does not relieve the Contractor of his obligation to provide full and comprehensive design documents which are necessary for the satisfactory completion of the project.

### General

Survey findings

Phasing and programme for construction

Agreed Hazardous zone classification drawings and proposals to meet them

Fire Strategy including drawings and operational philosophy (identifying dilapidations)

### Architectural

Outline specification including all coatings

### Civil/Structural

Plan, Elevation and Section drawings confirming the proposed works

### Electrical and Mechanical

Outline design philosophy and criteria statement

Outline ventilation proposals

Initial strategy drawings for electrical proposals.

## 65% Design Documents

The Contractor shall provide as a minimum the following documents and drawings for the 65% design submission for acceptance by the Project Manager and for comment by the Employer. The items listed below are for guidance only and represent the minimum acceptable for this design submission package.  This does not relieve the Contractor of his obligation to provide full and comprehensive design documents which are necessary for the satisfactory completion of the works.

### General

Details of the Contractor’s design house and any special details of the Contractor’s design house and specialist designers

Details of the Contractor’s design coordinator and Principal Designer

Construction works methodology

Fire strategy document, developed from outline provided in the tender documents

Construction phase H&S plan based on the requirements of USAFEI 32-1007 or section 1.11 from the UFC 3-260-01

Designers Hazard Risk Assessments appropriate to the stage and work content

Draft asset register – Form 140

Proof of Compliance Plan

Health & Safety Risk Assessment

The complete submission shall be fully co-ordinated and include a design philosophy statement to explain design decisions made and how each element of the design interacts with other aspects. The Contractor shall include the design philosophy statement when providing a pack of drawings and calculations to ensure that the information is clearly conveyed.

### Architectural (Appendix A)

Site Location Plan

Floor and roof plan

Schedules of fixtures and fittings

Schedule and samples of finishes

Fire Strategy including drawings and operational philosophy (identifying dilapidations), included in the Fire Strategy Report

Building Regulations (Fire Regulations) calculations and supporting information

### Structural and Civil (see Appendix B)

Plan, Elevation and Section drawings confirming the proposed works

Results of survey of Efflux chamber walls, Shelter roof, front and rear doors

Design philosophy and criteria statement

Structural arrangements

Calculations to justify the proposals shown on the drawings and support Building Regulations (Fire Regulations)

### Electrical and mechanical (see Appendix C and Appendix D)

Design philosophy and criteria statement

Detail design drawings indicating mechanical services plant & layouts to all areas.

Distribution diagrams.

Schematic diagrams for electrical distribution, telecoms, security systems and grounding/earthing.

Fully detailed mechanical services ductwork layout drawings for all services throughout the facility

Summary calculation sheets.

Summary of selected manufacturers with type and model, selected rating, and performance criteria.

Drawings indicating co-ordination of all mechanical services and indicating access zones for maintenance with all other installations i.e. electrical services, structural and architectural etc.

Life time cost analysis including proof of compliance with UFC 3-410-01FA and costing from LED luminaries as UFC 3-530-01.

Plan drawings and principal key sections indicating plant items and the associated manufacturers’ minimum access zone requirements for maintenance & replacement shall be provided to demonstrate compliance with DE DMG 08. These drawings shall be dimensioned and indicate all services i.e. Mechanical, Electrical etc. together with the appropriate DMG 08 checklists shall be provided at the Detail Design and Construction stages.

Plans (minimum scale 1:50) showing:

Lighting, lighting control and emergency lighting layouts

socket and switch positions,

switchgear

Telecoms Equipment

Ground Earthing

Ventilation ductwork etc.

Completed lighting calculations indicating the following parameters:

Maintenance factor determined by Contractor from parameters detailed in Appendix D.

Reflectances determined by Contractor

Selected luminaires

Working Plane

Target Lighting Level

Achieved Lighting Level

Life cycle comparison costing as UFC 3-530-01

Completed Emergency lighting calculations indicating the following parameters:

Maintenance factor determined by Contractor from parameters detailed elsewhere

Selected luminaires

Working Plane

Target Lighting Level

Achieved Lighting Level

Luminaire in Emergency Mode output

Infrastructure connections and materials

Description of the proposed controls strategy

Estimated maintenance costs

Grading calculations

Maximum Demand

Draft schedule of equipment with life span less than 20 years, with draft schedule of maintenance and delivery periods

Draft access maintenance schedule/access maintenance statement

Draft CIBSE log book

Draft Asset Register

Draft BMS points schedule indicating the following parameters:

Each item to be connected

Type of connection digital/analogue

Function

Test certificates for existing LV, Voice and IT points, grounding, lighting protection system (including testing of existing systems).

The information listed above is for guidance only and represent the minimum acceptable for the 65% design submission package.  This does not relieve the Contractor of his obligation to provide full and comprehensive design documents which are necessary for the satisfactory completion of the Works.

- If the Employer considers that the Design does not comply with the Information, it will not be accepted and need to be re-submitted by the Contractor for review by the Employer, complete with any amendments to achieve compliance.

## 95% Design

The 95% design shall be the complete design and shall fully reflect all comments raised at the 65% design submission stage. Where comments have not been adopted, responses shall be given as to why this has not been done prior to the 95% submission and the agreed solution incorporated within the 95% design solution.

The drawings shall be adequate to be presented for design award submittals with minor amendments and colouring/rendering.

The design documents list requested below is for guidance only and represents the minimum acceptable for the 95% design submission package. This does not relieve the Contractor of his obligation to provide full and comprehensive design documents which are necessary for the satisfactory completion of the project.

The 95% design shall be a design complete in all respects and shall not contain any references to information that shall be “to follow” in the 100% submission. The subsequent 100% submission is only required to allow any 95% review comments to be incorporated and for acceptance by the Employer and his representatives.

The Contractor shall provide as a minimum the following documents for the 95% Construction Document for comment by the Employer as to whether or not they are satisfactory:

### General

Final fire strategy report, with all design elements bound and including dedicated drawing numbers

Final Fire Strategy Report and drawings as a separate package for DSA Fire Officer review and issue of a Fire Certificate A upon their acceptance

Final DSEAR Assessment

Final JSP 482 Explosives Assessment

Programme for the Works

Construction works methodology

Proof of Compliance Plan

Health & Safety Risk Assessment

Completed CIBSE log book, less test, completion certificates, etc

Completed DIO Forms 140, 148 and 153

Access maintenance schedule

Completed asset register in DIO format

Agreed Material selections and samples for all disciplines

### Architectural (see Appendix A)

Architectural Design Statement

Floor and roof plans

Specifications

Constructional details

Schedules of doors and ironmongery

Schedules of fixtures and fittings

Site layout plan showing all external works, existing and proposed services, items of plant, etc.

Site location plan

Sample boards detailing all finishes in all areas including external materials.

Builders work in connection with M&E Building Services

Internal area elevations

Asset register

### Electrical and Mechanical (see Appendix C and Appendix D)

The entire 65% submission plus all fully detailed & dimensioned for construction including offsite prefabrication of ductwork, duct manufacturers detail fabrication drawings

Completed lighting calculations, highlighting where revised since 65% design submission indicating the following parameters:

Maintenance factor determined by Contractor from parameters detailed in Appendix D

Reflectance’s determined by Contractor

Selected luminaires

Working Plane

Target Lighting Level

Achieved Lighting Level

Lifecycle comparison costing as UFC 3-530-01

Revised Emergency lighting calculations where design changes result from 65% design review indicating the following parameters:

Maintenance factor determined by Contractor from parameters detailed elsewhere

Selected luminaires

Working Plane

Target Lighting Level

Achieved Lighting Level

Luminaire in Emergency Mode output

Control panel wiring diagrams including an updated control strategy and a fully detailed points schedule.

Drawings indicating co-ordination of all mechanical, public health, electrical services, with all other installations i.e. drainage, structural and architectural etc. indicating access zones for maintenance.

Full working drawings indicating co-ordinated positions & access zones for maintenance of all equipment, accessories etc., dimensioned where appropriate, in plant rooms and mains service routes. These are required prior to construction commencing on site.

Detail design drawings indicating layouts of equipment throughout the building including drawings detailing co-ordinated furniture, mechanical and electrical services layouts to all areas.  These drawings are to be detailed at a minimum scale of 1:50:

lighting layouts

socket and switch positions

fire detection i.e. fire alarms, etc

ventilation

fire extinguisher positions

ventilation ductwork principal details

HVAC control schedule and description of operation of flow charts

Layouts showing all plant, equipment and pipework including access spaces fully complying with Design & Maintenance Guide 08.

Distribution diagrams for power distribution; Schematic diagrams for all mechanical and electrical services, including fire alarms, major plant items, controls and interconnection between services.  Plant plans and elevations fully detailed at a minimum scale of 1:20

Detail drawings as applicable

Design calculations

Final Schedule of selected manufacturers with type and model, selected rating, performance criteria for all plant items

Drawings indicating co-ordination of all mechanical and electrical services with all other installations, i.e. structural and architectural, etc.

Running and maintenance costs

Infrastructure connections and materials

M&E working drawings indicating co-ordinated positions of equipment accessories etc., dimensioned where appropriate, for key locations including plant and main service routes as a minimum.

Maximum Demand indicating the following parameters:

Connected loads, to be carried forward to cable calculations

Diversities to be carried forward to cable calculations

Equipment loads to be carried forward to cable calculations

Allowance for portable equipment, IT equipment etc. to be carried forward to cable calculations.

Cable calculations indicating the following parameters:

Cable type

Origin and destination of circuit

Method of installation

Length of circuit

Maximum load current

Maximum circuit voltage drop

Maximum circuit impedance

Type of Circuit Protective Conductor (CPC)

Method of over current and short circuit protection

Details of over current and short circuit protection

Connected load

Maximum demand

Diversities

Where circuit breakers are utilised, details of the over current and any earth fault settings shall be detailed on the drawings together with any other settings that the protective device may have.

Cable containment calculations, as a minimum to indicate the following:

Spare capacity

Space factor for installed cabling

Space factor for spare capacity as identified subsequently or in standards subsequently identified

Adequacy of support systems

For all systems including sub mains, final sub circuit cabling, communications structured cabling, fire alarm cabling, vindicator cabling, and all other cabling systems

Cable containment calculations shall be completed for all runs of primary containment, i.e. trunking and trays, for all sizes used

BMS points schedule indicating the following parameters as a minimum:

Each Item to be connected

The type of signal to each item

Modifications to existing item to allow connection

Schedule of equipment with life span less than 20 years, with draft schedule of maintenance and delivery periods

Schedule of specialist tools, for all systems

Materials selections

Access maintenance schedule

Design Certificates

Completed CIBSE log book, less test, completion certificates

Completed DE Forms 140, 148 and 153

Complete Asset Register

Proposed Generator Specification following the requirements identified in the Site Information, comprising of a minimum:

Table of specifications,

Proposed Electrical Services Schematic Diagram

Electrical Power Drawing

### Civil and Structural (see Appendix B)

Floor and roof plans

Floor plan and section for the plant room enlargement

Results of survey of wall to be removed

Full design calculations

Plumbing and drainage layouts and details including manhole schedules (external)

Foul and storm water layouts

Site layout drawings

The drawings shall be adequate to be presented for design submittals with minor amendments and colouring.

The information listed above is for guidance only and represent the minimum acceptable for the 95% Design submission package. This does not relieve the Contractor of his obligation to provide full and comprehensive design documents which are necessary for the satisfactory completion of the Works.

The 95% Design shall be a design complete in all respects and shall not contain any references to information that will be “to follow” in the 100% submission. The subsequent 100% submission is only required to allow any 95% review comments to be incorporated and for signing off by the Client and his representatives.

- If the Employer considers that the Design does not comply with the Works Information, it will not be accepted and need to be re-submitted by the Contractor for review by the Employer.

## 100% Design

After review of the 95% design submission by the Project Manager, the Contractor shall incorporate any comments made into a 100% signing package. This shall include all the documents listed in section 3.6 above and any comments made or particular requirements of the Project Manager. The package shall be provided within 4 weeks of comments being received from the Project Manager. The Contractor shall present the 100% submission at a formal acceptance meeting, along with completed DIO Forms for operation and maintenance manual purposes. It shall include the Fire Certificate A issued by the DSA Fire Officer; failure to attain or include this document will lead to the 100% Design not being accepted.  Similarly, the package must include a Building Regulations (Fire Regulations) compliance certificate as detailed in section 3.15.1.

## Design Calculations

The Contractor shall submit four (4) copies of the design calculations to the Project Manager for comments.  Any comments made by the Project Manager shall not diminish the Contractor’s responsibility under the Contract.  All calculations shall be submitted at the appropriate time that shall support the element of the work and/or the drawings being submitted for acceptance.

The calculations shall include but not be limited to following:

Any concrete slabs requiring replacement

Foundations

Certification of structural calculations

Fan sizing and selection curves

Pipework sizing

Ductwork sizing

Annual expected running costs of the building’s mechanical and electrical services.

Annual and peak energy consumptions

Fault current at intake and characteristics of Base supply.

Lightning protection

Life cycle cost analysis which indicates cost effective and energy efficient system(s) have been chosen

It is the responsibility of the Contractor to arrange for an independent check of the structural design calculations and details by an independent chartered civil or structural engineer and to provide the Employer with the necessary certification in accordance with BS 1192 – Construction Drawing Practice. The Contractor shall also complete a structural design completion certificate in compliance with DIO USF 2518 and a Building Regulations Compliance Certificate BR1.

### Maximum Demand calculations

At 95%, indicating the following parameters;

Connected loads, to be carried forward to cable calculations

Maximum demand

Diversities to be carried forward to cable calculations

Equipment loads to be carried forward to cable calculations

Allowance for portable equipment, IT equipment etc. to be carried forward to cable calculations

### Cable calculations

At 95%, indicating the following parameters;

Cable type

Origin and Destination of circuit

Method of Installation

Length of Circuit

Maximum load current

Maximum circuit volt drop

Maximum Circuit Impedance

Type of Circuit Protective Conductor CPC

Method of over current and short circuit protection

Details of over current and short circuit protection

Connected load

Maximum demand

Diversities

Where circuit breakers are utilised, details of the over current and any earth fault settings shall be detailed on the drawings together with any other settings that the protective device may have.

### Lighting calculations

At 95%, as subsequently detailed in the lighting section in Appendix D of this Works Information.

### Cable containment

For all systems including sub-mains, final sub-circuit cabling, communications structured cabling, fire alarm cabling, access control cabling and all other cabling systems.

Cable containment calculations shall be completed for all runs of primary containment, i.e. trunking and trays, for all sizes used.

Calculations, as a minimum to indicate the following;

Spare capacity

Space factor for installed cabling

Space factor for spare capacity as identified subsequently or in standards subsequently identified

Adequacy of support systems

## Fire strategy documents

The Contractor shall submit a fire strategy document, as detailed in Appendix E. This shall be prepared by the Contractor‘s fire protection engineer.

## Other construction documents

The Contractor shall provide, no later than 5 weeks before the commencement of construction of each individual sequence of work, all construction documents for acceptance by the Employer.

The Contractor’s attention is particularly drawn to the requirement for working drawings as detailed by DE Specifications 036 and 037. A statement of intent from the installation mechanical, public health, electrical and fire suppression. Subcontractors confirming their commitment to the production of working drawings shall be required as part of the design.

Other construction documents required to be submitted by the Contractor are as follows:

Fabrication drawings

Final electrical and mechanical working drawings.

Final specialist Subcontractors’ working drawings

Drawings prepared by the Contractor’s fire protection engineer:

Ductwork

Light levels

Fire extinguisher cabinet positions if applicable

- for review by the Fire Advisor/DSA Fire Officer prior to issue of a Certificate A.

Detailed method statement for pre-commissioning and commissioning of all mechanical and electrical installations including details of the commissioning company and their status is terms of quality assurance status.

Photographic evidence of firestopping to barrier penetrations in non-visible or inaccessible areas.

## Waste Management

The Contractor shall:

Develop a waste management plan provided at the 95% stage, reflecting any comments made by the Employer (or the Project Manager). This shall be based on the information in the draft waste management plan included in Additional Information.

Take responsibility for the implementation and execution of the requirements of the final agreed waste management plan, providing monthly information returns to the Project Manager setting out:

The amount (in tonnes) of material removed from the Site and the amount disposed of to landfill or similar sites and the approximate disposal cost. Copies of disposal documentation shall be provided by the Contractor.

For each material recycled, reused, or salvaged from the works, the amount (in tonnes), the approximate value of any money paid or received for the recycled or salvaged material, and the net cost or savings of salvage or recycling each material.

All documentation should clearly distinguish between quantities of “special or hazardous wastes” and “solid wastes” that were recycled and disposed.

In addition, the following information shall be provided to the Project Manager and Employer on a monthly basis (all amounts to be reported by weight):

The amount of solid waste disposed of by landfill, incineration, etc;

The amount of solid waste recycled;

The amount of construction/demolition debris disposed of by landfill

The amount of construction/demolition debris recycled.

## Working Methods, Method Statements and Permits

The Contractor shall submit method statements and risk assessments for each item of work involving disconnection of supplies, removal of equipment, digging, installation of cables, lifting, placing of equipment, testing and commissioning.

The Works will be controlled by the issue of permits to work (e.g. for electrical, water, drainage, communications utilities and excavations) with all isolations of existing equipment undertaken by the Base’s authorised persons.

The following clearances and associated time scales shall be required before commencing the Works at the site:

AF 103 – Work Clearance:			Issued at commencement for duration of contract

Airfield Construction Equipment waiver:	Require 12 weeks’ notice

Explosive Safety waiver:			Require 2 weeks to issue

Airfield working waiver:			Require at least 6 weeks’ notice

Utility Shutdown:				Required 45 days in advance

Hot Works Permit:				These are the responsibility of the contractor. Prior training must be undertaken with the base Fire Protection office – Refer to SI

Permit to Work (Electrical)			Required 3 weeks in advance

Permit to Work (Mechanical)			Required 3 weeks in advance

Permit to Work (Confined Spaces)		Required 3 weeks in advance

Road Closures 				Required 4-6 weeks in advance

All the Works are to be in accordance with the DIO Standards and Industry Regulations as listed in Section A.2.1.

The Contract must comply with the RAF Lakenheath permit to work system detailed below.

### Existing infrastructure, permit to dig, permit to work

Although external works are not envisaged to take place as part of the Works, should they be necessary the following procedures shall be adhered to.

A current ‘Work Clearance Request’ shall be required prior to construction start and the Contractor must request all utilities to be marked prior to any dig.  The Contractor shall also be required to hand dig to locate all utilities and check locations of suspected utilities, even if not identified as part of the work clearance process, prior to the commencement of work.

The Contractor shall ensure all works carried out to the existing site infrastructure services are planned and carried out in accordance with the requirements of JSP 375.  This shall include the certification of operatives working on these systems.

The Contractor shall note that the infrastructure indicated on the Site Information is for information only and that the Contractor shall be responsible for ascertaining the location of all existing services identified in the Site Information when on the site.

Prior to working on electrical services, the Contractor shall ensure all such persons attend a meeting / interview with the RAF Lakenheath BCE Co-ordinating Authorised Person for authorisation and certification.

Before any excavations are carried out on site the Contractor shall obtain a Form 103 Work Clearance Request from the Employer. The Contractor must notify the employer in writing at least three weeks prior to the AF103 being required. The Contractor shall also contact British Telecom “Dial before you Dig” to ensure all BT plant on the Contractor’s site including his working area is identified by BT prior to the Works commencing.  This shall be done irrespective of any duct information shown on the Form AF103.

The number for Openreach British Telecom is:

0800 023 2023

cbyd@openreach.co.uk

Office Hours: Mon-Fri 09:00-17:00

14 Working Days’ notice is required.

The Contractor shall also coordinate his external works with USAF Specialist Engineer TS Network Consultants.  The contact is:

Mr Tim Smith

Tel: 01638 713 116 or 07802 768615

tim@ts-network.co.uk

It should be noted that there are likely to be unknown services on the site and along the route of any new infrastructure cables and ducts.  The Contractor shall therefore carry out a search of the site using services detection equipment, before any excavations are undertaken.

All excavations within 3000mm of any existing services including BT ducts and chambers shall be hand dug.

The Contractor shall provide 3 weeks advance notice for all interruptions to existing services.  The Contractor shall also note that all services interruptions shall be assumed to be out of hours, as previously detailed.

All requests for Permits to Dig, Permits to Work, interruptions to existing services, etc., shall be coordinated through the Project Manager.

### Cranes and Construction Equipment

The Contractor will require an Airfield Construction Waiver and shall submit all details relating to his proposals for the use of either mobile or fixed cranes, mobile concrete pumps, drilling equipment and the like to be utilised on the site. Details shall include, but not be limited to, the maximum jib height, exact locations, weight capacity and hours of operation. The Contractor shall allow a minimum period of twelve (12) weeks for the Employer to accept the proposals. The Airfield Construction Waiver must be obtained prior to any equipment being moved onto or erected on the site. In addition, the Contractor shall note that the height of a crane when fully extended must not exceed 150 feet and must also include for the provision of a red flag and a red light at the top of the crane.

### Electromagnetic Interference

The Contractor shall take all necessary precautions to avoid excessive electromagnetic disturbance of apparatus outside the Site. Equipment which may cause such interference shall be identified to the Employer prior to use.

### Laser Equipment

The Contractor shall install, use and store any construction laser equipment in accordance with BS EN 60825: Part 1 and the manufacturer's instructions.  He shall use either Class 1 or Class 2 laser equipment ensuring that the laser beam is not set at eye level and is terminated at the end of its useful path. Under no circumstances shall laser beams extend beyond the boundaries of the Contractor’s site.

The use of Class 3A and Class 3B laser equipment shall not be permitted without the acceptance of the Employer and subject to the submission of a method statement on its safe use.

### Powder Actuated Fixing Systems

These shall not be permitted under any circumstances.

## Behaviour on Site

### Smoking

Smoking shall only be permitted in designated areas of the Contractor’s compound, not in the construction area. Smoking shall not be allowed in the Project Manager’s office accommodation or the meeting room.

### Burning on site

Burning of any materials arising from the works shall not be permitted.

### Plant and Machinery

No machinery shall be left unattended whilst on site.  All engines shall be turned off when machinery is not in use. This shall be a requirement of the Environmental Management Plan identified and as submitted by the Contractor.

### Planning/siting approval

This project comes under the Permitted Development rights with the possible exception of the option for coloured external coatings and involves repair works only; therefore, a planning application is not required.

## Working drawings

The Contractor shall provide working drawings as required by all documents referred to in section 3.2 above.

Working drawings shall be submitted to the Project Manager for comment 4 weeks prior to the work progressing on site. Completion of the working drawings is a key payment milestone and completion is required prior to application of all subsequent milestones.

The Contractor’s attention is particularly, but not exclusively, drawn to the requirements of DE 034 to provide working drawings. No additional amounts shall be paid due to site problems encountered through lack of working drawings or the lack of planning, coordinating and sequencing of the works required to produce the working drawings. No additional time shall be allocated for the resolution of design issues which would have been foreseen by the production of working drawings in a timely manner. Working drawings shall include the text of all labels to be installed during the works.

A copy of the working drawings shall be available on Site for inspection by the Project Manager during the course of the works.  These drawings shall be marked up with all Site alterations, changes arising from Compensation Events, etc. as the works progresses.

## Technical literature

### Building Regulations

The Contractor is required to comply with the current building regulations (compliance with Defence Infrastructure Fire Standards (DIFS))  as a minimum standard. Higher standards may be required by NBS, this Works Information or Base Standards in which case they are to be priced accordingly, the most onerous and mandatory shall always apply.

The Contractor is required to give stage notices to the Employer via the Project Manager who shall act in lieu of the local authority.

A certificate confirming that the design complies with all aspects of the Works Information, including applicable building regulations and the other technical standards and DIO design documents is required to be supplied to the Project Manager by the Contractor.  Such certification shall be required upon completion of the design stage and upon completion of construction.  If required, the Contractor shall also supply the requisite number of copies of all documentation, including drawings, documents, schedules and calculations to the Project Manager for building control audit.

A certificate confirming that the works are designed and constructed in accordance with the building regulations shall also be supplied by the Contractor for each section of the works. Working drawings shall include the text of all labels to be installed during the Works which shall be in accordance with the requirements the Works Information and DE 034. Copies of the C1, C2, C3, N1 and D1 Certificates (where relevant) in electronic format may be obtained via the Project Manager or from: DIOSDTFM-USF1iSBCOWyt@mod.uk

# WI 400 Completion

## Works to have been finished by the Completion Date

By the Completion Date the Contractor shall:

Provide all a suitable and complete health and safety file, in line with CDM 2015 and associated guidance

Provide all required as-built drawings, operating manuals and calculations in accordance with TECH012

Complete successfully all tests on completion necessary to Provide the Works

Provide all required Subcontractor warranties

Complete all specified instruction and training required to be provided to the Employer’s staff

## Take over

The Contractor shall provide all documentation required for hand over including, but not limited to the information required by the DIO Handover Requirements, primarily under DE Tech 012.

Before the works commence on Site, the Contractor shall appoint a designated person to develop the operations and maintenance manuals and coordinate the input of all disciplines.

The Contractor is to take ownership of the development and submission of all forms, documents, information and processes within the Handover Process document and is to submit such forms, documents or information as may be required up to and including Completion, in a timely fashion, to the Project Manager for their acceptance.

The Contractor is to identify the relevant forms necessary to validate their design and construction as compliant against the project brief and also relevant regulatory requirements. These forms are to be signed off by suitably qualified and experienced members of the Contractor’s project team.

### Asset register

The Contractor shall prepare an asset register of all materials which shall be used in the construction of the building using the latest edition of Form DIO USF 140. This shall be presented to the Project Manager at 65% submission, 95% and 100% design stages and updated at the construction stage at least three months prior to handover, to enable the placement of maintenance contracts in advance of completion and enable the transfer and acceptance of military real property. Typical information to be included shall be mainly mechanical and electrical equipment requiring regular maintenance and shall not be limited to:

External works: paving, parking, lining, lighting, drainage, roads, kerbs, hardstandings, bollards, equipment and ducting

Substructure: foundations

Superstructure: doors and roller doors

Electrical: lights, cabling, trunking, switches and sockets

Fittings and equipment: filters, valves and pipework.

- Note: Omit where not required

- This shall be developed with extra information at handover in order to meet the Department of Defense (DOD) standard process for facility condition assessment (FCA). All building components affected by construction, refurbishment or demolition works need to be recorded in the Air Force's adopted Sustainment Management System (BUILDER). As such all Defense Components need to be inventoried utilising the American Society for Testing and Materials (ASTM) E-1557-09 UNIFORMAT 2 Classification of Building elements - Level 4.

- A pre-formatted spreadsheet for asset detail recording purposes by the construction Contractor is available from 48 CES/CEOR Asset Managers upon request. The Contractor shall liaise with the Base Lead to determine the format and level of information required.

### Transfer and acceptance of property

The Contractor shall demonstrate to the Project Manager throughout the execution of the works that adequate, accurate records are being kept, to ensure the ultimate completeness and accuracy of the record documents. The documents are to be progressively compiled as the works proceeds. The facilities management manual shall then form part of the agenda for the construction stage progress meetings to ensure progression to completion of Form 1354 to the Project Manager’s satisfaction and issue at the pre-handover meeting.

### Provisional information on services

The Contractor shall provide the Project Manager with relevant drawings and preliminary performance data at the commencement of commissioning to enable the Employer’s staff to familiarise themselves with the installation.

### Training of Employer’s staff

Before Completion, the Contractor shall explain and demonstrate to the Employer’s maintenance staff the purpose, function and operation of the installations including all items and procedures listed in the health and safety file. The Contractor shall carry these demonstrations out over a period of at least two working days.

### Spare parts

Within two weeks of request, the Contractor shall submit to the Project Manager a quotation, priced in detail, for the initial supply of spare parts to the Employer, and including for:

Checking receipt, marking and numbering in accordance with the schedule of spare parts.

Painting, greasing, packing and other similar requirements to prevent deterioration during storage.

### Tools

At Completion, the Contractor shall provide two complete sets of any specialist tools and portable indicating instruments for the operation and maintenance of all services plant and equipment, manhole covers, together with suitable means of identifying, storing and securing same.

### Deep clean

The Contractor shall undertake a deep clean of the completed facility prior to handover additionally, all accessible ducts and voids shall be cleaned and vacuumed.

## Operation and Management Manual

Contents of manuals should follow the broad sectionalised structure of the current edition DIO form 141 unless agreed otherwise by/through the 48 CES/CEN US PM via the Project Manager.

When accepted, the Contractor shall provide two (2) sets of the documents, in stiff-backed ring binders, to the Project Manager at the handover inspection. The handover shall not take place without this documentation being accepted by the Project Manager.

Digital scanned copies of the completed/accepted hard copy O&M manuals should be provided on a finalised DVD-R disc in a similar sub-divided folder structure to that of the hardcopy/form 141.

An Operational & Maintenance Instruction Manual (O&M Manual) shall be provided containing the information necessary to enable the Client to safely operate, maintain, dismantle, reassemble, re-commission, modify and adjust, all parts of the Works (civil, mechanical, electrical and instrumentation). The Works shall not be regarded as complete until the full O&M Manual(s) have been provided and approved by the Client.

The process is further detailed in DE Tech 12. The table below summarises the requirements.

Table 4.1:	Handover Timetable

| Time | Document | Requirement |
| --- | --- | --- |
| Twelve (12) weeks prior to completion | Handover Document proposal | Index of Handover Document enclosures |
| Six (6) weeks prior to completion | Initial Draft Handover Documents | Detailed schedule of enclosures with brief descriptions. This shall include details of all the manuals and test certificates etc. All materials installed at this point shall be included. |
| Two (2) weeks prior to completion | Revised Draft Handover Documents | Full set of all proposed handover documents including working drawings marked up by hand |
| Completion | Finalised Handover Documents | Documents accepted by the PM in final form including as-built record drawings |

On completion as installed and as-built drawings are also to be provided by the Contractor to 48 CES GEOBASE office via the Project Manager on a separate disc duplicating information provided for the O&M manuals. Contractor to confirm with the Project Manager the current AutoCAD and other individual file / naming / formatting that is required by 48 CES.

## Notice of Completion

The Contractor shall give the Project Manager at least four (4) weeks’ notice of the anticipated date of completion of the whole or sections of the works and inform the Project Manager of where their attendance is required for activities to allow for the works to be completed.

# WI 500 Programme

## Sequencing of the Works

At Contract Award, access to the facility shall be provided to the Contractor to allow survey work and design, etc., to proceed. During the design phase, further requirements for access and handover of the facilities will be discussed, along with detailed phasing requirements, for the grant of vacant possession to Contractor at the date of works mobilisation.

The works shall be undertaken in sections of six (6) PAS’s being made available at any one time although this may increase or decrease dependent on constraints to their electrical supply, geographical location on Base and taxiway operations as the programme progresses. PAS’s can be handed back individually and a new one will be released subject to funding and constraints as above.

## Programme

### Requirements of the programme

The construction works shall not commence until the 100% design submission process is completed and the final design accepted and all documentation complete. The design period below is a generic example showing the design being completed within a 32 week period from the project mobilisation meeting: The Employer review periods of, four (4) weeks for the 65% Design, four (4) weeks for the 95% Design and four (4) weeks for the 100% Design are mandatory, the Contractor has the option to submit alternative design submission preparation periods to those listed below.

The “design” section of the programme shall, as a minimum, include the following activities and the associated durations for the acceptance periods for the Project Manager/Employer:

Security clearances

Design periods

35% design presentation: four (4) weeks

65% design submission: ten (10) weeks (Includes the onboard 35% design presentation at four (4) weeks)

- Acceptance by the Project Manager and any comment by the Employer shall be carried out within four (4) weeks of the submission of the 65% design

95% design submission: six (6) weeks

- Acceptance by the Project Manager and any comment by the Employer shall be carried out within four (4) weeks of the submission of the ‘95% design’

100% design submission: four (4) weeks

- Acceptance by the Project Manager and any comment by the Employer shall be carried out within four (4) weeks of the submission of the ‘100% design’

Planning and mobilisation by the Contractor

Adjustment, commissioning and testing of all engineering services and installations

Running in / proving period

Work by or on behalf of the Employer and concurrent with the Contract

- Programme durations for the design submission phases shall be developed by the Contractor or they can be as listed above; however, the programme durations for all aspects of the construction phase shall be developed by the Contractor.

The Contractor shall ensure that they allow themselves sufficient time to obtain the appropriate security clearances and Base passes so as not to delay the works, with the application period to run concurrently with the design period.

When developing the programme, the Contractor shall make themselves aware of the required approvals to be sought from the appropriate authorities, including the Base, DIO and any other relevant stakeholders before the proposed works can progress.

A three (3) week mobilisation period shall be allowed for in the Contractor’s programme following completion of the 100% design submission, to ensure adequate provision of welfare facilities on Site and the review process is completed. Note that welfare facilities cannot be sited until the construction waiver is in place.

The period for construction, commissioning and handover of the works, shall take into account any further constraints contained within this Works Information. However, this programme shall show the above design periods and also satisfactory periods for commissioning and handover.

The tracked programme shall be reissued by the Contractor on a monthly basis. The programme shall also be submitted to the Project Manager within 1 week of an instruction by the Project Manager.

Should the Contractor have any items of Plant and Materials with a long lead-time then the Contractor shall identify these in the programme and any separate design submissions that are required, allowing for review periods as above.

All milestone payment events must be linked to activities that are on the critical path of the programme and should be numbered sequentially by the date in which they will be claimed, not activity commenced. The programme shall also include the key milestones for handover procedures as detailed in DIO USAFE Standard Tech 012.

### Phasing

The Contractor shall provide at tender stage a clear development control plan for phased construction, which will set out the mobilisation, any enabling and diversion works, construction and demolition/strip out phases, including any sub-phases. It is preferred that the works are completed in a single phase.

### Programme/progress

The Contractor shall record progress on a copy of the programme kept on Site. If any circumstances arise which may affect the progress of the works, the Contractor shall put forward proposals or take other action as appropriate to minimise any delay and to recover any lost time.

# WI 600 Quality management

## Workmanship

### General quality of installed Plant and Materials

All Plant and Materials shall be new and previously unused, unless otherwise specified in this Works Information.

For products specified to a British or European Standard, certificates of compliance shall be obtained by the Contractor from manufacturers, to provide the Works or when specifically requested by the Project Manager.

Where a choice of manufacturer or source of supply is allowed for any particular product, all components required to complete an element of the works must be of the same type, manufacturer and/or source, unless otherwise agreed with the Project Manager.  The Contractor shall produce written evidence of sources of supply when requested by Project Manager.  If products are prone to deterioration or have a limited shelf life, the Contractor shall order in suitable quantities and use these products in an appropriate sequence.

#### Aesthetics and neat installation

The Contractor shall ensure that all Plant and Materials shall be capable of passing through any door or roof openings necessary to achieve its final location and future replacement.

Full allowance shall be made in setting out the runs of pipe and equipment location for the future removal of parts of the works as may be required for maintenance purposes.

#### Equivalent Plant and Materials

The Contractor may submit a proposal to the Project Manager, for their acceptance, to use Plant and Materials from a manufacturer which has not been specified in this Works Information. The Contractor shall submit documentary evidence that the alternative Plant and Materials are equivalent in respect of material, safety, reliability, function, compatibility with adjacent construction, availability of compatible accessories and, where relevant, appearance. Certified English translations of any foreign language documents shall be submitted for acceptance.

Any proposal for use of alternative Plant and Materials must also include proposals for substitution of compatible accessory Plant and Materials and variation of details as necessary, with evidence of equivalent durability, function and appearance of the construction was a whole. The operation of and any documentation associated with any Plant and Materials proposed to be utilised shall be in English.  If such substitution is accepted by the Project Manager, and before ordering the relevant Plant and Materials, the Contractor shall provide revised drawings, specification and manufacturers’ guarantees as required by Project Manager.

Wherever products are specified by proprietary name and the phrase “or equivalent” is not included it shall generally be deemed to be included.  Any exceptions to this, for example where a specific product must be used to ensure compatibility and standardisation with existing equipment, are noted within this Works Information.

### Protection of products

#### Robustness

The works shall be designed to withstand continual and robust usage.  The works, including all finishes, fittings and services installations, shall be of robust construction appropriate to their proposed use and life-span.

#### Kitemarked Plant and Materials

Kitemarked (or equivalent standard) Plant and Materials shall be used, where available.

#### Use of Timber

The Contractor shall note that all timber, both soft-wood and hard-wood, is to be sourced from managed, sustainable sources to be suitably identified, labelled and monitored throughout the duration of the contract.

### General quality of workmanship

The Contractor shall take responsibility for all aspects of the works, including the quality of workmanship carried out, including the following:

Operatives must be appropriately skilled and experienced for the type and quality of work they are to undertake.

All necessary precautions shall be taken to prevent damage to the work from frost, rain and other hazards.

Components and products shall be inspected carefully before fixing or using in the works, with any defective components and products to be rejected.

All components shall be fixed or laid securely, accurately and in alignment.

Fastenings are to comply with all relevant standards.

Suitable, tight packings at screwed and bolted fixing points shall be provided to take up tolerances and prevent distortion, with fixings not overtightened.

The location and fixing of components and products shall be adjusted so that joints which are to be finished with mortar or sealant or otherwise left open to view are even and regular.

All moving parts shall be installed so that they operate properly and freely. Pre-finished components and products shall not be cut, ground or planed to remedy binding or poor fit without approval.

The Contractor shall prepare a specification incorporating specific requirements of this Works Information, in particular he shall include in his specification clauses pertaining to the testing and standards of workmanship. The NBS Standard Specification shall be taken as a minimum standard for materials and workmanship. Particular attention is drawn to the Third Party Quality Assurance Schemes and the Contractor is to specify, where possible, those products in order to achieve compliance with the Employer.

### Samples

Where acceptance of products is required, the Contractor shall submit samples or other evidence of suitability. Orders shall not be confirmed or Plant and Materials used by the Contractor until acceptance of samples has been obtained from the Project Manager. All samples accepted shall be retained and stored in a good, clean condition on Site, for comparison with other Plant and Materials used in the works. All samples shall be removed by the Contractor by the end of the contract or when the Project Manager has confirmed that the sample is no longer required.

### Samples of finished work

Where samples of finished work are specified the Contractor shall obtain approval of stated characteristic(s) before proceeding with the works. The Contractor shall Retain approved samples in good, clean condition on site for comparison with the works. The Contractor shall remove samples which are not part of the finished works when no longer required.

## Photographs

The use of photographic equipment on the Site shall require the issue of a permit via prior approval and application through the USAF Project Manager (allow four (4) weeks) and is enforced by the Base’s Security Forces. The USAF Project Manager will confirm general restrictions and requirements for photography at the Base. Typically, this could include inspection of any photographic equipment and photos to ensure security is not compromised.

The Contractor shall provide a sufficient number of colour progress photographs to represent the works on site from points agreed with the Project Manager at monthly intervals in JPEG format at 300dpi min resolution on CD. The Contractor shall note that photographs may only be taken when an authorised representative of 48CES/SF is in attendance.

# WI 700 Tests and inspection

## Tests required

### Testing, pre-commissioning and commissioning

The Contractor shall provide to the Project Manager a commissioning plan, including method statements for all testing, pre-commissioning and commissioning works. The commissioning plan shall be submitted, for the Project Manager’s acceptance, at least 4 weeks prior to the proposed commencement of commissioning. The timing and method of all commissioning shall also be subject to agreement with the Employer.

The Contractor shall demonstrate that all installed Plant and Equipment meet their specified requirements during the commissioning stage, including demonstrating to the Project Manager and the Employer that maintenance can be safely and appropriately carried out, in accordance with all manufacturers’ instructions and costs in connection with extending warranty / guarantee periods.

The Contractor shall clearly indicate on his programme the dates when light shall be available for any area. The Contractor shall allow for the general use of the lighting equipment after these dates prior to commencement of any defect liability period for the purpose of final finishes works including the costs of:

Extending warranty/ guarantee periods

Maintenance to comply with manufacturers’ instructions

Attendance by suitably qualified personnel

Any other associated works in connection with this clause

The Contractor, having ensured that electricity, water, fuel and other necessary supplies are available, shall set to work the completed works or part thereof, at the selection of the Project Manager, and make all necessary adjustments to ensure correct functioning.

After the installation or part thereof has been set to work and adjusted, the Contractor shall demonstrate its operation at a time and for a duration selected by the Project Manager.

The tests shall demonstrate, amongst other things, that:

The Plant and Equipment provided complies with this Works Information and is of adequate capacity for its full rated duty.

All items of Plant and Equipment operate at the volumes stated by the manufacturers

All electrical circuits are properly fused, graded and protected, and conduit systems are electrically continuous and properly earthed.

Any representative of the Employer shall be at liberty to be present and to participate in the tests. This shall not relieve the Contractor of his responsibilities for carrying out the tests satisfactorily.

The Contractor shall make all necessary records during the tests and, on completion thereof, shall provide the Supervisor with two copies of all test reports and records, for the Supervisor’s acceptance.

The Contractor shall provide all necessary Equipment, including adequately trained and experienced personnel, for carrying out the testing and commissioning.

If tests fail to demonstrate the satisfactory nature of the installation, or portion thereof, the Contractor shall carry out such alterations or replacements as are required to ensure satisfactory operation of the works. The Supervisor shall be at liberty to call for a further test after such alterations have been made; the Supervisor’s decision as to what constitutes a satisfactory test shall be final.

It is important that testing does not disrupt the Employer’s existing installation or systems; the Contractor shall be fully responsible for any costs or consequential losses arising from any failure to ensure this.

Prior to handover the Contractor shall provide suitable and sufficient training on the installed systems for Employer maintenance personnel. The current expectation is that this will be a minimum of two days.

### Defects in existing construction

Any Defects shall be reported to the Supervisor without delay. The Contractor must obtain instruction from the Project Manager before proceeding with any work which has the potential to:

Cover up or otherwise hinder access to the defective construction, or

Be rendered abortive by the carrying out of remedial work.

### Timing of tests and inspections

The Contractor shall agree dates and times of tests and inspections with the Supervisor at four weeks in advance of the relevant dates and times of tests, to enable the Supervisor and other affected parties to be present. The Contractor shall confirm to the Supervisor at least five working days prior to each such test or inspection that the work or sample in question is ready or, if not yet ready, agree a new date and time for the test and inspection.

### Test certificates

The Contractor shall submit a copy of each certificate to the Supervisor as soon as practicable and keep copies of all certificates on Site. All test certificates are to be completed and form part of the maintenance manuals.

### Proposals for rectification of defective Plant and Materials

As soon as possible after any part(s) of the works or any Plant and Materials are known to be defective or not in accordance with the contract or appear that they may not be in accordance, the Contractor shall submit proposals to the Supervisor for opening up, inspection, testing, making good, or removal and re-execution.

The Supervisor may issue different instructions to the Contractor if the proposals of the Contractor are deemed unacceptable.

### Measures to establish acceptability

Wherever inspection or testing shows that the work, or products are not in accordance with the Contract and measures, such as during testing, opening up and making good, are taken to help in establishing whether or not the work is acceptable, such measures:

shall be at the expense of the Contractor

shall not be considered as grounds for an extension of time

### Quality control

The Contractor shall establish and maintain procedures to ensure that the Works, including the work of all Subcontractors, comply with specified requirements. The Contractor shall maintain full records, keep copies on Site for inspection by the Project Manager, and submit copies of particular parts of the records on request.

The records must include:

Identification of the element, item, batch or lot, including location within the works

The nature and dates of inspections by the Supervisor, including all tests and test acceptances

The nature and extent of any non-conforming work found

Details of any corrective action for non-conforming work

### Work at Completion

The Contractor shall:

Make good all damage resulting from the works

Remove all temporary markings, coverings and protective wrappings unless otherwise instructed

Undertake a deep clean of the works, thoroughly inside and out including all accessible ducts and voids, remove all splashes, dust, deposits, efflorescence, rubbish and surplus materials consequent upon the execution of the work, referring to section 4.2.7.

Cleaning materials and methods shall be as recommended by manufacturers of the products being cleaned and are to be such that there is no damage to other materials or plant.

Obtain COSHH dated data sheets for all materials used for cleaning and ensure they are used only as recommended by their manufacturer.

Correct minor faults in newly coated/recoated work, carefully matching colour, and brushing out edges. The Contractor shall recoat badly marked areas back to suitable breaks and junctions.

Adjust, ease and lubricate moving parts of the Plant and Materials as necessary to ensure easy and efficient operation, including valves and controls.

Rectify all Defects identified which would prevent the Employer from using the works and Others from doing their work.

### Security at completion

Prior to Completion, an inspection shall be made by the Base Security Forces to inspect the installation and certify its security. Access must be granted by the Contractor for this inspection.

At Completion, the Contractor shall:

Leave the works secure with all accesses locked to an appropriate standard.

Account for and adequately label all keys, handing these over to the Employer with an itemised schedule, retaining a duplicate schedule which has been signed by Employer as a receipt.

### Making good Defects

The Contractor shall:

Make arrangements with the Supervisor and give reasonable notice of the precise dates for access to the various parts of the works for purposes of making good Defects.

Inform the Supervisor when remedial works to the various parts of the works are completed.

The Contractor shall attend to make good any Defects within 24 hours any Defects which are identified as having the potential to compromise the running and use of the works.

## Notices for Witnessing

The Contractor shall give Project Manager, Supervisor and DSA fire officer at least 4 weeks’ notice of their proposed dates of carrying out testing and commissioning of all mechanical and electrical Plant and Equipment and any testing and investigation of Structural elements.

## Notice of Completion

The Contractor shall give PM at least four (4) weeks notice of the anticipated dates of Completion of the whole or parts of the Works.

# WI 800 Management of the works

## Site organisation

The Contractor shall maintain a site organisation under the full-time control of the Contractor’s agent who is conversant with British Standards and codes of practice and with the health, safety and welfare regulations and is experienced in project managing similar contracts and capable of assuming complete responsibility for a contract of this nature.

### Changes to proposed key works staff

The Contractor’s proposed management structure and staff should be as detailed in his Tender. Any subsequent alternative proposals for staffing should be at least equal in standard to the original staff proposed and are subject to acceptance by the Project Manager.

### Coordination of the works

The site organisation staff must include persons during both the design and construction phases with appropriate knowledge and experience of their technical discipline and the interrelation and compatibility between other disciplines and existing services. The Contractor shall submit to the Project Manager, when requested, CVs or other documentary evidence relating to staff employed on the works.

### Status and experience of Contractor’s key staff

#### Design coordinator

Throughout the duration of the works, the Contractor shall include a person responsible the design of the works, who is experienced in the co-ordination and control of the design process. A fully detailed quality assurance procedure for the co-ordination and checking of the design undertaken by the design team shall be maintained by this member of staff. They shall be responsible for:

The management of the Contractor’s design

Acting as a focal point for the issue of drawings to the Project Manager and the receipt of comments

Co-ordination between the design team and the Site team

Control of the issue of construction status production information to Site

Design co-ordination between the Contractor’s departments, including Subcontractors and if applicable, any statutory authority.

#### Mechanical and Electrical Design Coordinator

Throughout the duration of the works, the Contractor shall include a person who is responsible for the design of mechanical and electrical aspects of the works. A fully detailed Quality Assurance procedure for the co-ordination and checking of the design undertaken by the Design Team shall be maintained by this member of staff. They shall be responsible for:

The management and coordination of the Contractor’s mechanical and electrical design

The review of design packages prior to formal submission, to ensure that designs are checked and co-ordinated between disciplines

Control of the issue of construction status M&E production information to Site

Ensuring that installation at Site matches what is stated in the Contractor’s designs

Managing and coordinating with the Supervisor for the testing and Defect rectification processes.

#### Structural Design Coordinator

Throughout the duration of the works, the Contractor shall include a person who is responsible for the design of structural aspects of the works. A fully detailed Quality Assurance procedure for the co-ordination and checking of the design undertaken by the Design Team shall be maintained by this member of staff. They shall be responsible for:

The management and coordination of the Contractor’s structural design

The review of design packages prior to formal submission, to ensure that designs are checked and co-ordinated between disciplines

Control of the issue of construction status structural production information to Site

Ensuring that installation at Site matches what is stated in the Contractor’s designs

Managing and coordinating with the Supervisor for the testing and Defect rectification processes.

#### Chartered Fire Engineer

Throughout the duration of the works, the Contractor shall include a person who is in overall control of the fire engineering design, who is qualified, competent and experienced in the coordination and control of the fire engineering design process. The fire protection engineer shall be experienced in works of a similar type to these works.

This person shall meet the post description as defined in UFC 3-600-01, which is repeated below:

“A qualified fire protection engineer is an integral part of the design team, and must be involved in every aspect of the design as it relates to fire protection. This includes, but is not limited to, building code analysis, life safety code analysis, design of automatic detection and suppression systems, water supply analysis, and a multi-discipline review of the entire project. For the purposes of meeting this requirement, a qualified fire protection engineer is defined as an individual meeting one of the following conditions:

An engineer having a Bachelor of Science or Master of Science Degree in Fire Protection Engineering from an accredited university engineering program, plus a minimum of 5 years work experience in fire protection engineering.

A registered professional engineer (P.E.) who has passed the fire protection engineering written examination administered by the National Council of Examiners for Engineering and Surveys (NCEES).

A registered P.E. in a related engineering discipline with a minimum of 5 years’ experience, dedicated to fire protection engineering that can be verified with documentation.”

The fire protection engineer shall be responsible for:

The completion of the fire strategy document and associated design packages

Ensuring that the design and works comply with the fire protection requirements of the Works Information.

## Site Progress Meetings

Once construction has commenced at Site, progress meetings shall be held at least monthly.  The Contractor shall ensure the availability of accommodation at the time of such meetings.  The Contractor shall attend all meetings and inform Subcontractors and suppliers when their presence is required.

### Reporting Requirements

The Contractor shall submit a progress report, at least five (5) working days prior to the site progress meetings, which includes, as a minimum:

Updated programme (Gantt Chart & QSRA) showing progress against the accepted programme, with the summary to include a percentage achieved against percentage planned

Gantt chart and QSRA accepted programme marked up with a progress drop line

Explanation of any changes to the Programme (including actual or potential delays and the Contractor’s proposals for mitigation)

Schedule of milestones showing those achieved and dates for future milestones

Register of Early Warnings and Compensation Events

Updated NEC Risk Register noting Risks requiring review by the parties

Any value engineering proposed

Schedule of requests for information, showing outstanding items

Validation of works against Proof of Compliance Plan

Health and safety summary records (including AIR / RIDDOR)

Records of resources used on site

Availability of materials

Any changes to approved Subcontractors

Waste transfer details

Quality Control

Information Required

Base Issues

Design Update

### Information Requirements / Electronic Systems and Communications

Information storage and communication shall be in line with the construction security regulation relevant to the contract is JSP 440 Defence Manual of Security, Resilience & Business Continuity. .

The Contractor shall propose to the Employer and Project Manager a suitable online electronic system for the management of the Contract. The acceptance of this system shall be at the sole discretion of the Project Manager.

The online Contract Event Management and Reporting tool for NEC3 - ‘CEMAR®’ has been tested on the Employers network and has been confirmed to be a suitable working platform for the organisation of event management and reporting. The Contractor is to approach CEMAR® or a similar provider and include within their works all costs associated with the use of CEMAR® or equivalent to gain a tailored online management tool suitable for this Contract.

The online extranet document management system Aconex has been tested on the Employers network and has been confirmed to be a suitable working platform for the distribution and design information for review and acceptance. The Contractor is to approach Aconex or a similar provider and include within their works all costs associate with the use of Aconex or equivalent to gain a suitable extranet for this Contract.

A combined system for contract and document management would be acceptable.

The Contractor shall obtain approval from MoD for use of their proposed online systems for Contract Event Management and Reporting and Document Management.

## Aircraft Operations

The Contractor shall comply with the establishment flying control regulations and instructions regarding the movement of heavy goods vehicles, plant, work people etc. Provide approved danger markings on plant, structures, dumps of material etc. Copies of the regulations/instructions may be seen by prior arrangement with the Base Civil Engineer.

The Contractor must comply with any instruction provided on the ground by Military Personnel. The USAF PM and Project Manager must be informed immediately of any instruction provided.

## Foreign Object Damage (FOD)

The Works are on an active airfield, the Contractor shall take all necessary precautions to prevent the risk of debris arising from the Works being transferred onto the active Airfield.  This shall include, but not be limited to, the following:

Ensuring that all contract personnel are made aware of and comply with all mandatory FOD checks;

The incorporation of anti-FOD fabric/netting to compound and site boundary/free-zone fencing and gates;

All necessary anchoring/covering of items which have potential to be lifted and transported by wind;

Maintained usage of dedicated haulage routes which shall kept free of mud and detritus by frequent sweeping/cleaning;

General good housekeeping / site cleanliness; and

Skips covered at all times.

Should local agreement allow Works to be conducted within the active Airfield, the Contractor shall operate a signing in - signing out procedure for all tools/equipment required to complete the works.  In such circumstances, if required, the site operative shall be provided suitable cleaning equipment to ensure that the working area if left suitably clean on completion.  This may include provision of dust pan and brush or wet and dry vacuum depending on the nature of the task.

## Climatic Conditions

The Contractor shall keep an accurate record of:

Daily maximum and minimum air temperatures (including overnight).

Delays due to adverse weather, including description of the weather, type(s) of work affected and number of hours lost.

This shall be made available to the Project Manager and Employer within monthly progress reports and upon request.

# WI 900 Working with the Employer and Others

## Working with the Employer and Others

The Contractor shall provide coordination / access for others during the project e.g. to enable any works to the vaults.

### Liaison with agencies acting for the Employer

Work on the Base shall involve liaison with a large number of agencies. All contact with the Base must be carried out through the Base Civil Engineer’s office project manager.  It is envisaged that the agencies involved shall include, but not be limited to, the following:

BMS Administrator

Military Police (Base Police, MDP/MGS, Base Security Forces)

Airfield Management

Weapons/Explosives Safety (48 CES)

Security Forces (48 SF)

Fire Safety Department (DSA, Base Fire Dept)

Safety (48 FW)

Weapons/Explosive Safety (48 FW)

Environmental (Base Civil Engineer)

CE Infrastructure (Base Civil Engineer)

Electrical Utilities (Base Civil Engineer)

Base Operations (48 Ops)

Communications (Base Civil Engineer)

British Telecom (BT)

### Furniture, Fittings and Equipment

The Contractor shall not be responsible for decant of users back into the facility.

# WI 1000 Services and Other Things to be Provided

## Site accommodation

All site accommodation shall be as specified in the Base Standard for Construction Sites.

### Office, storage and workshop accommodation

The Contractor shall provide all office, storage and workshop accommodation for execution of the works and:

Obtain the agreement of the Project Manager as to the location of temporary buildings

Provide sufficient space within the offices and workshops for use by Subcontractors

Provide space for storage of materials by Subcontractors

Provide sufficient protection against the weather for all Plant and Materials and Equipment stored

Maintain, adapt and/or relocate accommodation as required

Remove and clear away all accommodation at Completion, making good any disturbance to existing buildings, services and surfaces.

### Room for meetings

The Contractor shall provide suitable temporary accommodation for Site meetings, which shall be adequately heated and controlled to 18.5ºC.  Lighting to 350 lux illuminance shall be provided together with table and chairs for 20 people.  The room shall be separate to the Project Manager’s office but may be part of the Contractor’s own Site offices.

### Site offices for the Project Manager and Employer

The Contractor shall provide, maintain for the period of the contract and remove on Completion, all temporary offices for the sole use of Project Manager and Employer.  The temporary offices shall have a minimum ceiling height of 2.2 metres, heated and controlled to 18.5°C and lit to 350 lux illuminance.  The requirements for these offices and the provision of power, drinking water, consumables and cleaning services shall be as scheduled below:

Total floor area:

Offices for the Project Manager and Employer: Minimum of 20 m2 consisting of 2 individual offices.

Furniture requirements for office for the Project Manager and Employer:

Furniture: 2 number lockable desks, one table, one lockable cupboard, one plan chest, 3 office swivel chairs, two filing cabinets, two waste bins, one white board, coat hooks

The Contractor shall provide, maintain and insure the following items of equipment for the exclusive use of the Project Manager and his staff, which will remain the property of and be returned to the Contractor on Completion:

- One steel tape of 5m length

- One spirit level of 1m length

- One steel straight edge of 2m length

- One max/min thermometer

Pegs, nails, chalk, paint, lines and other minor consumable items to be provided as directed

The equipment for the Employer and Project Manager’s personnel shall be kept in the Project Manager’s Site office and be available for use on Site until the offices are removed.

Power supply points to the office for the Project Manager and Employer:

At least six 13 amp points.

Kitchen/tea point: power supply points, as required.

Internet / wifi connection (speeds no less than 40Mbps)

Telephone

Drinking Water for the office for the Project Manager and Employer:

Tap and sink plus supply for tea boiler, where required.

Name plates and directional notices:

As directed by Project Manager.

Attendance and cleaning:

On a regular basis at an agreed time, carried out at least once per week.

The Contractor shall bear all charges, including the cost of telecoms and electricity.

The Contractor shall also provide and maintain in a clean condition sanitary accommodation for the use of the Employer, the Project Manager and Others, which can be either separate or shared with the Contractor’s supervisory staff.  The accommodation must include an adequate number of appliances and wash hand basins (with hot and cold water supply) and adequate heating, lighting and ventilation.

### Sanitary facilities

The Contractor shall provide all sanitary, messing and welfare accommodation necessary for the safe execution of the works.

### Site security

The Contractor shall provide a secure and robust Site compound. Site security fencing shall be designed with consideration of the operational requirements of the Base, including the use of fixed wing and rotary aircraft. The Contractor shall install Darfen fencing with fixed posts into the existing concrete hardstanding. The Contractor shall adequately safeguard the site, the Works, products, materials, plant, and any existing buildings affected by the Works from damage and theft. He shall take all reasonable precautions to prevent unauthorised access to the site, the Works and adjoining property.

Due consideration shall be given to breaks which may be required in the perimeter for the installation of temporary and permanent services.

### Signage

The Contractor's and any Subcontractors’ signage shall be submitted to the Base and Project Manager for approval and shall comply with the RAF Lakenheath Base Standards for Construction Sites.

A project sign board shall be provided this shall be submitted to the Base and Project Manager for approval

## Services and facilities

### Lighting and power

Electricity supply from the Employer’s mains may be used for the works as follows:

Supply shall be metered and costs reimbursed to the Employer. The meter shall be installed by the Contractor.

The Employers shall not be held responsible for the effects of any failure or restriction in supply.

The point of supply shall be advised by the DIO AP.

The supply voltage shall be 240 volts, 50 Hz, in single phase.

### Water and drainage

Water from the Employer’s mains may be used for the works as follows:

Supply shall be metered and costs reimbursed to the Employer. The meter shall be installed by the Contractor.

Source: Base water mains

Location of supply point: By arrangement with Employer/Base Civil Engineer

Conditions/Restrictions: By arrangement with Employer/Base Civil Engineer

Conditions/Restrictions: By arrangement with a Base facility manager. Static pressure is limited to 2.5 bar.

The Contractor is to provide his own stand pipes

Backflow prevention shall be provided by the Contractor

### Communications

The Contractor shall:

Provide as soon as practicable after the access date a temporary on-site telephone installation for use by the Contractor and Subcontractors. The Contractor shall pay all charges relating to his usage. The Contractor shall make arrangements to ensure that incoming calls are answered reasonably promptly.

Mobile phones may only be used within the restricted area (including the site compound) by the Contractors supervisor in an emergency only.

Provide as soon as practicable after the access date a separate temporary line with one extension in approved location(s) for the sole use of the Employer or those acting on behalf of the Employer.

Provide as soon as practicable after the access date a suitable on site facsimile installation, with a separate, dedicated telephone line, for use by the Contractor, Subcontractors, the Employer and those acting on behalf of the Employer. The Contractor shall allow for the cost of a modest number of transmissions made by those acting on behalf of the Employer.

Provide jack points for the provision of a broadband connection and pay all charges in connection with the use of this facility.

Provide reasonably unrestricted access to and reasonably limited free use of an on-site photocopier, which may be located in the Contractor’s own Site offices, for which the Contractor shall bear all costs.

### Use of permanent installations

Unless specific permission is given, the permanent supply, disposal, mechanical, electrical, communications and transport installations may not be used for any purpose other than running in, testing and commissioning.

Where the Contractor proposes to use the permanent electrical installation, including use for testing and commissioning electrically driven or operated equipment, the Contractor must:

Obtain prior agreement of the Project Manager

Observe any limitations on extent and nature of use

Install a meter and pay the cost of energy used

Take responsibility for safe operation and the costs of maintenance of the electrical installation for such use

Bear all costs relating to this use

Ensure systems are operated within the design limits to avoid warranty invalidation.

### Meter readings

Where charges for service supplies need to be apportioned, the Contractor shall ensure that meter readings are taken at the required locations and time as appropriate. The Contractor shall ensure that copies of readings are supplied to the relevant parties.

### Thermometers

The Contractor shall provide on-site and maintain in accurate condition:

A maximum and minimum thermometer for measuring atmospheric shade temperature, in a location accepted by the Project Manager.

A thermometer for measuring concrete and ground temperature.

## Use of the Site

### Access restriction and use of the Site

The Site is not to be used for any purpose other than carrying out the works.

Access to many areas of the RAF Lakenheath Base is prohibited to both personnel and vehicles.  Anyone found in, or attempting to access, these areas shall be subject to disciplinary action.  Other restrictions may be enforced during the works dependent on RAF Lakenheath operations.

The Contractor must maintain pedestrian and vehicle access and services to all facilities adjacent to the Site and ensure fire routes and fire muster points are not impeded or blocked for the duration of the works.

### Site compound and laydown area

The area to the north east of the proposed Site shall be used by the Contractor as a laydown area and site compound for at least Phases 1 and 2 this is shown on drawing 375767-MMD-00-XX-GIS-GEN-002. The Contractor’s compound will be located adjacent to a Contractor working on the Fuel Hydrant Main project, close liaison and communication will be required and access for fire tenders must be maintained. The cabins shall be erected on ground prepared by the Contractor within the Site compound.  The Contractor’s facilities may utilise multiple storeys.

Heras fencing is the preferred fencing for the site boundary.

The Contractor shall be entirely responsible for restricting access to the Site to his personnel and visitors and shall ensure that the security of any entrances and any fencing is maintained at all times.  The Contractor shall be required to maintain records of personnel at the Site at all times and shall be responsible for ensuring that this information is transferred to the security personnel at the main gate at RAF Lakenheath.

Designated safe pedestrian and vehicular walkways shall be provided by the Contractor to ensure the safety of pedestrians entering and walking around the Site.

The Contractor shall adequately safeguard the Site, all aspects of the works, any Plant and Materials and Equipment and any existing buildings affected by the works from damage and theft.  The Contractor shall take all reasonable precautions to prevent unauthorised access to the Site and adjoining property.

The Contractor shall ensure that this Site compound is maintained in a neat and tidy manner at all times.

Parking of the Contractor’s and employees’ vehicles will be restricted to the Contractor’s Site compound.

# WI 1100 Health and safety

## Health and safety

The Contractor will be appointed as the “Principal Contractor” and “Principal Designer” under the Construction (Design and Management) Regulations 2015 and carries out all duties required by the regulations.

The Contractor shall provide details of how he proposes to safeguard the health and safety of all its operatives, Subcontractors, Others and anyone else associated with the works. These details shall include:

A copy of the Contractor’s health & safety policy, including all required risk assessments.

Contractor’s complete accident and illness records for the past 5 years.

Contractor’s records of any previous H&S enforcement action.

Contractor’s records of training and its training policies

The number and type of staff responsible for health and safety for this contract, with details of their qualifications in relation to health and safety and their proposed duties.

- The Contractor shall provide an acceptable construction phase health and safety plan prior to commencement on Site.

### Risks to health and safety

All relevant national health and safety legislation shall apply, including the requirements of CDM Regulations 2015.

As part of these regulations, the design process must consider the facility whilst it is in use.

The health and safety plan, policy documents and local regulations of RAF Lakenheath shall be fully complied with.

## Safety Equipment

The Contractor shall inform the Project Manager prior to entry onto the Site of all safety provisions and procedures, including those relating to Plant and Materials used by the Contractor which may be deleterious, which will require the compliance of the Employer or its representatives when visiting the Site.

All safety equipment, breathing apparatus and protective clothing required to Provide the Works by the Contractor’s personnel, the Project Manager’s personnel and the Base security personnel shall be provided and maintained by the Contractor.  All such equipment and procedures shall be in accordance with MOD safe systems of work and UK regulations.

The Contractor shall provide all necessary basic provisions to ensure the safety, health and welfare of all personnel on Site, including the Employer, the Employer’s representatives and Others. The Contractor shall provide the following:

Four general purpose industrial safety helmets to BS 5240: Part 1, in accordance with the Construction (Head Protection) Regulations 1989.

Four Class 3 high visibility jackets to BS EN 471.

An adequate supply of suitable safety glasses, general purpose safety gloves and ear defenders as appropriate.

# WI 1200 Subcontracting

## Restrictions or requirements for subcontracting

The Contractor is required to provide a schedule of Subcontractors for the scheme for all elements of the works. The schedule should state, the Subcontractor’s:

Company name

Registered office

Annual turnover (in pounds sterling)

Projects in which the Subcontractor has worked for the Contractor in the past 5 years

The Contractor complies with the following limitations on subcontracting:

The Contractor does not subcontract the management or supervision of the works

Subcontractors must not be replaced or changed by the Contractor from those stated at tender stage without the prior written acceptance of the Project Manager.

# WI 1300	Title

## Marking

The Contractor shall identify and tag each item of plant in accordance with DIO Specification 034. This shall include tagging of all items of civil, mechanical and electrical Plant and Materials, including all instruments, motors, valves and pumps.

All tagged items shall be listed on a plant item list. The Contractor shall submit the plant item list in the Employer’s required format.

## Materials from Strip Out and Demolition

The Contractor shall remove all unusable materials and plant and dispose of said materials at a suitable licensed landfill  or recycling centre as appropriate. Redundant plant, motors, panels shall be offered to the Employer prior to disposal including but not limited to the following:

Door Motors

Control Gear including pedestal and panel

Light movement sensors

Side and emergency lights

Main distribution board

Generator changeover panel

It is likely the Employer will only require parts from the initial Phase of PAS’s to keep the remaining PAS’s in operation during the programme.

Appendices

A. General Specification 59 B. Civil and Structural Engineering Specification 63 C. Mechanical Specification 76 D. Electrical Specification 82 E. Fire Precautions 107

General Specification

General Description

At RAF Lakenheath, repairs are required to 58 No. Protective Aircraft Shelters (PASs) to enable the continued operational use by the United States Visiting Force (USVF). The PASs are located around the runways and taxiways on the airfield at RAF Lakenheath and are used for the storage, maintenance and testing of F-15E aircraft.

Each PAS consists of a single storey curved barrel vault roof structure approximately 36m long by 22m wide and 9 m high. The front of each Shelter is protected by motorised, bi-parting, heavy, steel-framed doors with external welded steel lattice for stability. The rear wall is concrete with internal metal protective plates and has a pair of manually-operated, centrally-placed, bi-parting, heavy, steel protective doors. These doors open to reveal the jet exhaust efflux structure behind which is there to vent the jet exhaust of the aircraft while their engines are running.

General Requirements

The Contractor shall design facilities, and their associated systems, that are suitable for the End User purposes as described in the Works Information and are reliable with minimal on-going maintenance.

Design Standards

In general, for all design issues, the most onerous and mandatory of the UK or US requirements shall be applied. The Contractor’s design shall satisfy all relevant specifications and standards, which includes, but is not limited to, the following:

General Specifications and Standards

The Building Regulations Approved Document B

British Standards and Codes of Practice

The Health and Safety at Work Act 1974, and all associated regulations, including:

Construction (Design and Management) Regulations

The Electricity Safety, Quality, and Continuity Regulations

The Electricity at Work Regulations

HSE Noise at Work Regulations (especially Guides 1-8, S11790/1988)

The Control of Substances Hazardous to Health Regulations

Management of Health and Safety at Work Regulations

The Control of Pollution Act 1974 and amendment Acts

The Workplace (Health, Safety and Welfare) Regulations

The Control of Asbestos at Work Regulations

The Provision and Use of Work Equipment Regulations

The Personal Protective Equipment at Work Regulations

The Lifting Operations and Lifting Equipment Regulations

British Board of Agreement (for tested products)

Environmental Protection Act

Energy Conservation Act

Local authority by-laws, and local Environment Agency recommendations where appropriate

BS EN 60079-10-1 Explosive atmospheres

BS 8300 - Design of buildings & their approaches to meet the needs of disabled people

National Joint Utilities Group Guidelines, particularly Volume 1 Positioning and Colour Coding of Underground Utilities' Apparatus

Traffic Signs Regulations of General Directions

Dangerous Substances and Explosive Atmosphere Regulations (DSEAR) (Refer JSP 375 Chapter 9)

Defence (and partners) Specifications and Standards

The Contractor shall be aware of and be compliant with the requirements of the following MOD and Defence Estates publications:

Design & Maintenance Guides, including:

DMG 03 - Storage of Dangerous Substances

DMG 08 – Design and Maintenance Guide

DMG 16 - Asbestos Based Materials

DMG 17 - Design Energy Targets

Specifications, including:

PSA Standard Specification 158

DIO Functional Standards (as appropriate e.g. 1, 7)

DIO Specifications (as appropriate e.g. 034, 039)

DE (DIO) USVF Standards, including:

MOD DE/USF Guidance Note ref 201.120 rev 2 March 2002

DE USAF TST 0121

MIL STD 3007

DIO Local Operating Instruction SD TFM USF SMT LOI 13/14 – Fire Safety Compliance Process

TECH 003 – DE USF HazMat & Pollution Prevention Procedures

TECH 004 – DE USF HazMat Spill Planning & Reporting Procedures

TECH 005 – DE USF Division Asbestos Survey Procedures

TECH 012 – DE USF Handover Process for Works Projects

Joint Service Publications, including:

JSP 375 – Management of Health and Safety in Defence

JSP 418 - MOD Environment Manual

JSP 482 - MOD explosives regulations

Health & Safety Warning Notices

Technical Bulletins

MOD Building Regulations Compliance System

Defence Infrastructure Fire Standards(DIFS)

Explosives Storage and Transport Committee (ESTC) Standard No. 6

Most of these documents are available from the Stationery Office. The Contractor is expected to purchase any published matter, including Stationery Office publications. Alternatively, several documents are available in electronic form on the Defence Infrastructure Organisation's website Download Area.

The Contractor shall also be aware of and comply with the following USA and USAF publications:

RAF Lakenheath Base Standards and Architectural Compatibility Guide

Current Engineering Technical Letters

All current design and construction guidance published by the Air Force Civil Engineering Center (AFCEC)

Air Force Instructions (AFI’s)

AFI 32-1065 Grounding Systems

AFI 32-1054 Corrosion Control Air Force 31 Series Publications (Security)

Air Force 32 Series Publications (Civil Engineering)

HQ USEUCOM AT OPORD 16-03 18 Mar 2016Antiterrorism

International Building Code, current edition

NFPA’s (Particularly  NFPA 70 National Electrical Code, NFPA 101 Life Safety Code, current edition)

Unified Facilities Criteria especially but not limited to:

UFC 4-211-01 Aircraft Maintenance Hangars

UFC 3-260-01 Airfield and Heliport Planning and Design, Appendix B, Section 14

UFC 3-401-01 Mechanical Engineering

UFC 3-420-01 Plumbing Systems

UFC 3-501-01 Electrical Engineering

UFC 3-520-01 Interior Electrical Systems

UFC 3-530-01 Design: Interior and Exterior Lighting and Controls

UFC 3-535-01 Visual Air Navigation Facilities

UFC 3-270-01 O&M Manual: Asphalt and Concrete Pavement Maintenance and Repair

PDC Technical Report 10-02

AFMAN 32-1084 Facility Requirements

Air Force Space Command Military Construction Project Guide

Most UFC and AFI documents are available to download from the Whole Building Design Guide website (www.wbdg.org). US Air Force documents may be obtained from the Air Force e-Publishing website (www.e-publishing.af.mil). All other US documents are available from the End Users. Any documents marked ‘FOUO’ require the Contractor to demonstrate a specific need to access the document. These may be obtained from the Employer (in part or in whole, as necessary), and may be subject to security processes and/or controls.

Other requirements;

Loss prevention Council (LPC) rules

Insurance Company Requirements. - AGE Pads Flood lighting, may be some for doors.

- (Discuss with 48 CES via the Project Manager)

Civil and Structural Engineering Specification

General Requirements

All new civil engineering works and structural alterations works shall be designed and constructed in accordance with all appropriate UK and European Codes of Practice to safely sustain and transmit to the foundations the combined dead, imposed and wind loads without failure or undue deflection or movement such as would impair the operational requirements, stability or serviceability of any part of either the altered or existing structure, or any adjacent existing structural element.

Building Form

Based on the record drawings available, the Protective Aircraft Shelters (PAS) were originally constructed around 1981/82 with subsequent replacement work being carried out in 1993 and 2001 to replace the main shelter door roller bearing assemblies.

Shelter Roof

Each Protective Aircraft Shelter (PAS) primarily consists of a single storey, cast in-situ, reinforced concrete, curved barrel vault roof structure with external dimensions approximately 37m long by 23m wide and 9 m high, and with a bolted, curved, corrugated, galvanised steel inner lining that was originally provided as permanent formwork during concreting and to serve as anti-spall protection in service. The concrete vault thickness varies with the depth of the steel liner corrugations but is thought to be at least 600mm thick at the outermost edges of the steel liner corrugations.

The barrel vault roof structure is assumed to be supported on a deep reinforced concrete ground beam along each side (which is continued along the rear wall) with a series of reinforced concrete tie beams lying across the width of the Shelter and buried beneath the floor slab, all to create a bow-string arch as the fundamental structural form.

Shelter Doors

The front of each Shelter is protected by motorised, bi-parting, heavy, steel-framed doors with cast in-situ, reinforced concrete, infill facing slabs thought to be about 600mm thick with steel sheet inner linings exposed on the inside face of the Shelter. These doors are stabilised by external welded steel frame structures with counterbalance concrete blocks, all running on roller bearings travelling along two sets of parallel door tracks with steel strips set into the existing apron slab/ground beams. One track is provided along the line of the door panels themselves and the other is provided along that of the counterbalance blocks. Each door section is estimated to weigh about 80 tonnes.

Rear Wall of Shelter

The inside face of the reinforced concrete rear wall of each Shelter is protected by approximately 2mm thick overlapping, galvanised steel plates fixed with a regular pattern of welded-on steel studs or J-bolts cast into the wall. These plates were originally provided as permanent formwork during concreting and to serve as anti-spall protection in service.

The rear wall also has a pair of manually-operated, centrally-placed, bi-parting, sliding, heavy, steel protective doors which are top-hung on rollers from a steel beam fixed along the top of the wall and with the bottoms of the doors running in a metal recessed track set into the floor slab, and which open to reveal a jet exhaust efflux structure behind.

Jet Efflux Structure

The jet exhaust efflux structure at the back of each Shelter is constructed in reinforced concrete and was built integral with the reinforced concrete rear wall. Its original purpose was to direct and safely vent the jet exhaust of an aircraft with its engines running inside the protection of the Shelter, for it then to be able to taxi out under its own power.

There appears to be at least 2 No. basic variants of efflux structures provided across RAF Lakenheath. Most of the efflux structures appear to consist of an enclosed efflux tunnel leading to open-topped side vent openings plus a varying width gap along the top, all of which is open to the elements. There is then a short distance to a symmetrical wedge-shaped jet-blast rear splitter wall plus an additional generator room at the back, all in reinforced concrete and extending back about 12m in total from the rear wall (except for one example – PAS 6058 – which has a smaller generator room resulting in a reduced overall length of about 9m).

The open-topped sections of the efflux structure are exposed to the elements and so allow rainwater to collect inside the tunnel which is also subject to freeze/thaw effects. The base slab has therefore been sloped and shaped to lead to a drainage outlet in the base of each return wall inside each side vent structure.

Other variants of efflux structures appear to incorporate the same basic features but are shaped differently.

Shelter Floor Slab

It is assumed that the original floor slab inside the Shelter was constructed as essentially a continuation of the airfield pavement immediately outside the Shelter, being laid in bays as unreinforced Pavement Quality Concrete (PQC) and separated by movement/contraction joints with some filled with joint sealant. Such floors were usually finished with a light brush texture finish to prevent slipping. The slab would be capable of supporting all anticipated aircraft wheel loads and/or jacking loads plus the weights of other support equipment.

The floor slabs in PAS 6050 to 6059 (not including 6057) have all been painted with a textured finish plus additional markings for the accurate positioning of aircraft and equipment. The floor movement joints have been continued and exposed through the paint finish.

Internal drainage was originally provided by 2 No. floor gullies, one on each side of the PAS and positioned at about mid-length, but which now appear to be mostly redundant. The floor slabs appear to have been gently sloped towards these outlets.

Building Survey Information

All of the above information is based on available record drawings and on non-intrusive visual surveys and shall be validated by the Contractor who shall undertake his own intrusive and non-intrusive structural investigations as necessary to complete his design and to ensure that the stability of the building is preserved at all stages, in part and in whole, and will not be adversely affected by the Works.

Although it is not envisaged that the contractor will need to undertake intrusive structural investigations to complete his design, if such a need is identified by the Contractor then the scope and details of any such intrusive work shall be costed and agreed beforehand with the Project Manager as a compensation event.

The Contractor shall take the results of all his structural investigations, surveys and inspections and prepare a fully comprehensive and detailed Proposed Schedule of Works for agreement with the Project Manager, including the results of any testing undertaken, photographs of work to be done, and the Contractor must also prepare marked up scaled drawings of each building (PAS). All testing must be offered to the Project Manager and Site Supervisor for witnessing.

For concrete repairs, the Proposed Schedule of Works shall be prepared in accordance with the principles and descriptions used in the Concrete Repair Association – Standard Method of Measurement for Concrete Repair, Third Edition 2015, where appropriate and applicable.

The agreed Schedule of Works shall then form the basis of a continuously updated record for project management and cost control purposes and shall form part of the documentation included in the Health and Safety File with completion photographs and record drawings identifying the works undertaken.

Scope of Proposed Structural Works

Since all the PAS buildings inspected are essentially identical in form and function, were built about the same time and all appear to be currently utilised in approximately the same way, they all tend to exhibit the same patterns of defects (but to varying degrees).

The following specification requirements are therefore given as overall descriptions of the proposed structural work required.

The proposed structural alterations and repair works shall consist of the following main areas of structural work:

Undertake structural investigations of the existing building including non-intrusive and any intrusive surveys, testing as required for the Contractor to complete the design of the Works, and prepare a Proposed Schedule of Works for agreement with the Project Manager, including photographs and marked up scaled drawings of building (PAS) plans and elevations.

Replacement of roller bearing running gear, door track and ground beam supporting the main door panels of each PAS, reprovision as necessary of the rack and pinion operating beams and teeth fitted on the back face of each main door (to be coordinated with the new door motors).

Taking up and renewing the existing painted floor surface inside each PAS including the reprovision of all appropriate aircraft wheel markings etc. and provision of a hatching warning area at the front doors, and also including the permanent infilling and sealing of the existing floor gullies which are considered to be redundant.

Cleaning off and coating the inside surfaces of the roof arch inside each PAS, and coating with a white-coloured anti-corrosion and anti-condensation product which is also washable.

Making good the corroded steel plating on the inside face of the back wall of each PAS, and repainting with the same anti-corrosion and anti-condensation coating as described above.

Making good and recoating both sides of the bi-parting efflux doors at the rear of each PAS with the same anti-corrosion and anti-condensation coating described above, including replacement of the running gear and repair/refurbishment/coating of the running beam along the top of the bi-parting efflux doors, plus repair/refurbishment/painting of the door track set into the floor slab.

Making good and recoating both sides of the existing personnel entry door with the same anti-corrosion and anti-condensation coating described above (colour to be agreed with Base) and recoating the concrete surround to the doorway on the inside of the PAS.

Reshaping the end of the efflux tunnel by removal of damaged concrete and cutting back all around the end of the tunnel, including cleaning off the black staining from the concrete walls inside the Efflux tunnel.

Concrete patch repairs/remediation to the efflux splitter back wall and surrounding areas, plus reshaping/cutting-back of more heavily damaged areas, followed by application of a proprietary heat-resistant coating to all concrete surfaces (including all necessary surface preparation required beforehand).

External concrete patch repairs to the outside surface of the main roof arch.

External cleaning off and repair to the transformer room concrete structure at the end of each efflux tunnel and cleaning out of all roof drainage details, including resealing of joints etc.

- Additional optional areas of structural repair work shall consist of the following:

Preparation and coating of the outside surfaces of the main roof arch and all other external wall surfaces with an elastomeric coating system.

Fitting of new underwing lights to be set into the concrete floor slab of each PAS, including coring out of the floor slab for individual light fittings, and the routing of all new cabling via enlarged and extended existing bay joints in accordance with DIO Functional Standard 06 or by an alternative agreed means that shall still preserve the structural integrity of the floor slab and its bay layout.

The trial installation of a more extensive replacement of the surface of the efflux back wall on one of the first batch of PASs, using a proprietary heat-resistant concrete.

Detailed Scope of Proposed Structural Works

Shelter Main Doors

The Works shall include, but not be limited to, the temporary repositioning of the main doors of each PAS, the design, breaking out and construction of a new door ground beam and door track under the doors themselves, and replacement roller bearing carriages etc.

The existing roller bearing carriages and associated brushes are to be replaced on a like for like basis and shall incorporate whatever modern new materials, new bearings, new and wherever possible reduced maintenance and lubrication details which are both suitable and beneficial.

The existing main door track and ground beam including steel I section is all to be taken up, removed and replaced with a new door track of an equivalent design to the existing construction. However, in response to a recognised weakness in the existing design, the overall door track and ground beam design shall be modified to include a thicker steel top plate (at least 30% thicker) and provision of new countersunk set screw fixings of larger diameter and at half the existing spacing dimension along the length of each beam, i.e. provide twice as many fixings as existing. The steel top plate shall be corrosion resistant as existing and compatible with the steelwork and concrete to avoid galvanic action between dissimilar metals.

It is envisaged that the replacement reinforced concrete ground beam containing the new main door track shall also be doweled into the front edge of the existing floor slab so as to prevent the possibility of differential settlement across the PAS threshold and any resulting impedance to the aircraft wheels. Similarly, the thickened door track plating referred to above is to be incorporated into a revised/lowered I-beam detail so as to produce a flush top surface across the PAS threshold as existing, and then resetting and relevelling the doors back in place.

The replacement roller bearing running gear shall include for possible shimming and adjustment as necessary for relevelling the doors both now and in the future, and for ease of access for periodic maintenance of the rollers and bearings etc., including but not limited to such work as lubrication, adjustment, repair and/or eventual replacement. The replacement roller bearing running gear shall be based as far as possible on the assumption of a minimal maintenance regime.

The door rail track shall be open-ended and provided with adequate drainage to either new soakaways or to existing surface water drainage where already present and shall be designed on the basis of a minimal maintenance requirement where any blockages can be readily cleared away but there will be no significant collection of water in the event of blockages.

Strong points shall also be constructed at both ends of each door track to allow the doors to be opened (and closed) by a tow truck using cable hawsers, in the event of the door opening/closing mechanism failing.

The outer door carriages positioned under the external steel support work carrying the counterbalance concrete blocks are subject to lesser loadings and so may remain as roller bearings running on surface-fixed steel plating, all as existing. All such existing roller bearings, their carriages and all steel plate running surfaces shall be renewed and replaced.

The exposed structural steel support framing on the main doors shall be repaired and repainted. Where poor detailing has resulted in water-traps in the steel frameworks, then new additional drain holes shall be provided with all corrosion removed, by blasting or other suitable method and the steelwork made good before recoating.

All areas of concrete spalling on the outside faces of the doors shall be repaired to BS EN 1504 with a suitable concrete repair material. All such repairs and all the other externally-exposed steel/concrete interfaces where structural steel members have been cast directly into the concrete faces of the main doors shall be cut back with a narrow and shallow isolation slot to isolate the outside edges of the steel members from the adjacent concrete and so help to prevent the re-occurrence of such spalling, and all such slots shall be filled with a ASTM C443 flexible joint sealant or similar approved sealant.

All areas of damage to the external flashings, edge trim, door brushes etc. around the main doors and roof arch shall be replaced with material of the same type and colour.

The horizontal steel beams fixed behind the main doors and carrying the rack and pinion teeth on their undersides shall be repaired or replaced as necessary and drainage holes provided in the centre of every section along each beam.

The steel plating on the rear face of each main door shall be made good and repaired as necessary, and all surfaces recoated with anti-corrosion and anti-condensation coating as elsewhere. (Note: It is not required for the existing squadron decorations on the rear faces of the doors, where present, to be retained or protected, but are to be coated over. 48 CES will arrange for the Base historian to take photos.)

Shelter Floor Slab

The existing floor paint shall be taken up and replaced with a new matt (not gloss) textured epoxy-coated surface which is rated to Class 1 of BS 476 for surface spread of flame and shall be resistant to oils, lubricants and fuels, including the reprovision of all necessary floor markings for the correct positioning of aircraft and equipment. All coating colour schemes and markings shall be confirmed with the Base, but should be the same markings and dimensions as the existing except where the winch is removed.

Warning areas shall be painted on the floor slab in the area of the main doors for persons to keep clear during opening or closing of the doors.

Existing movement joints shall be preserved through the new coated finish as at present. All damage to the slab joints, either pre-existing or incurred during the removal of the existing painted floor finish or subsequently shall be repaired. All joints shall be resealed.

The determination of an acceptable applied texture providing a balance between surface friction, surface maintainability and long-term performance/durability as obtained from the addition of grit to the wet floor coating shall be decided based on-site trial floor areas (allow for 50m2) with differing grit contents, for agreement with Base.

It is understood that the existing floor gullies were deliberately filled sometime in the past to prevent any fuel spillages reaching the stormwater disposal system and perhaps leading to ground contamination issues. These gullies shall therefore have their gratings removed, be thoroughly cleaned out and then be permanently infilled and smoothed over with a concrete repair material and coated.

The concrete plinth for the existing aircraft winch shall be carefully removed and the concrete slab surface made good and coated, together with the removal/infilling around of any associated pulley fastenings present in the floor slab.

Inside of Shelter Roof Arch

Internally, the water staining and presumed ground equipment exhaust deposits present on the corrugated steel inner lining of the roof arch shall be thoroughly cleaned off by a non-abrasive method (such as water-jetting NOT metallic media blasting) that does not damage the steel lining or its original galvanised coating or generate large amounts of airborne dust or particles, for the steelwork to then be primed and coated with a smooth, glossy, white-coloured, anti-corrosion and anti-condensation coating which will adhere to the galvanised surfaces and which is rated to Class 1 of BS 476 for surface spread of flame, which would also help increase ambient lighting levels for persons working inside the PAS buildings, and which is also washable and readily maintainable/overcoated. Any such coating should also preferably be water-based and odourless, with a low VOC content.

Depending on the actual nature and chemical composition of the surface deposits present inside the arch and on the back wall, and thought at present to mostly contain compounds such as carbon particulates and unburned hydrocarbons etc. from various exhaust emissions over an extended period of time, the Contractor shall initially determine the actual nature of these deposits and confirm to the Project Manager whether these deposits represent an environmental health hazard requiring special containment, treatment and protective measures during the cleaning and shall also arrange for their subsequent safe collection, removal and disposal as appropriate for the level of contamination present; for the purposes of Tender assume it is contaminated waste.

All existing plant and equipment that is identified to be retained in place inside the PAS shall be thoroughly protected against damage and water, dust or paint ingress during all aspects of the works inside the PAS, including works to the floor slab, and shall be retained in place until completion.

It is also required that all redundant low-level service entry ports/ducts/pipes passing through the shelter arch structure shall be broken out and the areas reinstated in concrete, unless these service entries are considered to be so substantial that their removal is considered impractical and could lead to excessive damage, in which case they shall be cut back and externally covered by thick welded steel capping plates.

Inside of Rear Wall of Shelter

The corrosion observed along the bottom of most of the steel anti-spall plating on the back wall of each PAS shall be cut back to sound material along a straight level line approximately 150mm above the existing concrete edging all along the bottom of the rear wall of the Shelter, and the exposed concrete cleaned of all debris and staining. The line of freshly-cut metal shall then be protected against corrosion.

The remainder of the steel plating shall then be cleaned off by a non-abrasive method as described above, all residues collected and removed, and all surfaces primed and coated with the same anti-corrosion and anti-condensation coating as described above.

Efflux Doors

The bi-parting, sliding, steel efflux doors shall be rehung, with replacement rollers fitted and alterations made to the high-level beam as necessary to ensure ease of operation for the doors to be opened and closed manually. The doors themselves and all exposed steelwork members and fittings shall be repaired or replaced as appropriate, and recoated with the same anti-corrosion and anti-condensation coating as described above.

Particular attention shall be given to the condition and provision of steel shims or washers to the supporting steelwork and their replacement with suitable fittings to prevent movement and to resist vibration (refer to DIO Safety Alert, Part A, Number: SA 2018/01, date of issue: 27 February 2018; Subject: Inspection and Maintenance of Efflux doors to Hardened Aircraft Shelters (HAS)).

Make good all corrosion to the existing door track set into the floor slab and apply a new protective coating for the full length of the track and adjacent concrete.

Personnel Entry Door and Doorway

The existing steel personnel entry door shall be suitably cleaned off, rubbed down by mechanical means and recoated, and all door ironmongery (including door handles and hinges etc.) cleaned off, lubricated and recoated with the same anti-corrosion and anti-condensation coating as described above (colour to be agreed with Base).

Efflux Tunnel

It is not proposed to repair the efflux tunnel to try to recreate the same original 1981/82 concrete profiles and edges which have helped to concentrate the damaging effects seen in practice and which have so far proved incapable of satisfactory repair to resist repeated and ongoing damage.

Instead, the existing reinforced concrete efflux structure shall be reshaped into a more resilient form, as suggested by the pattern of damage observed. This work shall apply equally to all PAS efflux structures, whether the walls and roofs are damaged or not at this time.

To do this, an approximately 300mm continuous strip of reinforced concrete shall be carefully removed from the ends of both side walls and from the end of the roof slab, all around the above-slab profile of the end of each efflux tunnel, in order to remove all damaged material and cut back to sound concrete (size and depth of strip to be increased as necessary to achieve sound material all around the ends of the efflux tunnel walls and roof slab of each PAS, to be confirmed on a case-by-case basis), while also increasing the available clear space available for the dissipation of efflux gases in service.

Preference shall be given to concrete cutting methods which produce clean, defined and accurate cut lines with no additional damage, spalling or cracking being caused in the remaining existing walls and roof slab. The resulting exposed cut ends of all reinforcing bars shall be treated and protected against corrosion using a high-build protective coating which is also heat-resistant.

The black staining present on the inside faces and underside of the roof slab of the efflux tunnel is to be thoroughly removed back to clean concrete.

The existing blast and heat erosion damage to the raised edges of the ground floor slab shall be rounded off by careful scabbling and grinding off to a regular smooth surface and not repaired further.

Other cracking, spalling, delamination and other damage in the floor slabs in the return ends of the efflux tunnel and wing walls shall be repaired using appropriate specialist concrete repair materials.

Once repaired, all exposed concrete surfaces that will be subject to jet efflux gases (including inside the efflux tunnel and the efflux back wall) shall have an application of a heat-resistant sodium potassium aluminium silicate-based concrete surface sealer such as Thermopel CS100 or equivalent.

Efflux Back Wall

The original extent of the top corner of the central wedge of the efflux rear splitter wall created a ‘pinch-point’ with a minimum gap of only about 150mm where it was closest to the original leading edge of the efflux tunnel roof and so has noticeably suffered some of the worst damage. In a number of cases, this top corner has either been completely lost or is at least extensively cracked and/or spalled.

For all PAS efflux structures, whether these features are damaged or not at this time, the top corner of the central wedge shall be carefully cut back at an angle of about 45 degrees and ground off as necessary to create a regular smooth profile to create the maximum possible gap at this point (including the minimum 300mm strip of roof slab to be removed as described above).

For certain areas of the central leading edge of the rear splitter wall where there is extensive loss of material and/or cracking, and in the absence of a proven long-term, large-scale repair material that can resist the extreme conditions inside the efflux at this point, the vertical central leading edge is to be carefully ground back to a regular smooth rounded surface, removing all damaged, loose or cracked material.

For other areas of damage, these shall be repaired by careful scabbling to remove all loose and/or cracked material and reinstated with a specialist heat-resistant concrete repair material where appropriate.

The existing rainwater outlets in the existing return walls shall be cleared out and repaired/improved as necessary, to discharge outside as at present, and to prevent ponding inside the efflux structure (including replacement of delaminated or lost floor finishes as described above).

Upon completion of all necessary repairs and whatever additional surface preparation may be required, the whole of the efflux back wall shall be treated with a specialist heat-resistant coating material such as Thermopel CS100 or equivalent.

The proposed coating material shall adhere to the existing underlying Portland cement-based concrete structure (following whatever repairs and surface preparation are required and also following the application of whatever primer and/or bonding agent is required as part of the coating system) and be resistant to the following imposed conditions (based on the F-15E aircraft):

- Maximum jet engine operational rating up to about 80% MIL Power.

- Maximum applied jet exhaust temperature up to about 300OF (150OC).

- Maximum applied jet exhaust velocity applied at surface of concrete up to about 350MPH.

- Maximum engine operational duration up to 1 hour (under varying engine power).

- Minimum distance from end of aircraft jet pipe to nearest part of reinforced concrete efflux end wall about 18m.

- Surfaces will be exposed to the elements so heat-resistant coating material to be able to perform immediately from surface water-saturated condition.

- Surfaces will be exposed to the elements so heat-resistant coating material to be able to perform immediately from surface-frozen condition.

- Surfaces will be exposed to the elements so heat-resistant coating to be able to resist normal freeze-thaw effects.

- Surfaces will be exposed to the elements so heat-resistant coating to be able to resist normal thermal expansion-contraction effects without delamination from the underlying original concrete, as well as resisting delamination under extreme heat-expansion effects.

- Because of the confined nature of the efflux tunnel shape, it is anticipated that there is also a significant but unquantified amount of concentrated reverberation and acoustic shock waves generated inside the efflux structure and reflected between the various efflux wall surfaces, which could cause delamination and/or disintegration of any applied coating. These effects must also be resisted.

- Material to be capable of having eroded coatings directly reapplied/overcoated/renewed with more of the same material as appropriate.

Trial Installation

As a long-term trial installation, one PAS shall be identified by the Project Manager and Base to have a more extensive repair undertaken on its efflux back wall. This will require the complete removal of the front face of concrete for the full height and width of both faces of the efflux back wall, to be continued behind the front layer of reinforcement (which is to be retained intact) to an overall depth of removal not exceeding 100mm. The method of removal shall be based on high-pressure water jetting or similar that does not result in any residual damage to the remaining concrete.

The vertical wall surfaces shall then be recast behind shuttering to give a smooth outer surface using a specially-designed, heat-resistant, refractory-type concrete mix that shall also be self-compacting for careful placement by tremie pipe from above into the formwork avoiding discharge from height, segregation or honeycombing.

Bearing in mind the relatively small quantity of material required for the proposed trial area, the special concrete shall be based on the use of a dry, pre-mixed, pre-bagged specialist material enabling a calcium aluminate concrete to be made with an extremely high performance, such as FONDAG E by Kerneos (or equivalent).

Alternatively, a trial concrete shall be used which is compliant with the DIO Specification for High Temperature Resistant Concrete, November 2015, prepared by AECOM for the Defence Infrastructure Organisation on the F35B Lightning II programme and based on United Facilities Guide Specification UFGS-32 13 13.43, “High Temperature Concrete for Airfields with Applied Pavement Temperatures of 482OC or Higher, Using Lightweight and Traprock Aggregates”, March 2014.

Patch Repairs to Outside of Roof Arch

External repair work shall be undertaken to locations where there is concrete spalling, holes or other intrusive damage to the surface of the concrete, using an appropriate specialist concrete repair material, including areas of impact damage at the low level external door stops.

NOTE: The cracks observed at low level and on both sides of the barrel vault roof are thought to be minor shrinkage cracks and as such are not considered to be structurally significant or requiring repair. The efflorescence observed seeping from these cracks is thought to be caused by rainwater permeating the concrete of the vault structure and exiting via these low-level cracks.

Coating Outside of Shelter – Option

A flexible, waterproof, elastomeric coating system shall be applied to the external surfaces of the barrel vault roof (plus all the other external wall areas as well) in order to prevent continued water penetration into the concrete and thus stop further external deterioration and prevent ongoing internal water penetration and salt staining inside the PAS buildings.

The proposed coating system shall also be vapour permeable so that water can be allowed to be released over time and not remain locked between the impermeable barrier of the inner steel lining on the inside and the proposed new coating system on the outside.

The coating shall be flexible and capable of bridging over the minor cracks observed and be able to accommodate any future expansion or contraction of these and any other cracks as may appear.

The proposed coating system therefore shall include, but not be limited to, the following properties:

- System life of at least 15 years, resistant to UV degradation and weathering.

- Elastomeric properties, able to tolerate thermal and limited substrate movement.

- Flexible and able to bridge over non-moving existing shrinkage cracks not more than about 1mm wide.

- Spray-on, brush or roller application (not sheet materials) to provide a seamless membrane.

- System to be vapour-permeable.

- Coloured finish (colour/shade to be agreed with Base).

- Coating to have a smooth finish to discourage moss growth, with a dull, flat appearance (not shiny but not matt either).

- Readily repairable, allowing localised reapplication to damaged areas.

- Capable of being applied to damp (but not wet) concrete substrates.

- CE-marked in accordance with BS EN 1504 Part 2.

Successful application of any such coating, including all primer coats, shall demand the thorough preparation of the concrete substrate in full accordance of the coating manufacturer’s recommendations, probably involving such methods as wet grit or water blasting the concrete surface to remove all dust, dirt, debris, oil, mould, previous coatings, efflorescence and any loose material or other organic growth or deposits, followed by patch repairs to the concrete where necessary. Application shall then be undertaken by specialist subcontractors licensed, approved or trained by the system manufacturer. The works shall include the provision of all means of safe access necessary to reach all parts of each Shelter, as well as the collection, removal and safe disposal of all arisings.

External wall areas which are particularly exposed to hot efflux gases which could burn or blister any applied coatings shall be identified and confirmed for agreement with the Project Manager for possible omission.

Transformer Room

The existing transformer room structure at the rear of the efflux tunnel has been observed to have plant growth on the roof and water leakage down the outside walls in some cases. All such plant growth shall be removed and cleaned off. The source of the observed water leakage shall be determined and any blockages or other similar causes shall be remedied, including concrete repairs and resealing of all joints etc. as necessary.

Underwing Lighting – Option

- The fitting of new underwing lights, including coring out of the PAS floor slab for individual light fittings, and the enlargement and extension of existing bay joints for new cabling shall be undertaken to a suitable aircraft pavement design and detailed arrangement to suit the F-15E aircraft.

- As a minimum, cable slots to serve the new pavement lighting shall be provided in accordance with Defence Works Functional Standard 06 “Guide to Airfield Pavement Maintenance”, Section 4.13 “Service Trenches and Cable Slots”.

- Alternatively, if appropriate, an arrangement similar to that currently employed for the installation of similar underwing lighting in the existing Wash Rack at RAF Lakenheath, Building 1229 may be used.

- All such works shall not compromise the structural performance of the existing concrete pavement slab, or induce uncontrolled additional cracking of the pavement.

- All joints and cable slots shall be sealed in accordance with Defence Works Functional Standard 06.

Design Standards

Structural design standards to be referenced include, but are not limited to:

The complete suite of Eurocode Documentation including, as appropriate:

BS-EN 1990 – Basis of Design

BS-EN 1991 – Actions on structures

BS-EN 1992 – Design of concrete structures

BS-EN 1993 – Design of steel structures

BS-EN 1997 – Geotechnical design

UFC 3-270-01 – O&M Manual: Asphalt and Concrete Pavement Maintenance and Repair

BS EN 1504 – Protection and Repair of Reinforced Concrete

Contractor to prepare surfaces & apply protective coatings and paints in accordance with;

UFC 3-190-06 (2004) – Protective Coatings and Paints

Paint System Manufacturer Guidance & Recommendations

British Standards (B.S) requirements.

COSHH/MSDS and coating system product details/application records will be required by base corrosion engineer as part of the final O&M manual submission.

Design Life

All new permanent structural elements (such as the new ground beam for the main doors) shall be designed for a life of 50 years.

All new applied coatings shall be designed for a minimum life of 15 years to first maintenance.

Health and Safety

The design will be carried out in accordance with the requirements of the CDM Regulations.  All health and safety points that require action will be addressed by the design team.

Deflections

Deflections along the new ground beam supporting the new door track, new running gear and modified existing main doors shall be limited so as not to impede the operation of the main doors when opening or closing.

Furthermore, deflections and rotations along the new ground beam shall also be limited so as to ensure that sufficient clearance is always maintained between the rear face of the main doors and the leading edge of the PAS roof arch, eliminating the existing problem of doors scraping against the roof arch.

Coordination with services

The structural works shall be fully co-ordinated with all building services as necessary.

Exposure conditions

The structural works shall be designed for suitable exposure conditions.

Fire Engineering

The required fire resistance of structural elements, materials and coatings shall be provided in accordance with the Fire Engineering and Architectural requirements of this Works Information.

Construction Tolerances

Maximum permissible construction tolerances of the various structural elements shall be in accordance with the operational requirements of the main doors of each PAS. In particular, a flush threshold shall also be maintained at the front of each PAS where the new ground beams and door track are to be constructed, to allow the smooth operation of aircraft entering and leaving the PAS, and incorporating dowel bars in the ground beams as necessary to achieve this.

Loading

Dead, imposed and wind loading shall be obtained from the most onerous of the standards given above.

Stability

The Works shall not adversely affect the overall building strength or stability, or the strength or stability of individual elements of the PAS buildings. The Contractor shall carry out their own intrusive and non-intrusive surveys and carry out additional investigations as necessary to determine how the required structural works can be undertaken.

Substructure

The new ground beam for the main doors shall be ground-bearing but shall be so designed and detailed that there shall be no significant differential settlement, movement, deflection or rotation of the ground beam relative to the existing building. The ground beam shall penetrate to a minimum depth of 300mm into the loadbearing stratum and shall also be designed for all door loads and crossing by aircraft wheel loads etc.

The Contractor shall undertake whatever additional ground investigation work is necessary to determine the design of the new ground beam.

Mechanical Specification

General

The General and Technical Requirements for the mechanical services installations shall comply with the documents listed in the Works Information and in particular, but not limited to, those listed below.

CIBSE guides, technical memoranda, commissioning codes, applications manuals

The Building Regulations (Fire Regulations)

Defence Infrastructure Fire Standards

All relevant DE, US and USAF standards, regulations and requirements

DIO (DE) Specifications 034, 036, 037 and 047.

Defence Maintenance Guide 08

Defence Maintenance Guide 22

UFC 3-400-02	Design: Weather Data

UFC 3-401-01	Mechanical Engineering

UFC 3-410-01 	Heating, ventilation, and Air Conditioning Systems

UFC 3-450-01	Noise and Vibration Control

BISRA Guidance

The Contractor shall:

Provide all materials and works in accordance with the appropriate British Standard (BS) or Code of Practice (CP) and where no BS or CP is applicable the Agreement Certificate for the particular item.

Comply with the relevant Unified Facilities Criteria (UFCs) and Engineering Technical Letters (ETLs)

Comply with all Statutory Instruments and regulations, relating to the area of the site current at the date of tender.

Address any compliance issues with DIO Building Control Officer.

Comply with the requirements of the DIO Standard Specification 036 and 037.

The Contractor shall comply with all statutory obligations arising from current legislation and regulations, together with other requirements, including but not limited to, those listed in this document

All plant shall be accessible for maintenance and routine cleaning by staff without the necessity for specialist access equipment in accordance with, but not limited to the requirements of DE Design and Maintenance Guide 08.

The Contractor shall notify all authorities in accordance with their regulations and obtain any required approvals for the installation.

Where no specific design, performance or installation standards are quoted the following shall apply:

The Contractor shall ensure that all equipment and systems are designed and installed in accordance with the relevant standards and that operational compatibility exists between the systems and any other system installed at the same location.

Where different or conflicting standards are detailed, the most onerous shall apply.  Where particular standards are mentioned the Contractor’s attention is particularly drawn to these standards but all other relevant standards shall be adhered to.

The Contractor shall comply with the requirements of the RAF Lakenheath Base Facility Standard, also referred to as Base Standards and all supplements current at the time of tender.  Where the Base Standards, DIO documents, etc., refer to a preference, recommendation or similar these preferences, recommendations or similar shall be the requirements for this project.

All works detailed by this specification, accompanying drawings, documents specifically referenced or covered by applicable general standards shall be carried out by the Contractor, unless it is specifically stated that the works shall be carried out by “others”.

Scope of Works

General

The scope of the Works covers the provision for the refurbishment of the accommodation within the PAS along with modifications, amendments and renewal of mechanical and electrical services in the building. All building work shall be as indicated on the drawings and specifications associated with all works.

Unless specifically stated all clauses refer to all parts of the Works.

The mechanical services for PAS shall include, but not be limited to, the following:

Wholesale replacement of mechanical equipment

Refurbishment of associated ventilation services

Installation and Replacement of supply and extract fans

Filling in of existing ground drainage systems

Automatic Meter Reading System (AMRS)

Commissioning and setting to work of all systems installed

Working Drawings and Builders Work Drawings

Provision of As Installed Drawings and Operating & Maintenance Manuals.

Provision of Building Log Books

Weatherproofing

Where mechanical services pass through walls, foundations and roofs, the Contractor shall weatherproof the aperture around them to a standard not less than that provided by the building fabric penetrated.

Handover

The Contractor shall provide all documentation required for handover including but not limited to the information required by the following:

DE USF Tech 012

DD1354

Asset register in Uniformat 2 level 4

Additionally, the Contractor shall develop Building Log books in accordance with, but not limited to, the following:

CIBSE TM31 revised 2006

CIBSE TM31 Main Template

Fire Strategy

The Fire Strategy document shall be a separate document submitted at each design stage in accordance with the requirements of Appendix E of this Works Information.

The Contractor shall incorporate all necessary mechanical information relating to Fire Strategy document. The following in particular, but not exclusively, shall be considered, in accordance with the Defence Infrastructure Fire Standards when assessing interfaces with Emergency Lighting and ancillary services:

Designation of primary escape routes, etc., in all areas

Spares and Tools

The Contractor shall provide details of all spare parts and a schedule of spares as required by the Works Information.

In order to enable maintenance work to be carried out, two sets of all specialist tools shall be provided as required by Section 4.2.5.

Specialist tools shall be all tools specially provided by the manufacture specific to their plant, equipment and accessories.

Energy for Testing

The Contractor shall provide all equipment for testing and commissioning of the plant.

The Contractor shall supply and install the relevant check meters for the purposes of measuring energy used during the testing period.

All meters shall be read prior to and on completion of testing.

Maintenance Access

It shall be ensured that all new plant is accessible for maintenance and routine cleaning without the necessity for specialist access equipment in accordance with, but not limited to, the requirements of DE Design and Maintenance Guide 08 (DMG08).

Mounting Heights

Accessory and equipment mounting heights shall be installed to comply with the most onerous of following standards: DE Standard Specification 036, 037, DMG08 and the Defence Infrastructure Fire Standards.

Insurance Inspections

The Contractor shall provide initial insurance inspection reports and new or revised written schemes of examination using CES/DIO nominated inspector/competent persons (currently Ashdale engineering).

Any lifting beams, eyes, hoists, etc. shall also require initial inspection and certification by the base nominated surveyor prior to completion. (currently Ashdale Engineering).

Demolitions and Strip Out

The existing mechanical services shall be removed in their entirety.

Mechanical Services Installations to PAS

The Contractor shall conform to UFC 3-410-01 Heating, Ventilating, and Air Conditioning Systems (Latest Revision). This shall include isometric ventilation drawings and the capacities. Fresh air volumes and return air percentages stated on all drawings and charts. Full mechanical selection sheets required for all equipment provided by the Contractor.

Heating

No heating shall be installed in the PAS.

Ventilation

Ventilation System

The Contractor shall design and install the ventilation system within the PAS to meet the requirements of Contractor’s DSEAR assessment, DIFS and DMG08.

The supply fan shall be EX-rated and bifurcated in design and incorporate filters on the intake and shall provide 100% fresh air. No heating is required within the building.

The extract fan shall be EX-rated and bifurcated in design and incorporate course mesh filters to protect the fan from any debris. Extraction filters should not have the ability to absorb fuel vapour from the extract air. Attenuators should not be installed.

All new fans shall be of a variable speed type where possible to minimise energy consumption.

The existing supply and extract ductwork shall be replaced in its entirety. All existing external louvres and vermin and insect mesh grilles shall be replaced to meet the new requirements of the system.

The high-level swan neck ventilators shall be visually inspected and retained to provide assistive natural ventilation and make up air for the mechanical ventilation. Vermin and insect mesh to be installed. Any swan neck ventilators with excessive corrosion shall be replaced or made good.

Supply and extract grilles shall be positioned evenly along the length of the ductwork. Volume control dampers (VCD) shall be installed within the ductwork so the airflow can be balanced and provide even air distribution across the entire length of the ductwork.

The control of the ventilation system shall be via a motor control panel (MCP) capable of providing the following methods of operation:

ALL OFF – supply and extract fans off

Extract only ON FULL – Extract fan on at 100% duty, supply fan off

Extract only ON VARIABLE – Extract fan set with variable speed controller. Supply fan off

Supply & Extract ON FULL – Supply and extract at 100% duty.

Supply & Extract ON VARIABLE – supply and extract linked to variable speed controller. The minimum turndown of the supply and extract fan shall be confirmed and established by the manufacturer. The extract rate shall always be that or higher than the supply.

All new ductwork systems shall be pressure tested to confirm their integrity and suitability for use prior to connection of plant items, as detailed in the HVAC DW144 section A.5.

Final connections from the rigid ductwork to grille boxes shall be in spiral wound flexible ductwork.

Ductwork shall be aluminium clad as required by DIO Specification 037. In particular, ductwork shall be protected to prevent mechanical damage by enclosing within 1.0mm thick aluminium sheet or 0.8mm thick galvanised mild steel sheet and not painted.

The Contractor shall ensure that the new duct system remains protected during the installation period and prior to commissioning. The Contractor shall take specialist advice and specify the requirements for the periodic cleaning/maintenance of the ductwork and the consequent need for adequate access for specialist cleaning equipment and the size / type / location / frequency of actual access openings that are required in the ductwork together with stipulating the cleaning of the installation prior to commissioning and handover to the base. The cleansing requirements for both the new and existing elements of the proposed ventilation systems are set out in the HVCA publication DW144, Specification for Sheet Metal Ductwork and the HVAC publication TR19, Guide to Good Practice, Internal Cleanliness of Ventilating Systems.

Above Ground Drainage

The existing drainage within the PAS is no longer required so shall be filled and levelled with the existing finish floor level.

Fire Alarms

48 CES have confirmed flame detection and fire alarms are not required in the PAS.

Commissioning of all HVAC Installations

All installations shall be cleaned, fully set to work, commissioned and proportionally balanced in accordance with industry standard procedures e.g. CIBSE Commissioning Codes and DE Standard Specifications.

All commissioning shall be demonstrated to and witnessed by the Project Manager’s Representative and, where specifically required, by the Clients/Users Representative.

A stated sequence of operation is required by the Contractors design team as stated for ventilation above and should be reflected in the Measurement and Verification (M&V) plan. This shall be provided at each stage of the development from 65% until completion.

Training

The Contractor shall allow for a comprehensive training exercise to teach the End User and Facility Management in the understanding and operation of the Control Panel.

Maintenance Access

It shall be ensured that any fans, filters and   grilles are accessible for maintenance and routine cleaning without the necessity for specialist access equipment in accordance with, but not limited to, the requirements of DE Design and Maintenance Guide 08 (DMG 08). It shall also be ensured all new equipment does not restrict access to existing equipment such that the requirements of DMG 08 for existing equipment would not be met. Alteration of existing access arrangements to existing equipment is outside the scope of these works however the Contractor shall notify the Employer of any such eventualities.

Where the location of any existing plant conflicts with the requirements of DMG 08 this shall not be addressed unless the equipment is to be replaced as part of these works.

Fans shall be provided with rotary style isolators capable of physical pad-locking off for routine maintenance. These electrical devices need to be indicated on the Contractor’s design drawings.

Electrical Specification

Building Usage and Design Parameters

General

The works shall be in accordance with the scope of works subsequently detailed and shall be carried out within the parameters detailed below:

There are detail differences between the Electrical Installations in each Protected Aircraft Shelter (PAS) as minor alterations/additions have been made over their life to various PASs.  Also, the configuration of the internal mains distribution depends on the location of the Distribution Sub Station from which the supply is derived and on which side it enters the PAS.

A preliminary DSEAR assessment for the PAS, which has fuelling and de-fuelling activities, in accordance with the requirements of UFC 4-211-01 clause 5-6.6.4 specifies a Class 1 (gas), Division 2 (Zone 2) throughout the whole PAS, and the weapons vault as Class 1 (gas), Division 1 (Zone 1).  It is requirement of any USAF base to use the most stringent equivalent standard of the UK and US regulations.

Except where subsequently detailed, the electrical installation of the PAS shall be of two standards:

With Floor Vault

Without Floor Vault

Otherwise the electrical functionality to be provided for the use of the End User shall be identical for all PASs.

Some PASs have had recent lighting upgrades to incorporate LED luminaires.  Where this has already be done this installation shall remain and shall be protected during the course of the works.  Where this work has not been done the Contractor shall replace the existing lighting with LED lighting to a similar standard, as subsequently detailed.

The Contractor’s attention is particularly drawn to the requirements of JSP 482: “Ministry of Defence explosives regulations for the safe storage and processing of ordnance, munitions and explosives (OME).”  The Contractor shall comply with all relative requirements of this document as established by him during his design process and accepted by the Project Manager at each stage of design

Operative Certification

All electrical operatives carrying out any installation work shall have Competency in Explosive atmospheres (CompEX) training and shall be certified by a UKAS ISO/IEC 17024 accredited company, J.T.L. Limited.

Testing and Commissioning

As subsequently detailed parts of the existing installation shall remain., e.g. existing Lighting and Existing NATO equipment.

The new works shall therefore be treated as an alteration or addition to an existing installation.

On commencement of the works the Contractor shall carry out Periodic Inspection and Testing of the completed lighting installation.

The Contractor shall also carry out Parodic testing of the NATO equipment circuits ONLY up to an agreed defined demarcation point.  The Contractor shall also measure the supply parameters at the NATO demarcation point so that he can ensure his re-wring works up to this point do no adversely affect the supply characteristic at this point.

Any defects found due to et above testing shall be reported to the Employer.

The new works shall be inspected and tested in accordance with requirements of BS7671 for Initial Verification and the additional requirements of the regulations listed below, including the existing lighting installation and new wiring up to the NATO equipment demarcation point.

Compliance with Regulations

For all aspects of the works the Contractor shall comply with the most onerous requirements of all relevant documents including but not limited to the following documents, for all aspects of the works

- BS 7671 Requirements for Electrical Installations, current edition.

- Joint Services Publication (JSP) 482

- Explosives Storage and Transport Committee (ESTC) Standard No. 6 Part 1 – Electrical

- The Contractor’s DSEAR assessment

- The Contractor’s Fire Strategy

- Unified Facility Code UFC 4-211-01 Aircraft Maintenance Hangars

The Contractor shall comply with the additional requirements of ESTC part 6 for the commissioning, testing and documentation of the electrical installation.  The works shall be a new installation and all testing required for initial verification shall be carried out by the Contractor at the completion of each PAS.

The Contractor shall also provide a log book for each PAS in accordance with ESTC Part 6.

Existing Infrastructure, Form 121, Permit to Dig, Permit to Work

For all services excavations, the Contractor shall consider all electrical and Telecommunications infrastructure connections.  The Contractor shall note and make due allowance for the existing situation in which PASs share common electrical supplies from a common Distribution Sub Station (DSS) Feeder Pillar circuit.

The Contractor shall ensure that all works carried out to the existing low voltage infrastructure services are planned and carried out in accordance with the requirements of JSP375, Volume 3, Chapter 3.  This shall include the certification of operatives working on these systems.

The Contractor shall note that the infrastructure indicated in the Site Information is for information only and the Contractor shall be responsible for ascertaining the location of all existing services on the site.

The Contractor shall ensure that all persons working on the electrical installation complete Defence Estates, United States Forces (DEUSF) Form 0121 (Skilled Person Electrical - Confirmation of Competence), which shall be used as part of this Project.  This requires that all persons working on an electrical installation at RAF Lakenheath shall be competent to do so and be issued with a Skilled Persons Certificate by the DEUSF Authorising Engineer/Authorised Person (AE/AP).  The completed form for all prospective nominees shall be forwarded to the (AE/AP) at RAF Lakenheath.  The Contractor shall note that it shall be necessary for all nominees to attend a meeting with the AP before they can be certified.

The Contactor shall note and make due allowance for the fact that an electrical supply to a building when energised from the site electrical infrastructure it is part of the site infrastructure and therefore comes under the jurisdiction of JSP 375 Volume 3, Chapter 3.  This includes, but is not limited to, working on the main Switchboard and the requirement for suitable labelling to be in place.  The demarcation point between the RAF Lakenheath Base infrastructure and the Contractor’s site electrical infrastructure shall generally be at the load terminals of the incoming main isolator.  However, the Contractor shall formulate a demarcation agreement with the AP to formalise this arrangement when any supply is de-energised, fuses pulled at local DSS, or re-energised.  Once the Contractor commences works within the PAS any pre-existing electrical certification will be invalidated and the Contractor shall re test, dead testing, the system to the satisfaction of the Project Manager and AP before any request for re-energisation is made.

Before any excavations are carried out on site, the Contractor shall obtain from the Base Civil Engineer a Form 103 Work Clearance Request also known as a “Digging Permit”.

The Contractor shall also contact British Telecom. (BT) “Dial before you Dig” 0800 917 3993 to ensure all BT plant on the Contractor’s site including his working area is identified by BT prior to works commencing.  This shall be done irrespective of any Telecoms. duct information shown on the Form AF103.

The Contractor shall also coordinate his external works with British Telecom.  The contact for British Telecom is:

Mr Tim Smith

tim@ts-network.co.uk

Tel 01638 713 116

It should be noted that there are unknown services on the site.  The Contractor shall therefore carry out a search of the site using services detection equipment, before any excavations are undertaken.

All excavations within 3000mm of existing services including BT ducts and chambers shall be hand dug.

The Contractor shall provide four weeks advance notice for all disconnections and re-connections.

All requests for permits to dig, permits to work, interruptions to existing services, etc shall be coordinated through the Project Manager as detailed by the Contract Preliminaries.

The Contractor shall note Authorised Person (AP) availability is included within “Normal Working Hours” as defined by the DIO/Interserve contract.

Where the Contractor requires any input from the AP/AE out of “Normal Working Hours” the Contractor shall pay all costs.

Where the Contractor requires AE/AP attendance out of “Normal Working Hours” due to USVF operational reasons then he shall notify the Project Manager and provide a copy of his request and subsequent rejection.

Sequence of Works

The buildings will be vacated completely by the Base prior to the commencement of each Construction phase of the Works. Therefore, the Contractor shall be responsible for making his own fire alarm arrangements.  The Contractor shall confirm these arrangements with the Employer prior to the commencement of the Works.

As subsequently detailed in Section D.2.1, PAS are grouped on common Low Voltage supplies from the local Distribution Sub Station.  Therefore, the sequence of works shall be coordinated with LV supply groupings so that the PASs on a common circuit are worked on together and the supply Fuse at the Feeder Pillar can be pulled to isolate the whole circuit.

Where this is not possible the Contractor shall provide a mobile temporary generator for each building on an LV distribution circuit which is to be isolated but is not included as part of these works or the phase of these works being carried out.  The temporary generators shall operate 24 hours per day, 7 days per week to ensure all alarm systems etc. in the buildings remain operational.  Where the temporary generator is required to supply a PAS the generator rating shall be suitable for the door motor load of the PAS as well as the PAS normal operating load.  Generators shall comply with EU emissions Stage IIIA standard for Non-Road Mobile Machinery (NRMM).  The generator shall be silenced to a minimum of 75dBa at 1m, super silenced.  Generators shall be fully bunded.  Bulk fuel tanks shall also be fully bended and all pipework between the generator and bulk tank shall be pipe in pipe and all connections shall be made within the generator and bulk fuel tank bunds.

A schedule of PAS supplies is provided within the Site Information, for information only at tender stage, all supply arrangement shall be confirmed with the RAF Lakenheath Electrical Approved Person during the Contractor’s design phase.

Operation and Maintenance Training

The Contractor shall provide operating instructions for all systems. This document shall include a description of all automatic controls the End User has no control over but affect the systems he uses.  This document shall be in a style and format that can be handed to new End User to allow them to understand the function of all systems in the PASs.

The Contractor shall provide detailed operating instructions to the End User and Facilities Maintenance in the operation of all systems, so that they can carry out system adjustments where these are accessible and explain clearly how systems operate.

The Contractor shall ensure all signage is in place before the instruction is carried out and that the information detailed by the signage is fully understood by all those instructed.

The Contractor shall include for the instruction of the End User and his staff in the operation of all systems. This instruction shall be based on the contents of the above documents. Where the instruction reveals that the documents need to be updated and / or corrected the Contractor shall carry out these amendments.

The Contractor shall submit copies of the End User and Facilities Maintenance manager’s document to the Employer before training commences on site.

Fire-Stopping and Weatherproofing

Where electrical services pass through walls, foundations and roofs, they shall be effectively fire-stopped and weatherproofed to a standard not less than that provided by the building fabric penetrated.  Fire stopping shall be carried out in accordance with the requirements of BS 476 Parts 20 and 22 and LPC Fire Test THE 92337.  Where fire stopping and/or weatherproofing is carried out, the control shall take into account and select materials that are appropriate to the potential atmosphere in the PAS and the potential effects of the fluids that may be present, e.g. Avtur, Oils, Hydraulic fluids, on any materials used.

The Contractor shall re-seal all existing penetrations where his works affect them, e.g. removal of redundancy Generator cables or Telecoms. cables.  Where the Contractor’s works do not affect existing firestopping or weatherproofing the Contractor shall test these penetrations in accordance with the manufacturer’s recommendations or where the manufacture cannot be established specialist testing organisation using a testing method agreed with the Project Manager and rectify any defect so that a re-test proves the integrity for the firestopping/ weatherproofing.

Fire Strategy

The Fire Strategy document shall be developed by the Contractor in accordance with the requirements of the Defence Infrastructure Fire Standards (DIFS), Chartered Institute of Buildings Services Engineers (CIBSE) Guide E “Fire Safety Engineering” and the additional requirements Unified Facilities Criteria (UFC) 3-600-01. This shall be developed from the draft document.

This shall include all necessary electrical information relating to the Emergency Lighting, etc.

For further information refer to Appendix E.

Loads, Diversities and Spare Capacities

The Contractor shall calculate the maximum demand in accordance with UFC 3-501-01 for the facilities using the following diversities.  The Contractor shall apply diversities to the electrical installation from the distribution boards to the supply intake. Spare capacity shall be included at distribution boards before applying diversities. Diversities (percentage of installed load in use at any one time) shall be based on the following:

| Service or equipment | Diversity | Loading Information |
| --- | --- | --- |
| Lighting | 100% | As Contractor’s design. |
| Specialist Power | 2No socket running at 50% load | 16A |
| Mechanical plant | 100% | As Contractor’s design. |

Spare capacity of 25% shall be provided at all distribution boards including 25% spare ways and a minimum of 25% spare current carrying capacity on the sub main cable and protective device serving the distribution board.  At the main switchboard, 25% spare capacity shall be included for all other loads directly fed from the main switchboard, excluding distribution boards.  An additional spare capacity shall not be added to the main supply.

Electrical Installation Life

It shall be ensured that, where practicable, all equipment that is provided under the Project has a service and maintenance quality that shall provide for components to be available on site within 48 hours of an order being received by the equipment supplier.  Where this cannot be achieved, for example for major components, this shall be clearly detailed, and a schedule of these components shall be provided along with the anticipated lead-in time to procure these items.

In all areas of the building, accessories shall comply with BS 7671 environment category AG3 High severity, below 2000mm and AG2 Medium Severity above.

The Contractor’s selected equipment and materials shall also comply with Electromagnetic Compatibility criteria as detailed by BS 61000 and shall be capable of withstanding the corrosive atmosphere within the PAS, humidity and fuel vapours.

The design life criteria required for the electrical services installation is 10 years in the case of retained / reused installations, and 25 years in the case of new installations. This period is from handover to expected replacement/renewal and shall assume normal usage and maintenance. All plant with an estimated life of less than 10 years shall be identified along with the suppliers’ estimate of efficient operating life.

Maintenance Access

It shall be ensured that any new switchgear, distribution boards etc. are accessible for maintenance and routine cleaning without the necessity for specialist access equipment in accordance with, but not limited to, the requirements of DE Design and Maintenance Guide 08 (DMG 08).  It shall also be ensured all new equipment does not restrict access to existing equipment such that the requirements of DMG 08 for existing equipment would not be met.

Insurance Inspections

The Contractor shall carry out an initial Insurance Inspection on the new AGE Pad Lighting column and written scheme of examination provided.

Mounting Heights

All new accessories and equipment shall have mounting heights as required by the Contractor’s DSEAR assessment and as required by the following documents where these do not conflict with the Contractor’s DSEAR assessment:

DE Standard Specification 034,

The Contractor shall ensure that all operable and maintainable equipment is placed in reach and is specified in accordance with the requirements of his DSEAR assessment and shall not use this assessment to install a lesser classification of equipment out of reach.

Electrical Services Infrastructure Connections

General

The Contractor shall isolate the supply to each PAS at the commencement of the works.  Where a PAS is on shared supply with other PAS which are not in the same phase of the works or other facilities not part of the works the Contractor shall make arrangements for the electrical supplies to the facilities not included in the current phase of the works to remain operational.

A schedule of PAS electrical supplies is provided for information only at tender stage.

All works associated with the supply cables shall be carried out in accordance with the requirements of:

JSP 375, Volume 3, Chapter 3.

Where the Contactor carries out external works including excavation he shall satisfy himself that he has accurately located thee LV supply cables and shall plot them onto record drawings, showing dimensional information from fixed points.

Standby Power

Permanently Installed Generator

Each PAS has an existing dedicated Low Voltage Generator located in a generator room constructed to the rear of the Efflux tunnel.

This Generator shall be disconnected and left in situ.  Generator back up is NOT required to the refurbished PASs.  The facility for connecting a Mobile Generator for PAS vaults shall be maintained as subsequently detailed.

The Contractor shall remove the supply cables between the Main switchgear and the Generator

The Contractor shall remove the LV supply to the distribution board in the Generator room.

These supplies shall NOT be replaced.

Generator Connection points, Vaults

Where a PAS is provided with a below floor vault, the vault switchgear is provided with an external generator connection point.

The Contractor shall replace this connection point with a new proprietary BS 60309, 63A, TP&N, IP67 appliance intel mounted in a suitable enclosure to ensure the inlet is sealed to IP67 at all times it is not in use.

The tails from the switchgear shall be connected directly to the connector terminals.  The Contractor shall provide an earthing/grounding connection to an earth stud on the new mounting box.  The earth stud shall be brass.  The Contractor shall ensure the resistance to earth at the earth/ground stud does not exceed 20 ohms.

The Contractor shall coordinate any works to the Vault generator connector with the Project Manager and the owning agency.

New Communications Infrastructure Connections and Cabling

Telecommunications Infrastructure Cabling

There are two Telecoms installations within each PAS.  A recently installed Fibre Optic based system with LAN and VoIP connectivity and a legacy BT Federal Copper service.

Where the PASs contain a Vault, the legacy system is used to transmit alarm signals etc. to remote locations

The Contractor shall employ British Telecom (BT) Federal to strip out all redundant Telecoms services within the PAS and external connectivity to the PAS.

Fire Alarm Infrastructure Connections

The PASs do not have any Fire Detection systems and Fire Detection is NOT to be installed as part of these works

Automated Revenue Metering System

An Automated Revenue Management Service (ARMS) to monitor Electricity use shall NOT be installed.

Internal Electrical Installations

Stripping Out

The Contractor shall remove the existing electrical installation and associated cabling except for the following systems, which shall remain intact and complete:

High Bay LED lighting, where already installed, including switching, control and final sub circuit cabling

Vault switchgear and connections to the Vault, except generator connection sockets

Telecoms, recently installed (2016 onwards and ongoing), LAN network including incoming fibre, Telecoms equipment enclosure, structured cabling to VoIP telephone, LAN (NIPRNet drops) WiFi access points.

GPS antennas, repeaters and associated cabling where installed.

Security systems, recently installed, to PAS

Vault security systems and the Telecoms infrastructure remote signals are routed over.

All cable containment and associated support brackets etc. serving the above systems shall also be retained.

Where any PAS system is to be retained, the Contractor shall carry out a condition survey and record the results, which shall be agreed with Project Manager before works commence.  This shall include as a minimum a visual inspection and report, and where Low Voltage (LV) cabling is provided verification testing as required by BS 7671 for Electrical Installation Condition Reporting (EICR).  All inspection and testing results shall be accepted by the Project Manager before works commence.  Where the Contractor establishes existing equipment is deficient or cabling systems do not meet requirements as established by testing and he does not raise these deficiencies at this stage he shall make good these deficiencies before completion at his own costs.

Where defects or deficiencies are noted during this initial inspection and testing, the Contractor shall include in his design for rectifying these defects and deficiencies and itemise them separately within his design.

All materials shall be disposed of by the Contractor in accordance with the Waste regulations and WEEE regulations.  The Contractor shall keep records of all material disposals.

Any open fixing holes left exposed in the concrete arch after services have been removed shall be filled with a non-shrink epoxy concrete repair mortar.

Mains Distribution

General

The Contractor shall replace all switchgear within the PAS in accordance with the requirements of his design and his DSEAR assessment.  This shall include the incoming service Main Switch.  New switchgear may be mounted on the existing switchgear support frames, subject to the following requirements:

- All framework shall be cleaned and inspected for corrosion.

- Any member with corrosion other than surface corrosion which can be removed without affecting the integrity of the member, shall be replaced.

- The Contractor verifies by calculation that the new switchgear load can be supported by the existing switchgear frame.

- The frame is re-finished, with an appropriate coating which has the appropriate fire resistance and chemical resistance to comply with the Contractor’s DSEAR assessment and corrosive substances assessment.

Alternatively, or where the Contractor cannot meet the above criteria the support framework shall be replaced.

A Fireman’s isolation switch shall NOT be installed.

New switchgear shall be installed to serve only the required equipment within the PAS, e.g. the protective device serving the generator room distribution board shall not be replaced.

Switchgear shall be suitable for the hazardous environment it is installed in as determined by the Contractor’s DSEAR assessment.  Switchgear shall be all of one manufacture and shall be installed in a logical sequence.

The Contractor shall employ a Specialist, competent in the field of Surge Suppression to design the Transient Voltage Surge Suppression (TVSS) installation, select TVSS devices and their installation.  The Contractor shall provide dedicated design submission for his TVSS design.

Transient Voltage Surge Suppression (TVSS)

Transient Voltage Surge Suppression (TVSS) shall be installed in accordance with the requirements of JSP 482.

The Main Switchboard shall incorporate TVSS which shall be provided on all external cables entering or leaving the building, e.g. main supply, generator supply (at both ends), external lighting, etc.

Additionally, TVSS shall be installed to all final sub circuits, as required by JSP 482.

TVSS units shall be tested in accordance with BS 62305, BS 2914: ‘Current power circuits’, and IEEE C62.41 1991 ‘Recommended practice on surge voltages in low voltage AC power circuits’.

The Contractor shall employ a Specialist, competent in the field of Surge Suppression to design the TVSS installation, select TVSS devices and their installation.  The Contractor shall provide dedicated design submission for his TVSS design.

All TVSS units shall have continuous indication of its protection status which shall clearly show full protection present, reduced protection (replacement required) and no protection (failure of protector). The status indication shall warn of protection failure between all combinations of conductors, including neutral to earth.

Remote indication of status is NOT required.

Fireman’s switch

A Fireman’s switch is NOT required.

A label shall be provided at the personnel entrance to indicate the location of the main switchboard(s).  This label shall read ‘MAIN SWITCHGEAR LOCATED…’. All signs shall be of rigid plastic type, NOT adhesive and shall be mechanically fixed.

Signage

The main switchboard shall be provided with a JSP 375, Volume 3, Chapter 3, P3 “Main Intake Switch Sign” sign.

In addition, each device shall be labelled to indicate the equipment it serves and the location of that equipment.  Labelling shall be offered for approval before it is manufactured.

Building Regulation Metering

Metering shall NOT be installed to comply with the Base Standard, Building Regulations Part L2 etc.

Vault Switchgear

The Vault switchgear is under the jurisdiction of a separate agency and shall not be replaced as part of these works.  The Contractor shall protect the switchgear during the course of the works from any damage, infiltration or contamination.  To achieve this protection, as a minimum the Contractor shall use a timber screen with 250micron (1000g) Polythene Sheeting fixed to timber frames and proprietary jointing tape.

The protection of the switchgear shall be accepted by the Project Manager and the agency having jurisdiction before any works near including above the switchgear is carried out.

Uninterruptible Power Supplies (UPS)

Uninterruptible Power Supplies other than those existing within existing Telecoms equipment are NOT required.

The recently installed Fibre Optic Telecoms systems incorporates a UPS, therefore once this equipment is isolated from the mains distribution within the PASs it shall remain live and the Contractor shall ensure all LV circuits radiating from the Telecoms equipment are verified as dead before any works around them are carried out.

On re-energisation the Contractor shall monitor the operation of the UPS.

Sub Mains Distribution

Sub Mains Cables General

As previously detailed, Final Sub Circuit Distribution Boards shall be incorporated within the main switchgear assembly.  The switchgear and associated distribution boards shall be arranged in a logical intuitive sequence to aide maintenance and fault finding.

Where End User controls and or indicators are incorporated within the Switchgear, distribution board assembly they shall be located on a dedicated section(s) away from any maintenance or control switching and shall be clearly identified showing their function.

Distribution boards shall include 25% spare ways at the conclusion of the works.

Sub main cables shall be of the ratings required and provided with mechanical protection in all instances.

Sub main cables shall be XLPE insulated, steel wire armoured, low smoke and zero halogen (LSOH) served (XLPE/SWA/LS0H to BS 5467) manufactured by a UK or Western Europe BASEC approved manufacturer.  Cable sheaths shall be black.  Reduced neutral cables shall not be used.  Cable glands shall be suitable for the environment as determined by the Contractor’s DSEAR assessment and Corrosive environment assessment.  Cable glands shall also be fitted with an earth tag.  A LSOH CPC conductor shall connect this tag directly to the switchboard or distribution board earth bar.

Where two or more armoured sub main cables are installed, they shall be provided with a galvanised steel cable tray to which they shall be secured.

Sub main cables shall be supported throughout their entire length.

Sub Main Cable Containment

Sub main cables shall be provided with adequate support and containment. Individual armoured cables may be secured directly to the building fabric.

Multiple runs of armoured cables shall be secured to cable trays or cable ladders.

Cable trays shall be suitable duty for the number and weight of cables supported.  However, light duty tray shall not be used.

Generally, sub main cables shall be secured to medium duty galvanized class 2 cable tray within the building.  Any cable tray used externally shall be hot dipped galvanised class 4.

Where cable trays are installed below 600mm in the horizontal plane or run across floors, they shall be heavy duty irrespective of the cable loading placed on them to protect them from physical damage.  Cable trays shall be galvanised finish and assembled using bolted connections with purpose made couplers, tees bends, risers, etc. Earth continuity shall be maintained at all connections.  All bends, tees, etc shall be gusseted.  Cable trays shall be supported in such a manner that cables can be laid onto it both during construction and post completion.

Cable Containment Support Work

Support steelwork shall be provided as necessary.  This support work shall consist of modular galvanised steel channel sections secured to or suspended from the building fabric.  The provision of support steel work shall be coordinated with other services to ensure common services support systems are used where appropriate.  Where systems are subject to movement or vibration, this movement or vibration shall be accommodated by any common support system or isolated from it.

Where cabling and equipment is to be hung from the building fabric, the building fabric shall be of suitable construction to support the proposed weights or additional support work shall be provided as necessary.

Support work shall be suitable for the hazardous and corrosive environment in which it is to be installed and shall either be floor standing with appropriate baseplates in turn secured to the floor, or securely attached to the mass concrete wall or soffit.

Fixings to the PAS walls and soffit shall be carried out using fail-safe expanding anchors drilled into the mass of concrete behind.  These anchors shall be capable of resisting vibration induced from running the aircraft engines for extended periods inside the PAS.  The Contractor shall include details of proposed anchors within his design submissions.

The Contractor shall not weld any fixings to the PAS metal lining.

Any open fixing holes left exposed in the concrete arch shall be filled with a non-shrink epoxy concrete repair mortar.

Sub-Circuit Management

Final Circuit Distribution Boards

Distribution boards shall accommodate BS EN 61009 “Residual current operated circuit. -All devices shall be behind a lockable or tool secured cover.  In addition, it shall be possible to lock each MCB in the ‘off’ position using a suitable accessory, as appropriate.  Three phase boards shall be B type and 1-phase boards shall be A type.  Distribution boards shall be finished to the manufacturer’s standard colour.

Final sub circuit cabling shall enter distribution boards directly or via a suitably sized cable marshalling box meeting the requirements of the Contractor’s DSEAR assessment.

Cable trunking shall NOT be used.

The correct type of RCBOs shall be utilised for the equipment controlled unless specific requirements are detailed, e.g. type C for LED lighting, to accommodate the driver inrush on start up. The Contractor shall ensure his selected RCBO ratings and type are suitable for LED lighting etc.

All protective devices supplying socket outlets shall be protected by RCBO.

Sub Circuit Cabling

Sub circuit cabling shall emanate from distribution boards to serve equipment, luminaires, and accessories, etc. The method of cabling shall meet the requirements of the Contractor’s DSEAR assessment, JSP 482 and comply with following

Rigid Non-Metallic conduit shall not be used.

Slip joints and sliding couplers shall not be used

Final sub circuit cabling shall generally consist of LS0H insulated 450/750V grade stranded copper conductors to BS 7211 installed in galvanised solid drawn conduit.

No final sub circuit cable shall be smaller than 1.5 mm2cross sectional area. Full size CPCs shall be installed. Furthermore:

All LV and functional extra low voltage (FELV) cable systems shall be capable of being rewired ;

All containment systems shall provide for an increase in power circuits of 25% and lighting circuits 20%, subject to a minimum of one circuit each;

Cables with integral mechanical protection XLPE/SWA/LSOH may be clipped directly to the building fabric.

All mechanically protected cables at low level, i.e. below 600 mm, shall additionally be protected by a section of galvanised steel channel.

All cabling shall be included within metallic containment, including all cabling on the outside of the building.

Labelling

Circuit labels shall be mechanically fixed laminated (tarfolite or similar).  The fixing of labels shall not compromise the hazardous zone classification of the equipment or accessories and the manufacturer’s requirements to retain the integrity of the hazardous zone.  Where necessary, the Contractor shall apply labels adjacent to the item of equipment.  Where labels are adjacent to equipment they shall be located consistently and logically.

Cable Containment System

The Contractor shall plan and provide detailed containment route drawings and details co-ordinated with all other services, including those existing that are to remain, and Architectural and Structural drawings / requirements.

The Contractor shall ensure all new containment provides a minimum of 25% spare capacity for installation of additional cabling in the future, this is deemed to be in addition to any space / fill factors required by the wiring regulations.

The Contractor shall carry out all containment sizing and shall indicate all sizes on the design, co-ordination and installation drawings.  All containment sizing calculations shall be submitted for comment prior to the commencement of the installation as previously detailed. It is the Contractor’s responsibility to ensure all submissions are made in due time to allow for comments and resubmission without affecting the construction programme.

All containment systems shall be installed in accordance with the manufacturer’s requirements and recommendations.

Trunking

Cable trunking shall NOT be used.

Conduits

Generally, all conduits to accessory fittings on walls shall be mounted to the galvanised steel lining using suitable brackets and or mounting plates where necessary.

All conduits shall be galvanized class 4. Galvanised solid drawn.  Conduits shall be made good with a Zinc rich self-healing Coating applied in accordance with the manufacturer’s requirements. Where the building is not water tight this shall be done as the installation progresses.

External Cabling

All cabling below ground shall be carried out using cables with integral mechanical protection.

Where trunking is utilised externally, it shall be gasketed to achieve the required IP56 rating. Conduits shall be galvanised class 4. All penetrations through the building skin shall be gasketed and sealed.

To comply with MOD JSP 375, Volume 3, Chapter 3, all underground cables shall be installed so that they are able to be isolated and earthed. This means that the external lighting circuits (which include underground cables) shall be supplied via a purpose made earthing switch. This may be in the form of a manual changeover switch. Any contactors controlled by photocells shall be able to be closed manually, or by-passed, to enable the earth to be applied to the outgoing cables.

Lighting

General

New lighting shall be installed using LED lamped luminaires to match that already installed in some PAS’s, subject to the requirements for Life Cycle Cost Analysis.

The lighting design shall comply with UFC 3-530-01 and as a minimum comply with the following

- Horizontal Illuminance (Average ±10%) 50 fc (500 lux) at 2’-6” (762mm) Above Finished Floor (AFF) level

- Vertical Illuminance (Average ±10%) 15 fc (150 lux) at 3’-6” (1067mm) AFF

Horizontal Illuminance Uniformity 3:1 average to minimum All eyebrow luminaires, luminaries mounted across the roof at high level at the rear of each PAS, and low-level luminaires along each side shall be replaced in all PASs

Lighting to the personnel entrance lobby shall be replaced.

Lighting to the AGE pad and external lighting around the rear of the PAS shall be replaced.

The lighting to the aircraft apron in front of the PAS shall be replaced.

All luminaires shall be hard wired. The plug and socket connection method, or flexible cable extending from a socket outlet mounting box method, (currently employed) shall NOT be used.

PAS existing High-Level LED Lighting

Where the PAS have recently been equipped with new LED high bay lighting this lighting shall be retained.

A schedule of PASs with existing LED lighting is included in the appendices.

This lighting shall be protected during the course of the works to ensure the luminaires are not affected by dust, paint and coating contamination.  On completion of the works the protection shall be removed and luminaires cleaned in accordance with the luminaire manufacturer’s instructions.

The Contractor shall test the electrical circuits feeding the existing high-level lighting at the commencement of the works and repair any faults found.  Where the cabling system is not to current colour identification standards the Contractor shall include for all necessary labelling to comply with current BS7671 requirements.

The Lighting is controlled by low level Passive Infra-Red (PIR) sensors.  Theses sensors shall also be protected during the works and cleaned after the works are complete.  The Contractor shall allow for re-setting and re-commissioning the PIRs and ensuring they correctly and consistent control the lighting throughout all PASs.

PAS New High-Level Lighting

Where PAS lighting has not already been upgraded to LED lighting the Contractor shall carry this work out as part of this refurbishment.

Lighting shall be provided using Light Emitting Diode (LED) lamped luminaires.  The Contractor shall select luminaires that meet the requirements of UFC 3-530-01 for the use of LED luminaires, including complying with including the requirement for lifecycle costing.  The Lifecycle costing shall include the requirement to periodically measure lighting levels and shall be submitted as part of the Contractor’s tender.

The lighting levels shall be as those achieved by the LED lighting recently installed in other PASs (where they are painted white) which the Contactor shall verify against the requirements of the Lighting UFC 3-530-01 3-9.2, including the requirement for limited up lighting.

The Contractor shall carry out a Lifecycle Cost Analysis (LCCA) to prove that his selected LED luminaires meet the requirements of the UFC 3-530-01 Clause 2-1.4, e.g. they out perform a discharge or induction lighting solution.  The analysis will account for the following variables:

Initial cost

Energy cost

Demand cost

Utility inflation rate

Maintenance equipment cost

Maintenance labour cost (including cleaning of luminaires)

Maintenance inflation rate

Replacement cost

Disposal/recycling cost

Annual hours or operations

Lifetime (all system must be capitalised twice in the analysis period but not to exceed 40 years)

The Contractor shall also carry out a Life Cycle Cost Analysis (LCCA) as required by UFC 3-53-01 clause 2-1.4 and UFC 1-200-02 and submit his LCCA as part of his design submission.  In addition, the Contractor shall provide a copy of the manufacturer’s 10-year warranty.

Energy cost shall be takes as £0.0866 per kWh (Jan 2018 costs).  Annual hours of operation shall be taken as an average of 6 hours per day/5 days per week (allowing for automatic lighting control)

The Contractor shall install new final sub circuit cabling and conduits to serve the new LED lighting installation.

New PIR lighting controls shall be installed which shall comply with the hazardous zone requirements and perform in a similar manner to the lighting controls in PASs where the lighting has recently been replaced.

An isolation switch shall be provided at the main switchgear, distribution equipment position to allow the luminaire to be isolated for maintenance purposes.  This switch shall be clearly labelled as to its purpose.

Eyebrow luminaires

In all PASs the Contractor shall replace the existing fluorescent eyebrow luminaires with LED luminaires.

These luminaires shall provide general illumination and emergency lighting.  Emergency lighting shall be High Risk Task Area Emergency Lighting at floor level to a distance of 2000mm from the back wall to a minimum lighting level of 10% of the normal light level provided by the eyebrow luminaires for general illumination or 15 Lux, whichever is the greater.

The eyebrow lighting shall be separately switched, by manual switch from a common switch location by the Personnel entrance and from a position on the personnel entrance side of the PAS at the back wall.

The emergency lighting function shall be Non-Maintained operation 3-hour duration.

Low level lighting

The Contractor shall install low level luminaires along the side of the PAS from the personnel door to the rear of the PAS.  This lighting shall be installed to provide illumination below the aircraft wings and shall therefore be mounted above the low-level ventilation ducts but not greater than the height of the aircraft wing.

These luminaires shall be selected to produce the required lighting levels, but secondarily to avoid disabling glare to operatives.  The lighting shall be designed to achieve a minimum of 150 Lux on a vertical plane on the PAS centreline from floor level to under wing level.

In addition, these luminaires shall incorporate emergency lighting battery packs to provided High Risk Task Area Emergency Lighting for the length of the PAS for 2000mm from the walls.  In addition, the Contractor shall ensure the following are illumined by the emergency lighting:

Switchgear

Vault Switchgear

Telecoms equipment

Aircraft door operating position

Fire Fighting Equipment marked storage positions

In addition to the low-level lighting, higher level emergency lighting luminaires shall be installed to ensure all the above locations are adequately illuminated.

Low level lighting shall be controlled by a separate manual switch at a common switch position by the personnel entrance.

Under Wing Lighting

The Contractor shall install in ground luminaires, to illuminate the underside of an aircraft when parked on the centreline in the position indicted by the PAS lining.

Luminaires shall be Zone 1 flush with the finished floor level of the PAS.  Luminaires shall be load bearing and provided with white lenses to provide vertical illumination to illuminate the underside of the aircraft.  NOTE luminaires used in other locations at RAF Lakenheath for a similar purpose are not Zone 1 certified and cannot be used in this location.

The exact positioning of the luminaires shall be coordinated with the floor concrete bay joint arrangement to ensure the structural integrity of the floor is not adversely affected.

The Contractor shall cable the luminaires from a dedicated circuit with manual switch located at a common switch position at the personal entrance.

The Contractor shall drill a pilot hole through the concrete slab to the sub straight, in line with the wet seating pot drain point to allow any water that enters the pot to drain away.

The final sub circuit cables serving the under-wing lighting shall consist of external grade 230V insulated and sheathed cables which shall be laid in bay joints and in new saw cuts across the top of bays as defined by Defence Works Functional Standard 06 “Guide to Airfield Pavement Maintenance”, in particular clause 4-13.

External Lighting

General

The Contractor shall install new external lighting luminaires to the following locations:

Personnel entrance door

AGE Pad

Security lighting to the rear of the PAS around the efflux tunnel and generator room

Aircraft ramp

Where external luminaires are controlled by Photocell switches, the Contractor shall install an isolation switch and manual on switch, for maintenance purposes, within the control circuit.

External lighting luminaires shall be LED and the Contractor shall carry out all Lifecycle costings as required by UFC 3-530-01 to justify his luminaire selection.

Luminaires shall be shielded or U0 rated to avoid glare.  The Contractor shall ensure the installation is designed to avoid glare to adjacent roads and taxiways and shall ensure the luminaires are mounted and aimed in accordance with his calculations.

Personnel Entrance Door

External lighting shall be provided to personnel doors for access, egress, and emergency egress. These luminaires shall be automatically controlled.  Luminaires shall be combined general and emergency lighting luminaires and shall be positioned to illuminate the approach to the PAS from the aircraft ramp and illuminate the outer lobby and draught lobby.

Luminaires shall be switched by movement sensors, with photo cell override for the luminaire lighting up the approach path and movement sensors of the draught lobby.

AGE Pad

The existing street lighting lantern and column illuminating the AGE pad to the side of the PAS shall be replaced by a new lantern and column.  The lantern shall be LED to Base Standards for industrial areas but shall be fitted with flat glass lens, not dished, and shall be mounted to avoid glare to any adjoining roads and taxiways.

This lantern shall be rewired from the new PAS distribution switchgear and new cable containment shall be provided.  The containment shall be routed through one of the existing PAS cable pass through tubes which shall be weather stopped on completion of the works,

This lighting shall be automatically controlled by photocell sensors which shall also control the rear security lighting.

The lantern column shall be connected into and grounded by the LPS system.

Security lighting to the rear of the PAS

The existing wall mounted floodlights around the efflux tunnel and generator room shall be replaced.

New luminaires shall be LED floodlights fixed to the PAS structure at high level, 500mm below the top of the wall

Security lighting shall comply with the requirements of UF3-530-01 for security lighting.  The illumination level shall be a minimum of 2-2   Lux (0.2 fc) illumination measured on the horizontal plane at ground level for a minimum distance of 3 times the luminaire mounting height.  External security luminaires shall be controlled by a photocell switch in common with the AGE Pad lantern.

Aircraft Apron

The Contractor shall replace the existing aircraft apron floodlights with new LED floodlights.

The existing floodlights are mounted on steel columns bolted to the PAS roof with cabling routed through PAS at high level and passing through the roof adjacent to each column position.

The Contractor shall examine the existing post fixings and replace any that are deficient or unsuitable for the prevailing conditions or load to be carried.

New LED Luminaires shall illuminate the aircraft ramp to 5 Lux (5fc) to a distance from the PASs equal to the floodlight mounting height, except where this would cause glare to adjoining road ways or taxiways.

The floodlights shall be switched by a manual switch located by the door controls and a photocell switch to prevent the floodlights being used during the hours of daylight.

The Floodlights shall be rewired from the new Switchgear/distribution equipment.   All new cabling shall be provided within metallic cable containment system conduit.  Final connections shall be made using flexible metal conduit with UV resistant PVC sheath no bare cables anywhere.

The new column shall be bonded to the Lightning Protection System.

Emergency Lighting

General

Emergency lighting shall be provided throughout the facility to enable occupants to safely leave and move clear in the event of local lighting failure in any one room or area in accordance with NFPA 101.  This system will include illuminated exit signs to the personnel door.  This sign shall have maintained operation for a 3-hour duration.

Emergency Lighting shall be incorporated within general lighting luminaires as previously detailed.

Testing System

Testing facilities for emergency lighting shall comprise local manual switches located at the main distribution board position.

The key switch shall simulate local circuit failure or area failure and shall illuminate a green neon indictor at the test switch position to show that the circuit is under test. The test switches shall be engraved 'EM LTG TEST’.

Where there is more than one test switch in any room or area the Contractor shall include a separate laminated mimic diagram for each of these rooms showing which luminaires are tested by which switch. A copy of this diagram shall be provided in the switch cupboard containing the distribution board that serves the circuits.

General (Utility) Power

General

The Contractor shall NOT provide any General Power or Specialist Power sockets to the PASs

External Sockets

The Contractor shall retain the two external 16A socket outlets with integral RCDs mounted on metal fares each side of the PAS ramp.

The Contractor shall locate the sub circuit cables serving these sockets and record their routing on his record drawings.

The Contractor shall test these circuits and, subject to acceptable test results, reconnect them to his new distribution equipment.  Where these circuits do not pass testing, the Contractor shall replace the circuits in total.

Aircraft Doors

General

The Contractor shall employ a Specialist door drive installer to install a new door drive system to the PAS Aircraft Doors.

As a minimum the drive system shall comprise:

Motor, clutch gearbox assembly for each door leaf

Control devices and limit switches etc. on the door

Control stand

Control panel

Waring device

This work shall be coordinated with the replacement of the door trucks and general refurbishment of the doors.

Motors

The Contractor shall replace the existing door drive assemblies, including their mounting frame, base plate, floor fixings etc.

The new drive system shall be coordinated by the Contractor with the replacement of the door running gear, and the revised alignment of the gearing mounted on the door.

The Door drive system shall comprise motor, fluid coupling/clutch manual dis-engagement facility or similar and gear box and brake unit.  The drive system shall be capable of starting the opening process, moving the static load of the doors, opening the doors in the required time, decelerating and stopping the doors before they contact the end stops.  The drive system shall allow the doors to be opened to any position and left in that position.  The drive system shall overcome any normal external effects, wind load, snow load, thermal expansion effects etc.

The fluid coupling/clutch shall ensure the motor does not burn out if the door is prevented from moving by external influences and shall be additional to the electrical overload protection provided to the motor itself.

The fluid coupling/clutch shall provide a manual dis-engagement facility.

The Contractor shall provide copies of his Specialist’s calculations which illustrate the following as a minimum:

Static load of doors

Rolling load of doors

Gear ratios

Motor power and torque

Drive system energy losses

These calculations shall clearly demonstrate the that drive system as a complete system is powerful enough to open the doors under any normal condition.

Controls

The Contractor shall provide and control position for manual operation of the doors.

This position shall allow an operative to face the doors from inside the shelter when the doors are being operated and shall include the following functionality:

Door selection, left, right or both

Door operation, requiring continued pressure, e.g. the doors will stop if the control is released.

Door system live indication

Door obstructed indication

Fluid coupling/clutch in powered operation position

Drive system overload

Emergency stop

The Controls shall be mounted at standing operator height and be intuitive in operation and function.

An engraved set of operating instructions shall be provided at the control position to clearly explain how the doors are operated.

Control Devices

The Contractor shall provide all new control devices required to allow the doors to function safely including

Limit switches for slowing and stopping doors at limit of travel

Obstruction detection devices, external to the PAS to ensure the door opening space is clear

Fluid coupling/clutch manual disengagement position

Gearbox low lubrication warning

Fluid coupling, where applicable low fluid warning

Brake engaged/dis-engaged

Warning devices operational

Door track heaters operational

All control devices shall be suitable for the harsh environment they will be installed in and the operation requirements.

Warning Devices

The Contractor shall provide audio visual warning devices to indicate when the doors are in motion.  These devices shall as a minimum cover the following areas:

Door overruns at both sides

Aircraft Ramp

PAS

Warning lamps shall be amber and sounders shall be consistent in all locations.

Controls shall be incorporated to prevent door operation if all warning devices are not operating, however a manual override shall also be provided for this facility.

Door Track Heaters

The Contractor shall install door track heaters.  These heaters shall be independent of the drop drive control system.

Heaters shall operate when the external temperature drops below freezing to prevent any accumulation of water, ice or snow in the door running track well or around the wheels etc. freezing.

The operation of this heating shall be monitored, and an external warning lamp shall be provided by the personnel entrance to indicate if the heating is not working when external conditions require it to.

The power supply and controls to the rail heating system shall be provided with a manual tests facility to allow maintenance inspections to verify that the system is operational.

Control Panel

All controls including motor overload protection, interlocking relays and contactors etc shall be located in a single control panel suitable for the environment within the PAS.

An emergency stop button shall be included on the Control Panel.

Aircraft Winches

The Contractor shall not replace or reinstate the existing aircraft winches.

Electrical services associated with these systems shall be removed.

Mechanical Services

The Contractor shall install all power supply and control cabling required for the mechanical ventilation services.

These services shall be as detailed in the Mechanical Section.

Where manual control switches are required these shall be grouped to together with the other control switches, lighting, at the Personnel entrance.

Communications

General

The existing functional Telecoms system shall be retained and the Contractor shall protect these systems, including all equipment control panels, Wireless Access Points (WAPs).

Structured Cabling

The recently installed Base LAN (NIPRNet) network installed in the PASs shall be retained.

This installation comprises an incoming Single Mode 12 Core Fibre Optic cable terminating in a National Electrical Manufacturers Association (NEMA) steel enclosure adjacent to the personnel door above the incoming cable duct.  The steel enclosures house the Active equipment in PASs Juniper Switch 220V providing 2-VoIP 1 in, 1 out.

LAN cables run from Box to NEMA in conduit.  This enclosure is provided with dedicated power supply and a dedicated conduit system extends from the enclosure to serve:

Voice over Internet Protocol (VoIP) Phone Points,

Intruder Detection System etc. managed by US Army Corps. Of Engineers.

Local Area Network (LAN) access points

2nd Generation Wireless LAN (2GWLAN) Power Over Ethernet Wireless Access Points (WAPs)

Satcom, currently being rolled out across PASs

The NEMA enclosure is mounted off new Unistrut steel support sections braced off the structure around the personnel door, the PAS galvanised steel lining, and the steel supports for the original legacy Telecoms installation.

The existing support steel work where required to support the cabinet shall remain in situ.  Where this comprises legacy steelwork the Contractor shall clean, prime and coat this steelwork to protect it from further corrosion.

The Contractor shall protect the existing LAN conduit system and WAPs during the course of the works, the conduits shall NOT be painted, however they shall be cleaned at the completion of the works.  Any equipment damaged by the Contractor shall be replaced by the 48th Comms Squadron (CS) at the Contractor’s expense.  The Contractor shall verify with the 48 CS that all equipment and systems are functioning before the works commence.

Any corroded fixings or metal background which fixings are connected to or penetrate shall be cleaned, primed and coated.  Care shall be taken NOT to damage the galvanised protective coating to the inner PAS lining.

Telephone Cabling

In addition to the recently installed LAN system a legacy copper voice system exists within the PAS.

This system is still active serving the PAS and Vault Intruder Detection System remote alarms and the Vault CCTV remote video connections.  These systems shall remain and shall be functional at the conclusion of the works.

The Contractor shall employ British Telecom (BT) Federal to establish which cables in each PAS are required to maintain the above systems and which cables are redundant.  All redundant cables, cable containment, fixings etc shall be removed.

All containment which is to remain shall NOT be coated but all fixings etc shall be treated as detailed above.

Fire Alarms

Flame Detection and Fire Alarm systems shall NOT be installed in the PAS as part of these works.

Closed Circuit Television (CCTV) System

The existing Vault has a CCTV camera mounted at high level, and an associated luminaire.  This equipment is cabled via the Vault switchgear and a connection is provided to the legacy copper BT system to the remote CCTV signal.

This equipment, cable contentment and supports shall be protected throughout the course of the works.  The Conduit shall not be coated; however it shall be cleaned at completion of the works.

Intruder Detection System.

The Contractor shall protect the existing PAS Intruder Detection Systems (IDS) during the course of the works.  Where PASs have Vaults there is a second Vault IDS system.

General IDS

The general IDS system within the PASs have recently been accredited and are in use.

The Contractor shall coordinate with 48th Security Forces and Army Corps of Engineers to de-activate these systems throughout the course of the works, eight (8) weeks’ notice shall be provided.

The IDS equipment enclosure is located to the left of the personnel entrance door.  The IDS transmits signals to the head end over the 48CS Fibre Base wide network.

The Alarm Control Panel Enclosure is mounted adjacent to the personnel entrance door next to the telephone is in each PAS.

There are in total 7 IDS microwave sensors mounted in each PAS.  There are 4 watching the front sliding doors, 1 to watch the pedestrian door, and 2 in the rear to watch the rear sliding doors.   There are also door contact switches on the aircraft doors, Efflux tunnel doors and personnel doors.  The Contractor shall liaise with the US Army Corps. of Engineers to remove the aircraft door, door contacts so that the doors can be removed for new carriages to be fitted.  On completion of the works the Contractor shall ensure the US Army Corps of Engineers reset, calibrate and test the alarms.

All IDS equipment, cable containment and supports shall be protected during the works.  Cable containment shall not be coated, however it shall be cleaned on completion of the works.  Any corroded fixings shall be cleaned primed and coated.

Vault IDS

The Vault IDS system within the PAS is operational.

The Contractor shall coordinate with the Owning Agency to de-activate these systems throughout the course of the works.

All IDS equipment, cable containment and supports shall be protected during the works.  Cable containment shall not be coated, however it shall be cleaned on completion of the works.  Any corroded fixings shall be cleaned primed and coated.

Mass Notification System

There is no requirement for the Base wide Mass Notification systems to be installed in the PASs as part of these works.

Lightning Protection System (LPS)

General

The PAS Lightning Protection Systems consist of the steel reinforcing of the Concrete structure which is brought out at low level and connected to earth rods.

Testing and Rectification works

The Contractor shall employ a specialist Lighting Protection Installation to carry out testing of the existing air termination works and any necessary rectification works.

Recent test results are available for guidance only at Tender stage.

The Contractor shall carry out the test required by ESTC Standard No 6 Part 1 and as detailed below to determine the integrity of the existing air termination network, with all electrodes disconnected:

Resistance from the uppermost part to every earth electrode connection point or where there is no access to the air termination at the uppermost part between every earth electrode and every other earth electrode connection point.

Resistance for all conductive parts on the outside of the PAS to the nearest earth electrode

Resistance from LPS earth rod connection point to Main Switchgear bonding connection

Steel PAS internal lining to ground at a minimum of four locations.

Where these tests reveal any defects, these shall be rectified.  The Contractor shall record all testing and complete the required certificates identified by ESTC Standard No 6 Part 1.

Earth electrodes

The existing earth electrodes shall be disconnected and abandoned.

The existing inspection chambers shall be lifted out and removed from site.  The rods shall be pulled out or where this is not possible cut off 300mm below the surface.  The position of any discarded rods remaining in the ground shall be clearly marked on record drawings.

The Contractor shall install a new parallel earth rod systems with appropriate horizontal spacing between rods as required by JSP 482 and BS 63025.

Earth electrodes shall be installed in concrete inspection chambers, which shall be numbered.   The connection between the tape and the electrode shall be coated in suitable grease.  The Contractor shall ensure the electrode chamber is cleared out at the completion of the works so that earth tape is visible within the pit, the tape to rod connections are clearly visible and accessible and that when the clamp is released the tape and rod can be separated.  Earth electrodes shall be copper clad, steel core.  They shall be fitted with a driving head and connections ensuring rod to rod connection.

Earthing (Grounding)

General

The existing grounding/earthing system shall be tested and repaired as necessary in accordance with the requirements of the following:

BS 7671

JSP 482 MOD Explosive Regulations

AFI 32-1065

MIL HDBK 274A Electrical Grounding for Aircraft Safety

UFC 3-575-01 Lightning and Static Electricity Protective Systems

Inspection and Testing.

At the commencement of the works, the Contractor shall carry out a visual inspection and electrical testing in accordance with the above documents.

As a minimum the Contractor shall record the following parameters:

Resistance between aircraft grounding points

Resistance between aircraft grounding points and main earth bar

Resistance between aircraft grounding points and PAS ground bar

Resistance between equipment stands and PAS grounding system

Resistance between all exposed conductive parts and all other conductive parts, including metal doors and frames.

The Contractor shall rectify any defects discovered by the above testing.

The Contractor shall re-test the installation on completion of the works.

Grounding Plates

The Contactor shall replace the existing steel, painted grounding plates mounted on the side walls of the PAS.  The grounding plates shall be hard drawn copper mounted on shock resistant insulators off a steel mounting plate, which in turn shall be fixed to the PAS structure.

The Contractor shall ensure there is no fortuitous connection between the earth bar and the PAS wall.  The Contractor shall ground the plate to the PAS metal lining using cable tags at each end of the bonding cable which are compatible with metal work it is to be connected to.  The Contactor shall provide a minimum of four brass studs with anti-shake washers and nuts to allow bonding fly leads to be attached.  The grounding bar shall be a minimum of 1200mm long.

Building Management System

A Building Management System (BMS) shall not be installed but a Main Control Panel shall control the ventilation system.

Fire Precautions

General

The Contractor shall develop the design of the Works to comply with the Building Regulations, British Standards, National Fire Protection Codes (NFPA), ETL, United Facilities Criteria (UFC) 3-600-01, Defence Infrastructure Fire Standards (DIFS) and other Standards or Codes of Practice detailed elsewhere in this document. Unless specifically stated within this document, no relaxation or derogation from these standards is permitted.

The PAS hangar is an existing building and the scope of the proposed works will not include any material alterations or change of use as defined in the Building Regulations. Additionally, as the project is not funded for more than 50% of reconstruction costs then under programming rules the USVF do not have to bring the PAS’s up to code.   Therefore, in accordance with Part B of the Building Regulations there is no requirement to bring any existing deficiencies up to current prescriptive code guidance.

As part of the works a Dangerous Substances and Explosive Atmospheres Regulations (DSEAR) assessment will be undertaken as well as a fire risk assessment. If any item on the fire risk assessment is established to carry an intolerable risk the contractor will bring this to the client’s attention. These items should be made good prior to the building being reoccupied.

It shall be the Contractor’s responsibility to provide a fire strategy to show compliance with the relevant legislation / codes of practice and to obtain the necessary compliance certification from the Defence Safety Authority (DSA) Fire Safety Regulatory, Base Fire Officer and the NFPA Authority Having Jurisdiction (AHJ). The NFPA AHJ shall be identified as DSA Project Fire Officer unless notified otherwise.

Fire Strategy Report

The Contractor shall prepare a Fire Strategy Report in the format of the requirements of the Defence Infrastructure Fire Standards and the Chartered Institute of Buildings Services Engineers (CIBSE) Guide E “Fire Safety Engineering”. The Contractor shall ensure that the Fire Strategy Report is compliant with all relevant legislation and the provision of the requirements as detailed in the Works Information. It is the responsibility of the Contractor to develop the design of the Works to meet the requirements of the Works Information.

The Fire Strategy Report shall be prepared by the Contractor’s Fire Protection Engineer – refer to section 8.1.3.4. The Fire Strategy Report shall be a standalone document that incorporates all related drawings, design certificates, etc., that relate only to the fire strategy. The Contractor’s design drawings will be appraised by the Contractor’s Fire Protection Engineer prior to submittal to the Employer and confirmed as being fully compliant without exception.

The Contractor shall incorporate all necessary architectural, structural, civil, electrical and mechanical information relating to the Fire Strategy Report. The following in particular, but not exclusively, shall be considered within the Fire Strategy Report:

The ratings of fire compartment

Fire doors

Locations of extinguisher cabinets if applicable

Designation of primary escape routes, etc., in all areas

Emergency Lighting

Hydrant locations

Signage

BMS if applicable

Deficiencies in the existing building not included in the scope of work

Any other element relevant to Fire Safety

- The Fire Strategy Report shall be submitted as part of the 65% and 95% design submittals detailed in sections 3.2.1 of this document. It shall include photographic evidence of firestopping to barrier penetrations in non-visible or inaccessible areas.

Employer Reviews

At completion of the Employer’s reviews of the Contractor’s Design, when satisfied that the Fire Strategy Report is in compliance with the Works Information, the DSA Fire Officer will issue a Fire Certificate A. The 100% Design will not be accepted without this document

At completion of construction, a Compliance Certificate (supersedes Fire Certificate B) will be issued by the DSA Fire Officer when satisfied that the Fire Engineering System installation is in compliance with the Works designs submitted for Fire Certificate A. Any changes to the design or installation that occur after a Fire Certificate A is issued will need to be re-submitted for acceptance. This may require that designs for the complete facility may need to be resubmitted.

The Contractor shall be responsible for arranging for the Employer’s Fire Advisor to attend and witness all testing and commissioning of installed fire safety equipment. Two weeks’ notice will be required for all such visits. All correspondence between the Contractor and the Employer’s Fire Advisor shall be via the Employer’s main point of contact and not directly with the Fire Advisor.

Roll of the DSA Fire Safety Inspector

A Project Fire Officer or Defence Safety Authority (DSA) Fire Safety Inspector will be appointed. For the purposes of this specification both titles should be considered as interchangeable.

For the avoidance of doubt, the role of the Project Fire Officer is to ensure compliance with host nation regulations and fire standards. They may review specific US requirements, but these will also be reviewed by the End Users. The Project Fire Officer will not be responsible for design/development/specifying of specific standards nor be responsible for developing and certifying design solutions that comply with these regulations and standards; that is the role of the designer.  At their sole discretion, the Project Fire Officer may offer goodwill advice or review comments on any documentation reviewed. The Contractor shall not rely upon receiving review comments or goodwill advice.

Upon review and agreement that the 100% design meets the specified standards criteria, the Project Fire Officer will issue a Certificate A (confirmation of design approval by DSA). If the building/project is completed exactly to the package/drawings/documents/fire strategy agreed/listed on the Certificate A, the project can expect to achieve a DSA ‘Acceptance Certificate’ once completed.  Should any works/aspect change from the original issued Certificate A, then the Certificate A is void and the process starts again, i.e. it will be treated as a new submission, and thus the DIO PFO may identify new failures to comply. Adjustments to the scope of work under these circumstances should be carefully considered and managed to keep from “voiding” the Certificate A.

The approval of Certificate A should be considered as Defence Safety Authority (DSA) approval and not that of an individual.  Should the PFO change during the life of a project following the issue of an approved Certificate A, the new PFO would be obliged to honour this certificate regardless of any differing thoughts or views.

Applicable Fire Regulations

RAF Lakenheath is occupied by the United States Visiting Force (USVF) and therefore all works are required to comply with the relevant requirements of the National Fire Protection Association (NFPA) standards in addition to the functional requirements of Part B of the Building Regulations 2010 (England and Wales).

The following codes will be used as the main basis for the design to achieve the life safety requirements for each of the proposed buildings at RAF Lakenheath subject to this project. In all cases the most onerous requirement will apply.

Approved Document B (ADB), Fire Safety – Volume 2 Buildings other than Dwellinghouses;

National Fire Protection Association 101 Life Safety Code (NFPA 101);

International Building Code (IBC);

US Air Force Engineering Technical Letters (ETLs);

Unified Facilities Criteria, UFC 3-600-01, Fire Protection Engineering for Facilities;

Unified Facilities Criteria UFC 4-211-01 Aircraft Maintenance Hangars, with Change 1

Defence Infrastructure Fire Standards (DIFS);

AFCESA, ETL 00-7, Fire Protection Engineering Criteria, Correlation of US and Host Nation Codes and Criteria.

Fire Systems Requirements

Means of Escape

It is not proposed to make any changes to the existing means of escape provisions to the building. However, the Contractor’s design team will review the existing provisions against that outlined in the prescriptive guidance for existing PAS hangars.

Fire Protection systems

Fire Detection and Alarm

No Fire Detection and Alarm is currently installed in the PAS. It is not proposed to install Fire Detection and Alarm required. The Contractor shall confirm that Fire Detection and Alarm is still not required for the PAS’s as the design progresses to 35% design.

Emergency Lighting and Exit Signage

As part of the proposed works, each PAS will be equipped with an emergency lighting system designed and installed in accordance with BS 5266 suite of standards as required by ADB and DIFS.

The system is further to be designed to incorporate the requirements of UFC 3-600-01.

Exit signage will be provided in accordance with BS ISO 3864 and BS 5499 suite of standards. As per the requirements of the RAF Lakenheath Base Standard, all exit signs will be maintained self-luminating type.

The contractor will provide an Emergency Lighting certificate. BS 5266-1 2016 1 Annex D procedures for measuring luminance of emergency lighting and model completion certificate shall be complied with.

Emergency Lighting Operational Test Certificate. BS 5266-1 Annex M model inspection and test certificate shall be complied with.

Fire Suppression

No fire suppression system is currently installed in the PAS building. It is not proposed to provide a suppression system as part of the works. The Contractor shall reconfirm that a suppression system is still not required for the PAS building as the design progresses to 35% design.

Fire Extinguishers

The provision of first aid firefighting equipment will follow the specification outlined in the RAF Lakenheath Base Standard with regards to the type of fire extinguishers to be provided. The location of extinguishers will follow the guidance of BS 5306 and NFPA 10.

In accordance with UFC 3-600-01, all fire extinguishers will be located in recessed or semi-recessed cabinets.

mottmac.com