## General Items
SCHEDULE OF WORKS
Client |  | Royal Borough of Kensington and Chelsea
Project |  | Roof Void Fire Compartmentation
Address |  | Blechynden House, Burgess Fields
Nature of Works
Revision: |  | 1.01
All sizes and quantities provided in this document are approximate and for guidance only. The contractor should undertake a detailed site survey to confirm all measurement.
Item | Description | Unit | Quantity | Rate | £
1.0 General Descriptions
1.01 | The works comprise: -
| Retrofitting of fire compartmentation within the roof voids of Blechynden House and Burgess Fields. | Item | 2
1.02 | The work includes, but not limited to: | Item | 1
Fire Compartmentation within Roof Voids
1.03 | The Contractor is to undertake the role as designer ensuring all proposals satisfy the requirements of all recent relevant Building Regulations such as Approved Document B Fire Safety, Approved Document K Protection From Falling, Approved Document F Ventilation
1.04 | The Contractor is to ensure all designs are compliant with all recent relevant British Standards such as BS 5250 Management of Moisture in Buildings, BS 5839 Fire Detection and BS 9999 Fire Safety in Design of Buildings, BS 9991 Fire safety in the design, management and use of residential buildings.
1.03 | The contractor shall make provisions within his/her individual pricing for assessing the working areas and all works to be undertaken therein. No extra cost shall be entertained by the Employer for failing to do so. | Item | 1
1.04 | The Contractor is to allow for an Building Control Officer as required to ensure the proposed and completed works are in accordance with the current Building Regulations. | Item | 1
1.05 | The Contractor is to develop/prepare all necessary plans and documentation in order to obtain all necessary Planning Permissions and Building Regulations approval. | Item | 1
1.06 | It will be a condition of granting Practical Completion (PC) that written confirmation is received stating the Approved Inspector/Building Control Officer will issue a Completion Certificate for Building Regulations Approval. | Item | 1
1.07 | On the appointment of the Contractor, it will be a condition of granting PC that all necessary completed/passed test certification including all fire related documantation and certification is available as soon as is practical. This should be no later than 48 hours before the Contractor's request for the grant of PC. | Item | 1
1.08 | The completed Health and Safety File, O&M Manuals, as-built drawings and completed forms must be issued in draft as required by the preliminaries in order for PC to be granted. | Item | 1
1.2 Working Procedures
1.21 | General preliminaries, contractual matters, Contract Administration details, are as described within the sections of this document. Whilst the instructions of variations should only be accepted from an appointed Contract Administrator (herein after referred to as CA), Health and Safety matters or those affecting the residents may be instructed by the property management company, in which case they should be adhered to and immediately referred back to the Contract Administrator. All details regarding welfare, toilet facilities, water etc. for the works are as per earlier/separate details. | Item | 1
1.22 | The works have been described in details, and the price and specification shall include all works necessary to achieve the required results including works specifically indicated as a part of the work, or implied by, or contingent upon the work specified. | Item | 1
1.23 | For the Contractor's information, the building will be occupied for the duration of the works by the residents. All dust, debris and noise is to be the responsibility of and contained by the Contractor. All areas, common parts and private residents' balconies affected by dirt and/or dust are to be thoroughly cleaned. | Item | 1
1.24 | Full protection regarding Health and Safety matters, particularly to public and communal areas, must be provided to all areas of works. The Contractor is to ensure the site or local working area is fully secure at the end of each day. All ladders, temporary staging, cherry pickers and access equipment is to be removed from the site. All open works to be left in a safe condition and sealed as necessary. | Item | 1
1.25 | The Contactor is to provide all access for the roof void works, to include scaffolding to carry out the specified works including all provisional repairs. The access will also be required for inspection of the works for instruction purposes and throughout the progress of the Contract. It will also be required for snagging inspections by the Contract Administrator and re-inspections thereafter if appropriate. No claims will be entertained for the Contractor's failure to allow for sufficient access, nor for any scaffold or other access that may need to be re-erected for the purposes of the CA's inspections/re-inspections. | Item | 1
1.26 | The Contractor is to remove and dispose away from site all debris arising during/from the works on a daily basis and ensure that the dust is kept to a minimum at all times. Any disposal must be via a controlled site and all carriage and disposal notices/certificates are to be provided on completion. | Item | 1
1.27 | Noisy operations are not to be carried out outside of normal working hours. Noisy work includes: all hammering, shot firing, use of power tools, grinders, etc., and any other operations causing noise, vibration, dust or fumes which will affect the quiet working of the office. Permission must be obtained in advance to work outside these hours. | Item | 1
1.28 | Works taking place to, or requiring access via a residential property are not to commence before 9.30am unless otherwise agreed with that particular resident. | Item | 1
1.29 | No overtime, claims considered or additional payments or extensions to the contract period will be granted for restrictions imposed on working hours for noisy, disruptive work. | Item | 1
1.291 | The contractor is to use only those products were directly specified, alternative products are only to be used with the CA's prior written approval. Where the contractor wishes to use alternative products, they will be expected to supply samples to the CA for agreement. Where products have not been specified, the contractor is to provide details of all products for CA's approval. | Item | 1
1.292 | Prior to works commencing, the Contractor will be required, in conjunction with the CA, to prepare a full and detailed photographic Schedule of Condition of the areas likely to be affected by the works. This should include any internal areas, external areas and the streetscape. The Schedule of Condition is to be provided no later than 1 week after the pre-commencement meeting for CA approval and in any event prior to the commencement of work on site. Should no schedule be provided the areas listed will be deemed to be as new and the Contractor will be responsible for any repairs arising. | Item | 1
1.293 | Contractors are to provide a full and detailed method statement on their proposals for successfully completing the project. The method statement is to include particular reference to the methods and proposals for working at height, negating noise and general disruption to the operation of the surrounding offices. | Item | 1
1.3 CDM Regulations / Programme
1.3 | The works will be notifiable under the CDM Regulations 2015. See CDM PD Prelims. | Item | 1
1.31 | The Contractor is to undertake the works in full accordance with the Construction (Design and Management) Regulations 2015, the Health and Safety at Work Act 1974 and the Management of Health and Safety at Work Act 1999, together with all other relevant legislation. | Item | 1
1.32 | The Contractor is to be responsible for producing their Construction Phase Health and Safety Plan, to be submitted to the Principal Designer no less than one week prior to the commencement date. The Health and Safety Plan is to be updated as necessary during the works and the contractor is to provide all relevant information with contents list and summary index of all information to the Principal Designer for inclusion in the Health and Safety File prior to PC. Include for all costs associated with CDM Regulations and associated statutory requirements. | Item | 1
1.33 | The contractor shall submit with their tender a detail programme outlining their proposals for executing the works. | Item | 1
1.34 | The Contractor is responsible for submitting to the CA a detailed programme for the sequencing of operations for the works, 7 days prior to the commencement date and this must be updated on a monthly basis. | Item | 1
1.4 Control of Substances Hazards to health Regulations 2002
1.41 | The Contractor shall at their own expense, observe and comply with the Control of Substances Hazardous to Health Regulations 2002 (COSHH) and all other Acts of Parliament instruments, rules, orders, regulations, by-laws and any updates and amendments thereof. The Contractor shall take all reasonable precautions for safeguarding their employees and any other persons' and property affected by the execution of the Contract. | Item | 1
1.5 Good Practice
1.51 | Where, and to the extent of materials, products and workmanship are not fully specified, they shall be: - In accordance with the manufacturer's instructions and good building practice (including the relevant provisions of current BS documents and BRE Digests) - Suitable for the purpose of the works stated in or to be reasonably inferred from the contract documents. | Item | 1
1.6 Specification Generally
1.61 | The Schedule of Works item should be carried out in accordance with the Materials and Workmanship clauses, manufacturers instructions and recommendations and best practice, applicable to the item of work concerned and under the direction of the CA. | Item | 1
1.62 | Where there are references in the Schedules to the Specification Clauses, the Contactor shall note that any reference to specific items in the Preambles shall be deemed also to include other general items relating to that trade and particular items contained in the Schedule referred to. | Item | 1
1.63 | All Provisional Sums are to be expended in whole or in part as directed by the Contract Administrator following inspection. | Item | 1
1.7 Stability of the Works
1.71 | The Contractor is to maintain the stability and existing structural integrity of the existing buildings within and adjacent to the Works at all stages of the Contract. | Item | 1
1.8 Site measurement and survey
1.81 | The contractor is to take all necessary site measurements and check dimensions to prepare fabrication drawings and other elements of the structure. | Item | 1
1.82 | It is the responsibility of the Contractor to check all measurements and Quantities provided in this Specification. All measurements and quantities provided are for guidance only. | Item | 1

## Clarifications
Not Evaluated - For Information Only
SCHEDULE OF WORKS
Client |  | Royal Borough of Kensington and Chelsea
Project |  | Roof Void Fire Compartmentation
Address |  | Blechynden House, 1 Kingsdown Close W10 6SQ
Nature of Works |  | Fire Compartmentation
Revision: |  | 1.01
All sizes and quantities provided in this document are approximate and for guidance only. The contractor should undertake a detailed site survey to confirm all measurement.
Item | Description | Unit | Quantity | Rate | £
2. Clarifications
2.1 | Prices to be in accordance with current inflation rate in line with the current base date as set out in the tender documents. – To note as of July 2023 the current inflation rate for CPI is 7.3%.
2.2 | Contarctor to provide Over heads and profit on all additional materials/specialist sub-contractors
2.3 | Contractor to provide a day rate for site suprtvision to undertake additonal works
2.4 | All variation the contractor is to refer to NHF 8.1 Schedule of Rates for works in relation to Compartmentation Works where applicable, and for non-compartmentation
2.5 | RBKC will evaluate the contractor schedule of rates in conjunction with the NHF 8.1 schedule of rates | For Information Only - Response not required

## Blechynden House
SCHEDULE OF WORKS
Client |  | Royal Borough of Kensington and Chelsea
Project |  | Roof Void Fire Compartmentation
Address |  | Blechynden House, 1 Kingsdown Close W10 6SQ
Nature of Works |  | Fire Compartmentation
Revision: |  | 1.01
All sizes and quantities provided in this document are approximate and for guidance only. The contractor should undertake a detailed site survey to confirm all measurement.
Item | Description | Unit | Quantity | Rate | £
3.0 Roof Compartmentation - Blechynden House
Note: Drawing number B202 Rev C is to be used for all items listed below for Blechynden House
| To the locations as shown on the drawing, within the roof void, from top of existing wall from floor below, supply and install new fire compartmentation including new door openings. | Item | All
3.1 | Fire Compartmentation
To the locations as shown on drawing B202 Rev C, within the roof void, from top of existing wall from floor below, supply and install including door openings new (please note only 1 of the following options will be used but the contractor is required to price both):
3.12 | Option A The contractor is to supply and install a minimum of 60 minute fire barriers from the floor below to the roof rafters separating each habitable space below. The contractor is to provide details of the proposed product to be used for instruction by CA prior works commence and will be required to obtain confirmation from the proposed manufacturer of the suitability of the product to be installed prior to commencement. | Item | All
3.13 | Option B The contractor is to supply and install an approved fire break stud walling to provide a minimum of 60 minute fire resistance from the floor below to the roof rafters and separating each habitable space. Allowance to be made to accommodate door openings in approved materials to provide a minimum of 60 minute fire resistance. An approved fire batt/barrier to be used to seal the wall at roof level and installed in strict accordance with manufacturers instructions. Contractor to provide product and build up details for instruction by CA prior works commence | Item | All
3.2 | Fire Doors/Access
3.21 | The contractor is to remove the existing door sets and dispose of all materials off site | Item | All
3.22 | The contractor is to supply and install 60 minute fire door sets where shown on the drawing - to each newly formed compartment. All to be installed in strict accordance to manufacturers instructions and include vision panels or FR viewers. Provisional Sum. | Item | All
3.23 | Contractor is to supply and install new 60 minute roof void hatch in strict accordance with the manufacturers instructions and include vision panels or FR viewers. Allowance to be made for increasing the hatch size to facilitate works and future maintenance. | Item | All
3.24 | Contractor to provide allowance for opening up new void within roof space to accommodate newly formed access hatch to allow alternative escape route/s from within the roof void and supply and install new 60 minute fire rated access hatch in strict accordance with manufacturers instructions and include vision panels or FR viewers. | Nr | 1
3.25 | The contractor is to ensure all gaps serving the fire breaks and door sets within the roof void are completely filled in strict accordance to the building regulations and to the products manufacturers instructions. | Item | All
3.3 | Penetrations
3.31 | The contractor is to ensure all service penetrations within the roof void are fire stopped and all fire stopping products are to be installed in strict accordance with the manufacturers instructions. For the avoidance of doubt, all service penetrations to include SVPs. Contractor is to provide a full photographic schedule of all fire stopping upon completion. | Item | All
3.4 | Smoke Detection
3.41 | The contractor is to supply and install new hard wired smoke detection units within every compartment as denoted on the drawing. Each detector unit shall be sufficient to cover the each area and where an area exceeds the limit of the detector head a second unit must be installed. All units to be installed in strict accordance with the manufacturers instructions, approved document B and BS-5839. The contractor is to provide product information for instruction by CA prior works commence | Nr | 8
3.42 | The contractor is to supply and install inspection hatches to allow for the inspection of the newly installed smoke detection units where access from the roof void is not possible, as denoted on the drawing - Hatches to be appropriately fire rated at 60 mins and installed as per manufacturers instructions. Provisional sum. | Item | All
3.5 | Lighting
3.51 | Allow for replacement of existing light fittings with new emergency light fittings and connection to existing emergency light circuit to each newly formed compartment zone | Item | All
3.52 | Allow for additional emergency light fittings so as there is sufficient light levels within each compartment within the roof space to meet the regulations. All to be connected to the existing emergency light circuit. | Item | All
3.53 | Allow for providing new light switch to control all roof void lights at each new roof hatch location. | Item | All
3.6 | Walkways
3.61 | The contractor is to supply and install new walkways where new smoke detector heads and new lighting units may be difficult to access from the original walkways. To be installed with adequate height to allow for insulation beneath. Provisional Sum. | Item | All
3.7 | Smoke Ventilation
3.71 | The contractor is to completely remove the existing timber constructed smoke ducting from the roof void and dispose off site. | Item | All
3.72 | The contractor is to design, supply and install new galvanised steel smoke ventilation ducting in place of the original timber ducting. The design must meet all requirements within approved document B and F and BS-1366, BS-9991 and BS-9999. Contractor to provide design details for instruction by CA prior works commence | Item | All
3.73 | The contractor is to allow for the removal of ventilation lattices located within the roof structure that facilitate the extraction of the smoke via the smoke shaft and replace with new non-combustible ventilation grilles in strict accordance with approved document B and F, BS-1366 and BS-9991 | Item | All
3.74 | Where ventilation lattices are to be removed, contractor to provide scaffolding to provide a safe working platform to the external areas of the roof void. | Item | All
3.8 | House keeping
3.81 | The contractor is to ensure all waste materials are removed from the roof void following completion and cleaned through removing all construction dust and debris and left to a professional standard. | Item | All

## Burgess Fields
SCHEDULE OF WORKS
Client |  | Royal Borough of Kensington and Chelsea
Project |  | Roof Void Fire Compartmentation
Address |  | Burgess Fields, 57 Wormington Road W10 5PT
Nature of Works |  | Fire Compartmentation
Revision: |  | 1.01
All sizes and quantities provided in this document are approximate and for guidance only. The contractor should undertake a detailed site survey to confirm all measurement.
Item | Description | Unit | Quantity | Rate | £
4.0 Roof Compartmentation - Burgess Fields
Note: Drawing number BS111 - Rev B is to be used for all items listed below for Burgess Fields
To the locations as shown on the drawing, within the roof void, from top of existing wall from floor below, supply and install new fire compartmentation including new door openings.
4.1 | Fire Compartmentation
4.11 | The contractor is to remove existing stud partition walls shown on the drawing and dispose of all materials off site | Item | All
4.12 | The contractor is to remove the existing door sets and dispose of all materials off site | Item | All
4.13 | The contractor is to supply and install an approved fire break stud walling to provide a minimum of 60 minute fire resistance from the floor below to the roof rafters and separating each habitable space. Allowance to be made to accommodate door openings in approved materials to provide a minimum of 60 minute fire resistance. An approved fire batt/barrier to be used to seal the wall at roof level and installed in strict accordance with manufacturers instructions. Contractor to provide product and build up details for instruction by CA prior works commence | Item | All
4.2 | Fire Doors/Access
4.21 | The contractor is to supply and install 60 minute fire door sets where shown on the drawing - to each newly formed compartment. All to be installed in strict accordance to manufacturers instructions and include vision panels or FR viewers. Provisional Sum. | Item | 15
4.22 | The contractor is to ensure all gaps serving the fire breaks and door sets within the roof void are completely filled in strict accordance to the building regulations and to the products manufacturers instructions. | Item | All
4.23 | The contractor is to supply and install inspection hatches to allow for the inspection of the newly installed smoke detection units where access from the roof void is not possible, as denoted on the drawing - Hatches to be appropriately fire rated at 60 mins and installed as per manufacturers instructions and include vision panels or FR viewers. Provisional sum. | Item | 4
4.3 | Penetrations
4.31 | The contractor is to ensure all service penetrations within the roof void are fire stopped and all fire stopping products are to be installed in strict accordance with the manufacturers instructions. For the avoidance of doubt, all service penetrations to include SVPs. Contractor is to provide a full photographic schedule of all fire stopping upon completion. | Item | All
4.4 | Smoke Detection
4.41 | The contractor is to supply and install new hard wired smoke detection units within every compartment as denoted on the drawing. Each detector unit shall be sufficient to cover the each area and where an area exceeds the limit of the detector head a second unit must be installed. All units to be installed in strict accordance with the manufacturers instructions, approved document B and BS-5839. The contractor is to provide product information for instruction by CA prior works commence | Nr | 24
4.5 | Lighting
4.51 | Allow for replacement of existing light fittings with new emergency light fittings and connection to existing emergency light circuit to each newly formed compartment zone | Item | All
4.52 | Allow for additional emergency light fittings so as there is sufficient light levels within each compartment within the roof space to meet the regulations. All to be connected to the existing emergency light circuit. | Item | All
4.53 | Allow for providing new light switch to control all roof void lights at each new compartment zone. | Item | All
4.6 | Walkways
4.61 | The contractor is to supply and install new walkways with associated insulation as denoted within the drawing. Walkways are to be installed with adequate height to allow for the installation of the appropriate depth of insulation. Newly formed walkways are to be created to ensure each smoke detector head has access for maintenance where main walkways are restricted. | Item | All
4.7 | House Keeping
4.71 | The contractor is to ensure all waste materials are removed from the roof void following completion and cleaned through removing all construction dust and debris and left to a professional standard. | Item | All

## Prelims
SCHEDULE OF WORKS
Client |  | Royal Borough of Kensington and Chelsea
Project |  | Roof Void Fire Compartmentation
Address |  | Burgess Fields, 57 Wormington Road W10 5PT
Nature of Works |  | Fire Compartmentation
Revision: |  | 1.01
All sizes and quantities provided in this document are approximate and for guidance only. The contractor should undertake a detailed site survey to confirm all measurement.
Item | Description | Unit | Quantity | Rate | £
5.0 Prelims
5.01 | Contractor to provide welfare units to facilitate toilets, office and adequate storage for the whole works | Item | 1
5.02 | Contractor to provide skips for waste to be removed from site regularly once full and at final completion of project. | Item | 1
5.03 | Contractor to provide permanent site management for the duration of the works. | Item | 1
5.04 | Contractor to provide resident liaison officer for the duration of the works. | Item | 1