## Sheet1
Company Name:-
Project:- Henrymoore Refurbishment
| Construction Specification | Design Area | Qty | Price
1 | Back Ground
2 | Henrymore is currently a ward for the elderly patients with 3no of multi-bed bays and 4no of single bays. The purpose of this project is to carryout refurbishment works which will increase the areas of single bed bays, create an additional multi-bed bay, provide en-suite facilities to all multi-bed bays and carryout general refurbishment works to all patient areas in Henrymoore.
3 | Scope of Works
4 | Preliminaries
5 | Skip, Site set up
6 | Building Works - Partitions - Areas 1, 2, 3 and 4. (Refer To Preposed Drawings)
7 | Area 1 - 1.114, 1.115, 1.116, 1.117, 1.118
8 | Wall Openings Area 1 -Remove Partition walls and doors from single bed bays (1.115 and 1.116), Remove partition walls from single bed bay En-suits (1.114 and 1.117), Create new door opening in W/C Shower (1.118) allowing en-suite access from multibed bay (1.120)
9 | Partitions Area 1 - Erect new partition walls in single bed bays (1.115 and 1.116) increasing the room area in both rooms. Partition wall shall be 100mm Plasterboard Stud wall Partition forming wall. Erect New petition walls in En-suite W/C showers for single bays (1.114 & 1.117), Infill partition wall to existing door opening in W/C Shower (1.118). Partition wall shall be 100mm Plasterboard Stud wall Partition forming wall.
10 | Area 2 - Rooms 1.12, 1.122, 1.123, 1.124, 1.125, 1.126
11 | Wall Openings Area 2 -Remove Partition walls and doors from single bed bays (1.123 and 1.124), Remove partition walls from single bed bay En-suits (1.122 and 1.125), Create new door opening in W/C Shower (1.126) allowing en-suite access from multi-bed bay (1.127).
12 | Partitions Area 2 -Erect new partition walls in single bed bays (1.123 and 1.124) increasing the room area in both rooms, Erect New petition walls in En-suite W/C showers for single bays (1.122 & 1.125)Infill partition wall to existing door opening in W/C Shower (1.126). Partition wall shall be 100mm Plasterboard Stud wall Partition forming wall.
13 | Area 3 - Room 1.192
14 | Wall Openings Area 3 rooms 1.192 Create an opening in wall to extend the area of clean utility room (1.192)
15 | Area 4 - 1.128A, 1.189A, 1.198
16 | Wall Openings Area 4 - Erect an opening in wall and remove double door next to Nurse station 2.
17 | Partitions Rooms Area 3 - Erect new partition wall with a double door opening extending corridor access from Henrymoore into multi-bay room 1.89, Erect new partition walls (1.128A & 1.189A) with door opening facing muilti-bed bays creating 2n No of Ensuite W/C Showers for Multi-bed Bays (1.128 & 1.189), Erect new partition wall creating new Nurse Station 2.
18 | 4 Bedded Bays: Rooms 1.120, 1.127, 1.128, 1.189
19 | Ceilings:- Allow for ceiling suspended grid system to all 4 bedded bays, Allow for supply and installation of an Armstrong Orcal metal pan tile system 600X600mm. This clip in tiling system shall be supported on a galvanised spring tee bar and within HTM60. Ceiling heights shall be 2.7m in all 4 bed bays.
20 | Flooring: - Remove Existing vinyl flooring, supply and install Polyflor's Polysafe wood FX PUR Vinyl flooring.
21 | Doors:- Allow for installing new Hygienic Hinged single action doors (F30) with vision panels to each mulit-bed bay.
22 | Nurse call:- Allow for repositioning Static Nurse call system as per new bed layout.
23 | Medical Gases :- Refurbish Medical gas outlets allowing to reposition services as per proposed floor plan drawings
24 | Lighting: - Allow for installing new energy efficient LED Lighting as per proposed floor plan drawings. Lighting shall be controlled via wall mounted dimmable light switches, automatic detectors in all multi-bed bays. The lighting design shall be as follows: • A maintenance Factor of 0.8. • max of 200 lux at floor level.
25 | Emergency Lighting: - Allow for approximately 25% of the luminaires in the suite to be complete with three hour back up. All emergency lighting shall meet the requirements of BS EN 5266 and CIBSE Lighting Guide for Hospitals and Healthcare Buildings. Allow for fully lit 8W IP20 Blade emergency exit (SLOTNMF8) signage within the corridors. These shall be fitted with three hour emergency batteries.
26 | Power:- Allow for relocating power as per new bed positions; 2no of DSO at each bed 1no of DSO to be on alternative circuit with different colour fascia (blue)
27 | Wash hand basin (2No per Mulit bed Bay as per proposed drawings) IPS Panel With recess unit floor to ceiling to mount Armitage Shanks Contour Basin and Armitage Markwik Single Lever Thermostatic Sequential Mixer Tap and to conceal waste , domestic pipework services and tap electrics where applicable. Equinox solid grade laminate 13mm panels with polished black radiused edges. Top Panel to be hinged giving access to isolating valves. Sanitary wash hand basin S2154 - Contour 21 washbasin : integral back Outlet , for connection to concealed services with concealed fixings, no tap holes, no overflow no chain no plug. Mixer Tap - A6243 Markwik 21 integral thermostat, demountable panel mixer, single sequential lever, Armitage Bioguard outlet fitted, S8750 Waste 1 1/4" outlet adaptor for all contour back outlet washbasins, S8920 (TRR1/p) Trap 1 1/4" plastic resealing bottle, 75mm seal, multi-purpose outlet, S9112 concealed hangers pressed steel toggle bolts for contour washbasins.
28 | Curtain cubicles :- Allow for installing new Curtin track for all mulit bed bays as per proposed bed layout
29 | Fire :- Allow to supply, install and carry out Fire/smoke detector alteration and reprogramming.
30 | 4 Bedded En-suits W/C & Showers ; Rooms Bays: Rooms 1.18, 1.126, 1.128A, 1.189A
31 | Domestic Services :- Allow for extending hot & cold domestic services to 1.128A & 1.189A from room 1.190. Fitting shall be with ful flow 1/4 turn isolating valve. ALLOWING Excavate floor to install soil drainage.
32 | Wash Hand Basin/WC:- Allow to supply and install new WC Wash Hand Basin to all multi-bed bay Ensuits which shall be of the type: HTM 64, (LB G S) portman 21 washbasin, single top-hole, no overflow, 400mm with swivel waste. All new Wash Hand Basin Taps in WC shall be of the type: HTM 64, A4169, (TP6) Contour 21 washbasin mixer thermostatic 1 hole, single sequential long lever, copper tube inlet. WC Toilet suite , Grab rails on IPS panel system, Static Nurse call and reset points with follow-on lights to HTM standard. Led lighting on sensor switch include Emergency lighting, Allow to install Altro white rock Plastic walling all round, extract ventilation, behind the WC IPS Panel system with all plumbing connections, WC with sensor flush, IPS Panel system. Allow for 920mm disabled single door with all ironmongery. Allow for beacon. Allow for 1Nr Mirror unbreakable. Allow to install coat hooks, grab rails as per drawing
33 | Shower:- Armitage Shanks, TM1 thermostatic shower in a box S6933 Trevi CTV concentric thermostatic mixing valve with extended lever, mounting bow with stainless steel cover plate with white finish. With Armaglide 2 shower kit with 3 function hand spray 1800mm spiral hose. Chromium plated, Allowing for shower tray, seat, curtain & curtain rail, waste trap and connections, Grab rails.
34 | Floor: - Finishes: Toilet/Wet Room Finishes: install Polysafe Vogue Ultra Pur, Decorative Heavy-Duty Safety Floor, WHIRLPOOL 4805 (weld rod 5570) vinyl floor. Weld all joints and hot seal all abutments / ducts, conduits etc. Include all necessary trims to floor access plates, hinge plates & thresholds where required in accordance with the manufacturer requirements. Install polyflor capping strip (CS-N) with cove former (CF20) in accordance with the product manufacturer specifications. Prepare all areas with latex & where necessary repair resin ready to receive new sheet vinyl. Make good any disturbance to existing floor finishes
35 | Allow for Extract ventilation systems
36 | Fire :- Allow to supply, install and carry out Fire/smoke detector alteration and reprogramming.
37 | Single bed Bays: Rooms 1.115, 1.116, 1.123 & 1.124
38 | Ceilings:- Allow for ceiling suspended grid system to all single bed bays, Allow for supply and installation of an Armstrong Orcal metal pan tile system. This clip in tiling system shall be supported on a galvanised spring tee bar and within HTM60. Ceiling heights shall be 2.7m in all single bays.
39 | Flooring: - Remove Existing vinyl flooring, supply and install Polyflor's Polysafe wood FX PUR Vinyl flooring.
40 | Doors:- Allow for installing new Hygienic Hinged single action doors (F30) with vision panels to each single bed bay.
41 | Lighting: - Allow for installing new energy efficient LED Lighting as per proposed floor plan drawings. Lighting shall be controlled via wall mounted dimmable light switches, automatic detectors in all multi-bed bays. The lighting design shall be as follows: • A maintenance Factor of 0.8. • max of 200 lux at floor level.
42 | Emergency Lighting: - Allow for approximately 25% of the luminaires in the suite to be complete with three hour back up. All emergency lighting shall meet the requirements of BS EN 5266 and CIBSE Lighting Guide for Hospitals and Healthcare Buildings. Allow for fully lit 8W IP20 Blade emergency exit (SLOTNMF8) signage within the corridors. These shall be fitted with three hour emergency batteries.
43 | Wash hand basin ( 1No per single bed bay as per proposed drawings) IPS Panel With recess unit floor to ceiling to mount Armitage Shanks Contour Basin and Armitage Markwik Single Lever Thermostatic Sequential Mixer Tap and to conceal waste , domestic pipework services and tap electrics where applicable. Equinox solid grade laminate 13mm panels with polished black radiuses edges. Top Panel to be hinged giving access to isolating valves. Sanitary wash hand basin S2154 - Contour 21 washbasin : integral back Outlet , for connection to concealed services with concealed fixings, no tap holes, no overflow no chain no plug. Mixer Tap - A6243 Markwik 21 integral thermostat, demountable panel mixer, single sequential lever, Armitage Bioguard outlet fitted, S8750 Waste 1 1/4" outlet adaptor for all contour back outlet washbasins, S8920 (TRR1/p) Trap 1 1/4" plastic resealing bottle, 75mm seal, multi-purpose outlet, S9112 concealed hangers pressed steel toggle bolts for contour washbasins.
44 | Fire :- Allow to supply, install and carry out Fire/smoke detector alteration and reprogramming.
45 | Single bed bays En-suits W/C & Showers ; Rooms Bays: Rooms 1.114, 1.117, 1.122 & 1.126
46 | Wash Hand Basin/WC:- Allow to supply and install new WC Wash Hand Basin to all multi-bed bay Ensuits which shall be of the type: HTM 64, (LB G S) portman 21 washbasin, single top-hole, no overflow, 400mm with swivel waste. All new Wash Hand Basin Taps in WC shall be of the type: HTM 64, A4169, (TP6) Contour 21 washbasin mixer thermostatic 1 hole, single sequential long lever, copper tube inlet. WC Toilet suite , Grab rails on IPS panel system, Static Nurse call and reset points with follow-on lights to HTM standard. Led lighting on sensor switch include Emergency lighting, Allow to install Altro white rock Plastic walling all round, extract ventilation, behind the WC IPS Panel system with all plumbing connections, WC with sensor flush, IPS Panel system. Allow for 920mm disabled single door with all ironmongery. Allow for beacon. Allow for 1Nr Mirror unbreakable. Allow to install coat hooks, grab rails as per drawing
47 | Shower:- Armitage Shanks, TM1 thermostatic shower in a box S6933 Trevi CTV concentric thermostatic mixing valve with extended lever, mounting bow with stainless steel cover plate with white finish. With Armaglide 2 shower kit with 3 function hand spray 1800mm spiral hose. Chromium plated, Allowing for shower tray, seat, curtain & curtain rail, waste trap and connections, Grab rails.
48 | Floor: - Finishes: Toilet/Wet Room Finishes: install Polysafe Vogue Ultra Pur, Decorative Heavy-Duty Safety Floor, WHIRLPOOL 4805 (weld rod 5570) vinyl floor. Weld all joints and hot seal all abutments / ducts, conduits etc. Include all necessary trims to floor access plates, hinge plates & thresholds where required in accordance with the manufacturer requirements. Install polyflor capping strip (CS-N) with cove former (CF20) in accordance with the product manufacturer specifications. Prepare all areas with latex & where necessary repair resin ready to receive new sheet vinyl. Make good any disturbance to existing floor finishes
49 | Allow for Extract ventilation systems
50 | Fire :- Allow to supply, install and carry out Fire/smoke detector alteration and reprogramming.
51 | Corridors - 1.119 & 1.129
52 | Ceilings:- Allow for ceiling suspended grid system to corridor areas, Allow for supply and installation of an Armstrong Orcal metal pan tile system. This clip in tiling system shall be supported on a galvanised spring tee bar and within HTM60, Ceiling heights shall be 2.4m in all Corridors.
53 | Flooring:- Remove Existing vinyl flooring, supply and install Polyflor's Polysafe wood FX PUR Vinyl flooring.
54 | Doors:- Hygienic Hinged Double Action Doors (F60), with vision panels, Allow for Pure hold PRO Handle (hygienic handle that automatically dispenses sanitising gel into users hand when pulled) This shall be installed for Corridor door connecting 1.119 to 1.129 only.
55 | Lighting:- Allow for installing new energy efficient LED Lighting as per proposed floor plan drawings. Lighting shall be controlled via wall mounted dimmable light switches, automatic detectors at various points(TBA) thought the corridor. The lighting design shall be as follows: • A maintenance Factor of 0.8. • max of 200 lux at floor level.
56 | Emergency Lighting:- Allow for approximately 25% of the luminaires in the suite to be complete with three hour back up. All emergency lighting shall meet the requirements of BS EN 5266 and CIBSE Lighting Guide for Hospitals and Healthcare Buildings. Allow for fully lit 8W IP20 Blade emergency exit (SLOTNMF8) signage within the corridors. These shall be fitted with three hour emergency batteries.
57 | Wall Protection:- Allow for “Intrad” Protection or similar system to be installed to corridor area including entrances to single and multi-bed bays. • Door face protection to internal doors to corridors
58 | Fire :- Allow to supply, install and carry out Fire/smoke detector alteration and reprogramming.
59 | W/C Shower 1.121
60 | Ceilings:- Allow for ceiling suspended grid system to all single bed bays, Allow for supply and installation of an Armstrong Orcal metal pan tile system. This clip in tiling system shall be supported on a galvanised spring tee bar and within HTM60. Ceiling heights shall be 2.7m in store room.
61 | Strip out:- Allow for stripout, remove W/c baisn, showers..etc (enebeling works to convert W/C Shower into a store room)
62 | Flooring: - Remove Existing vinyl flooring, supply and install Polyflor's Polysafe wood FX PUR Vinyl flooring.
63 | Doors:- Allow for installing new Hygienic Hinged single action doors (F30) with vision panels to each mulit-bed bay.
64 | Lighting: - Allow for installing new energy efficient LED Lighting as per proposed floor plan drawings. Lighting shall be controlled via wall mounted dimmable light switches, automatic detectors in all multi-bed bays. The lighting design shall be as follows: • A maintenance Factor of 0.8. • max of 200 lux at floor level.
65 | Fire :- Allow to supply, install and carry out Fire/smoke detector alteration and reprogramming.
Decorate :- 1.106, 1.107, 1.108, 1.109, 1.110, 1.111, 1.112, 1.113, 1.101, 1.97, 1.95, 1.121, 1.119, 1.129, 1.114, 1.117, 1.122, 1.126, 1.115, 1.116, 1.123, 1.124, 1.18, 1.126, 1.128A, 1.189A, 1.120, 1.127, 1.128, 1.189.
Allow decoration and make good all round, Allow for dulux egg shell paint double coat, Colour TBA.
66 | Total |  |  | 0
67 | Contingency @ 10% |  |  | 0
68 | Sub-Total |  |  | 0
69 | Add VAT @ 20% |  |  | 0
70 | Grand Total |  |  | 0