## OHP
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | COST (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
OVERHEAD AND PROFIT
1.0 | Percentage for Profit in %
2.0 | Percentage for Overheads in %
| TOTAL % | 0

## (A2) Preliminaries
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | Quantity | Rate (£/P) | Total Cost (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
A | SECTION A PRELIMINARIES
THE SITE / EXISTING BUILDINGS
TENDERING / SUBLETTING / SUPPLY
MANAGEMENT OF THE WORKS
QUALITY / STANDARDS / CONTROL
SECURITY / SAFETY / PROTECTION
SPECIFIC LIMITATIONS ON METHOD / SEQUENCE / TIMING
FACILITIES / TEMPORARY WORKS SERVICES
OPERATION / MAINTENANCE OF THE FINISHED WORKS
CONTRACTOR'S GENERAL COST ITEMS: MANAGEMENT AND STAFF
CONTRACTOR'S GENERAL COST ITEMS: SITE ACCOMMODATION
CONTRACTOR'S GENERAL COST ITEMS: SERVICES AND FACILITIES
CONTRACTORS'S GENERAL COST ITEMS: MECHANICAL PLANT
CONTRACTOR'S GENERAL COST ITEMS: TEMPORARY WORKS
ADDITIONAL CONDITIONS OF CONTRACT
| SUB TOTAL |  |  | 0

## 6th Floor
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | Quantity | Rate (£/P) | Total Cost (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
6th Floor SECTION B BUILDING WORKS
Contractor is to allow for all works to be undertaken outside of normal operating hours.
1.0 | DEMOLITION / STRIP OUT
1.0.1 | Contractor is to allow for all appropriate protection and sheeting prior to demolition works commencing. Contractor shall ensure all ventilation, fire sensors and lighting has been appropriately protected.
1.0.2 | Contractor shall allow for removing carefully all partition in accordance with demolition and proposed drawings supplied by IDEA on 8th September. The contractor shall highlight any conflicts in the drawing early.
1.0.3 | Contractor shall allow for removing all services contained within the dado level trunking and strip back to the nearest disturbution board in accordance with the electrical workmanship clauses contained within this schedule.
1.0.4 | Contractor shall allow for removing one number strip light and all cabling back to the nearest disturbution board in accordance with the electrical workmanship clauses contained within this schedule.
1.0.5 | Contractor shall allow to carefully take down fittings within the demolition area i.e. blinds, notice boards, clocks and store on site for reuse.
2.0 | CCTV DESK
2.0.1 | Contractor is to allow to relocate CCTV station within the 6th floor. Contractor is to allow for all data, power, and service provision in regards to its relocation.
3.0 | FURNITURE MOVE
3.0.1 | Contractor shall allow to move all existing furniture to the ground floor.
3.0.2 | Contractor shall allow to move all proposed furniture from the 8th floor to the 6th floor.
3.0.3 | Contractor shall allow to move existing printers from the print area within the 6th floor.
4 | POWER & DATA
4.0.1 | Contractor is to allow for the provision of 2 double electrical sockets per desk. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
4.0.2 | Contractor is to allow for the provision of 2no RJ45 sockets per desk, all cabling is to discharge at the comms cabinet. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
4.0.3 | Contractor is to allow to provide 4 double electrical sockets and 2no RJ45 sockets to wall which is directly adjacent to the Welfare room.
5.0 | LIGHTING
5.0.1 | Contractor is to allow to re-configure lighting to accommodate proposed layout. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
6.0 | FIRE ALARM
6.0.1 | Contractor is to allow to re-configure fire alarm as needed to accommodate proposed layout. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
7.0 | CARPET
7.0.1 | Contractor to supply and fit new 500 x 500mm loop pile carpet tiles of similar colour and design to demolition areas. Colour sample is to be provided and approved by PM prior to ordering.
8.0 | PAINTING / CLEAR FINISHING
8.0.1 | Contractor to prepare, fill, and plaster as neccessary to allow decoration of all existing and new wall surfaces newly created open plan office. Where decorating effects a wall, an allowance should be made to take the decoration to the next suitable junction. Contractor shall provide two coats of Dulux Matt Vinyl cotton white emulision to all effected walls.
8.0.2 | Contractor shall prepare and decorate existing and new joinery with two coats of dulux gloss to match existing colour and finish.
9.0 | INTERNAL FIRE AND SAFETY SIGNAGE SYSTEMS
9.0.1 | Supply and install vinyl adhesive fixed fire exit directional signage (incorporating running man symbols) to comply with The Health and Safety (Safety Signs and Signals) Regulations 1996.
10 | UNFRAMED ISLOATED TRIMS AND SKIRTINGS
10.0.1 | Supply and install pre-primed softwood square edge skirting to new formed walls where floor finish is carpet and to make good to skirtings where walls have been removed. Size and profile of skirting is to match existing.
11 | BUILDING FABRIC REFERENCE SPECIFICATION
11.0.1 | Sealants, mortars, adhesives to be applied as specified.
| SUB TOTAL |  |  | 0

## 7th Floor
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | Quantity | Rate (£/P) | Total Cost (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
B | 7th Floor SECTION B BUILDING WORKS
Contractor is to allow for all works to be undertaken outside of normal operating hours.
1.0 | DEMOLITION / STRIP OUT
1.0.1 | Contractor is to allow for all appropriate protection and sheeting prior to demolition works commencing. Contractor shall ensure all ventilation, fire sensors and lighting has been appropriately protected.
1.0.2 | Contractor shall allow for removing carefully existing glass partitions, resource centres units and set aside for re-use in accordance with demolition and proposed drawings supplied by IDEA on 8th September. The contractor shall highlight any conflicts in the drawings early.
1.0.3 | Contractor shall allow for removing all services contained within the dado level trunking and strip back to the nearest disturbution board in accordance with the electrical workmanship clauses contained within this schedule.
1.0.4 | Contractor shall allow to carefully take down fittings within the demolition area i.e. blinds, notice boards, clocks and store on site for reuse.
2.0 | FURNITURE MOVE
2.0.1 | Contractor shall allow to moved all existing furniture to the ground floor.
2.0.2 | Contractor shall allow to move all proposed furniture from the 8th floor to the 6th floor.
2.0.3 | Contractor shall allow to move existing printers for relocation within the 7th Floor, to the new proposed resource areas.
3 | POWER & DATA
3.0.1 | Contractor is to allow for the provision of 2 double electrical sockets per desk. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
3.0.2 | Contractor is to allow for the provision of 2no RJ45 sockets per desk, all cabling is to discharge at the comms cabinet. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
3.0.3 | Contractor is to allow to provide 4 double electrical sockets and 2no RJ45 sockets to wall behind all resource areas
4.0 | LIGHTING
4.0.1 | Contractor is to allow to re-configure lighting to accommodate proposed layout. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule. Particular attention should be paid to the new created resource area, as particular concern has been raised regarding the lighting configuration and how this will effect computer usage.
5.0 | FIRE ALARM
5.0.1 | Contractor is to allow to re-configure fire alarm as needed to accommodate proposed layout. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
6.0 | CARPET
6.0.1 | Contractor to supply and fit new 500 x 500mm loop pile carpet tiles of similar colour and design to demolition areas. Colour sample is to be provided and approved by PM prior to ordering.
7.0 | RESOURCE CENTRES
7.0.1 | Contractor is to re-install resource centres in accordance with proposed drawings. Contractor shall allow to relocate all shelfing and postal trays. Final arrangement and design to be agreed with PM before installation.
8.0 | SECURE AREA
8.0.1 | Option 1: Contractor is to provide a price to reuse existing glazed partition system to create a new proposed secure area as denoted within the proposed plans. Contractor is to add additional glass partitioning which match the existing design, profile and RAL colour. A sample of the system is to be provided prior to ordering. Contractor is to match existing fenestrations, and to apply misted window film to every glass panel. Contractor shall allow for creating double door entry system
8.0.2 | Option 2: Contractor is to provide new glazed partition system to the secure area. The partitioning should match the existing design, profile and RAL colour. A sample of the system is to be provided prior to ordering. Contractor is to match existing fenestrations, and to apply misted window film to every glass panel. Contractor shall allow for creating double door entry system
8.0.3 | Contractor shall allow for a card access system to both doors within the secure area.
9.0 | INTERNAL FIRE AND SAFETY SIGNAGE SYSTEMS
9.0.1 | Supply and install vinyl adhesive fixed fire exit directional signage (incorporating running man symbols) to comply with The Health and Safety (Safety Signs and Signals) Regulations 1996.
10 | UNFRAMED ISLOATED TRIMS AND SKIRTINGS
10.0.1 | Supply and install pre-primed softwood square edge skirting to new formed walls where floor finish is carpet and to make good to skirtings where walls have been removed. Size and profile of skirting is to match existing.
11 | BUILDING FABRIC REFERENCE SPECIFICATION
11.0.1 | Sealants, mortars, adhesives to be applied as specified.
| SUB TOTAL |  |  | 0

## 9th Floor
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | Quantity | Rate (£/P) | Total Cost (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
B | 7th Floor SECTION B BUILDING WORKS
Contractor is to allow for all works to be undertaken outside of normal operating hours.
1.0 | DEMOLITION / STRIP OUT
1.0.1 | Contractor is to allow for all appropriate protection and sheeting prior to demolition works commencing. Contractor shall ensure all ventilation, fire sensors and lighting has been appropriately protected.
1.0.2 | Contractor shall allow for removing carefully existing resource centres units and set aside for re-use in accordance with demolition and proposed drawings supplied by IDEA on 8th September. The contractor shall highlight any conflicts in the drawings early.
1.0.3 | Contractor shall allow for removing all services contained within the dado level trunking and strip back to the nearest disturbution board in accordance with the electrical workmanship clauses contained within this schedule.
1.0.4 | Contractor shall allow to carefully take down fittings within the demolition area i.e. blinds, notice boards, clocks and store on site for reuse.
2.0 | FURNITURE MOVE
2.0.1 | Contractor shall allow to moved all existing furniture to the ground floor.
2.0.2 | Contractor shall allow to move all proposed furniture from the 8th floor to the 9th floor.
2.0.3 | Contractor shall allow to move existing printers for relocation within the 9th Floor, to the new proposed resource areas.
3 | POWER & DATA
3.0.1 | Contractor is to allow for the provision of 2 double electrical sockets per desk. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
3.0.2 | Contractor is to allow for the provision of 2no RJ45 sockets per desk, all cabling is to discharge at the comms cabinet. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
3.0.3 | Contractor is to allow to provide 4 double electrical sockets and 2no RJ45 sockets to wall behind all resource areas
4.0 | LIGHTING
4.0.1 | Contractor is to allow to re-configure lighting to accommodate proposed layout. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule. Particular attention should be paid to the new created resource area, as particular concern has been raised regarding the lighting configuration and how this will effect computer usage.
5.0 | FIRE ALARM
5.0.1 | Contractor is to allow to re-configure fire alarm as needed to accommodate proposed layout. All work shall be carried out in accordance with the electrical workmanship clauses contained within this schedule.
6.0 | CARPET
6.0.1 | Contractor to supply and fit new 500 x 500mm loop pile carpet tiles of similar colour and design to demolition areas. Colour sample is to be provided and approved by PM prior to ordering.
7.0 | RESOURCE CENTRES
7.0.1 | Contractor is to re-install resource centres in accordance with proposed drawings. Contractor shall allow to relocate all shelfing and postal trays. Final arrangement and design to be agreed with PM before installation.
8.0 | INTERNAL FIRE AND SAFETY SIGNAGE SYSTEMS
8.0.1 | Supply and install vinyl adhesive fixed fire exit directional signage (incorporating running man symbols) to comply with The Health and Safety (Safety Signs and Signals) Regulations 1996.
9.0 | UNFRAMED ISLOATED TRIMS AND SKIRTINGS
9.0.1 | Supply and install pre-primed softwood square edge skirting to new formed walls where floor finish is carpet and to make good to skirtings where walls have been removed. Size and profile of skirting is to match existing.
10.0 | BUILDING FABRIC REFERENCE SPECIFICATION
10.0.1 | Sealants, mortars, adhesives to be applied as specified.
| SUB TOTAL |  |  | 0

## (D1) Electrical Workmanship
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | Quantity | Rate (£/P) | Total Cost (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
D | ELECTRICAL SERVCIES
The contractor shall make provision to carry out a detailed site survey at Earlsdon Park, Coventry, Office Refurbishment and acquaint themselves with all necessary information, building fabric details, access, existing utilities etc, together with reference to this schedule, specification and in conjunction with plans and associated drawings to distinguish the extent and understanding of the design work, installation and commissioning required and the co-ordination of existing services. No claims for extra payments will be made for lack of knowledge of these conditions.
1.0 | LIGHTING & EMERGENCY LIGHTING
1.0.1 | Generally the existing lighting & emergency lighting installation is to be retained. Modifications to the fitting locations, switching arrangement and control configurations shall be undertaken as required to serve the new office layouts as detail within the proposed plans presented by IDEA presented to Interserve on the 8th September
1.0.2 | Lighting shall comply with Part L and P of the Building Regulations, with the provision of switching to match existing.
1.0.3 | Contract shall confirmed proposed desk layout and current lighting will meet all current regulations including Health and Safety at Work Act 1974, lux levels, lighting design, VDU use and Health and Safety (Display Screen Equipment) Regulations 1992
1.0.4 | Where applicable the lighting shall be compliant with the ‘Use of VDT Regulations’ and CIBSE LG7.
1.0.5 | The contractor shall incorporate within the general lighting scheme, a system of emergency lighting. The scheme shall comply with BS5266 and shall cover all of the refurbished areas. The form of the emergency lighting maybe major lights covering the large open spaces together with illuminated exist signage.
1.0.6 | All attendant BWIC associated with the lighting system installations and modifications shall be included within the tender price. This shall include suspended ceiling system modifications, cut outs and replacement tiles where necessary.
1.0.7 | The lighting shall be switched as the existing lighting control system with modifications undertaken to cater for the formations of the new layouts. The lighting shall be switched in clusters associated with each element of the operation.
2.0 | FIRE ALARM SYSTEM
2.0.1 | The contractor shall examine the existing fire alarm and detection system and undertake modifications as needed to suit new layout. Contractor shall determine whether it fully complies with the British Standard BS5839. Where break glass devices or sounders need to be moved or additional devices added, then the contractor shall design, supply and install these to form a compliant system.
2.0.2 | Upon completion the system shall comply fully with BS EN 54 Part 2 & 4, BS5839-1:2013 providing a category L2 level of protection compliant with LCPB approvals and fire office / building control regulations. Alteration, modification and additions to the existing fire alarm installation as required to suit the modified internal layouts and room/area re-configurations. These works will include (where applicable) the provision and installation of new devices, controls, wiring, interfaces and all ancillary devices, as well as the relocation of existing devices and ancillaries to ensure the fire alarm installation is fit for purpose.
2.0.3 | All wiring for the fire alarm system shall be in 2L1.5 red OHLSF soft skin enhanced cables concealed throughout in the ceiling voids/roof space with flush drops to items of equipment and installed all in accordance with the workmanship relevant clauses.
2.0.4 | All attendant BWIC associated with the fire detection system installations and modifications shall be included within the tender price. This shall include suspended ceiling system modifications, cut outs and replacement tiles where necessary.
3.0 | ELECTRICAL POWER SUPPLIES
3.0.1 | The contractor is to ensure that the new office layouts have 2no double sockets per desk as a minimum. These includes both proposed and existing.
3.0.2 | The Contractor shall design, supply, install and commission new electrical power distribution systems to serve the new staff breakout areas, reconfigured kitchen areas and the refurbished office areas on 6th, 7th and 9th Floor of Earlsdon Park, Coventry. The existing core power supplies shall be retained and where necessary rewired to the new distribution boards.
3.0.3 | The work carried out to the electrical installation, whether adaption / modification or new installation, shall all be carried out to BS7671.
3.0.4 | The Contractor shall supply, install and wire final power circuits to supply socket outlets, fused connection units and the like all as shown on the layout drawings. Final power circuits shall generally be wired as ring mains, no spurs shall be wired from ring circuits.
3.0.5 | All general power ring main circuits shall be protected by a RCBO’s with 30mA rating.
3.0.6 | All socket outlets shall have dual earth terminals and be wired to include high integrity earthing to meet the current requirements of the wiring regulations.
3.0.7 | Local isolation switches and fused connection units for fixed items of equipment shall be provided as necessary with matching finish. All isolators fitted with a screw fixed engraved label indicating its function and fused connection units shall be engraved and colour filled.
3.0.8 | The electrical power distribution is to be via new floor boxes to distribute power and data services to the main office areas. Power outlet quantities are to be as indicated on layout drawings and agreed with the PM before installation.
DISTRIBUTION BOARDS
3.0.12 | Where necessary, new distribution boards shall be installed to replace existing and are to be type ‘B’ split load MCB units complete with a single main isolator and two multi-mode pulsed output (modbus) energy meters to separately monitor the general lighting and power loads.
FINAL CIRCUIT WIRING
3.0.13 | Final circuit wiring shall generally be in LSF single cables installed cable trunking and PVC conduits throughout the accessible ceiling voids within PVC conduits connecting LCM’s, switch drops and skirting trunkings. All wiring as far as practically possible shall be concealed within plastered finished areas of the building via installation within fabric/ceiling and roof voids.
3.0.14 | The Contractor shall supply and install distribution cable trays, trunkings, baskets and cable management skirting trunking in all areas to fulfil the design requirements. The final layout and configuration of the trays/trunking including all necessary fixtures and fittings shall be determined by the Contractor
3.0.15 | All sub-circuit wiring shall include a separate circuit protective conductor equal to the size of the phase conductors up to 16mm²
3.0.16 | Final connection cables to items of fixed equipment shall be single core cables reference 6491B as described above or LSF flexible cords and cables to BS6500 300/500 volt grade. Suitable LCM type luminaire connectors shall be used for final connection to all luminaires mounted on MF and accessible ceilings
3.0.17 | Tri-rated cables shall be used for termination to any heat producing equipment
3.0.18 | Flexible connections to plant shall be made where possible using steel flexible conduit with PVC cover and IP rated adapters for the final connections
3.0.19 | The installations shall be fully co-ordinated with door hanging, windows, radiator positions and client equipment locations
CONTAINMENT
3.0.20 | The Contractor shall supply and install cable trays, trunkings, baskets and conduits for all wiring systems utilising containment and cable management systems.
3.0.21 | Skirting multi-compartment trunking shall be installed where necessary i.e. print stations and the Contractor shall provide suitable colour inserts on all white accessories fitted on the white dado trunking to ensure that the installation is fully DDA compliant. Where dado trunkings rise to ceiling voids they shall be interconnected with the main containment routing throughout the accommodation areas.
ACCESSORIES
3.0.22 | All accessories unless detailed otherwise within the office and amenities areas shall be flush mounting MK Logic Plus or equal and approved range to match existing
3.0.23 | All accessories plates shall match in each area
3.0.24 | All accessories shall be complete with suitable mounting boxes for either flush or surface fixing as required. All floor boxes are to match existing
3.0.25 | All attendant BWIC associated with the power system installations and modifications shall be included within the tender price. This shall include suspended ceiling system modifications, cut outs and replacement tiles where necessary.
8.0 | DATA AND COMMUNICATIONS
8.0.1 | The Contractor shall design, supply, install and commission new Cat 6 structured cabling installation to serve the refurbished areas of the 6th, 7th, and 8th floors of Earlsdon Park, Coventry being refurbished.
8.0.2 | The contractor shall provide a new CAT 6 UTP structured cabling data (and containment) installation from the server room to the final outlet locations. The data system active components and cable link to the existing data network will be installed by others. The Contractor shall conduct a final review of the required containment requirements prior to installation
8.0.3 | The Contractor shall supply, install and terminate all data points indicated, terminated into wall / trunking outlets and within the cabinets. All of the data outlets shall be connected in the terminal cabinet(s). CAT 6 cables shall be installed from the Client’s server room to each outlet. The Contractor shall supply and install conduit adapter plates on the side of the basket trays and install 20/25mm conduits between the adaptor plates and the knockout boxes for each point. The CAT 6 cables shall be drawn into the flexible conduits between the basket trays and the floor boxes providing mechanical protection of the CAT 6 cables. RJ45 snap-in outlets shall be supplied for insertion into the final outlet plates in the numbers and gangs as shown on the tender drawings. All cable sheaths must, as a minimum, of the Low Smoke Zero Halogen (LSHO) type. The Contractor shall connect all RJ45 outlets and provide individual identification to each outlet and shall provide cable markers on the server cable end to indicate which outlet is served by the individual cables. All circuits shall be tested and documented prior to the Client making final connections from the termination plates to their servers and voice equipment.
8.0.4 | All UTP cable is to be run internally to the building, no UTP cables are to be run on the exterior of the building or in the lift shafts. All vertical cables shall be secured to installed tray / basket at intervals as recommended by the cabling manufacturer. Care must be taken to avoid close proximity of cabling to pipe work.
8.0.5 | Where cables, trunking, tray work or conduit pass through floors or walls, suitable fire sealing shall be provided in accordance with BS7671:2008 (including amendments). All cables shall be contained within containment, taking the form of Cable Basketwork, Steel Trunking and Galvanised Conduit.
8.0.6 | All containment shall be of sufficient capacity, such that the total of the cross sectional areas of the cables contained shall not exceed 45% of the internal cross sectional area of the containment. Cables must not be left lying on the top surface of suspended ceilings, nor should they be in contact with any heating pipes. Notwithstanding the compliance with BS6701 and the issues of segregation, additional care shall be taken to ensure UTP cables are not routed adjacent to other services where electro-magnetic emissions may be generated. Minimum segregation distances shall also comply with the standards provided by the cable manufacturer. UTP data cable must not be run in the same containment as mains voltage cables or fire alarm circuits. Where data cables are run in trunking containing mains cables, the data cable must be segregated in a separate part of the trunking.
8.0.7 | The outlet faceplate to be provided shall meet or exceed the Category 6 standard. Compliance with this standard must be met on all pair combinations at frequencies of up to and including 100MHz. In addition to the performance specifications, the faceplate shall also meet the following requirements: - All outlets shall be provided with shutters that automatically close when the device leads are removed - All IDC connector blocks shall be permanently fixed to the faceplate - All unused faceplate apertures shall be provided with blanking plates
8.0.8 | Cable Labelling and Identification The contractor shall liaise with the client to clarify the labelling to RJ45 outlets and patch panels in accordance with their requirements. All RJ45 outlets shall be clearly marked with a securely fixed label showing the circuit number. The label should be printed, with a self-adhesive backing. Patch panels should be clearly labelled with a securely attached label showing the patch panel identifier. Each panel on the patch panel should also be labelled with the full circuit identifier. All UTP cables should be labelled at each end with tie wrap-around label printed with the circuit identifier. The label should be located near the termination point at either end, such that the circuit can still be identified if the termination is removed.
8.0.9 | All circuits shall be tested in accordance with the manufacturers recommended testing procedures. For UTP circuits the test must establish compliance with Category 6.
8.0.10 | All attendant BWIC associated with the data system installations and modifications shall be included within the tender price. This shall include suspended ceiling system modifications, cut outs and replacement tiles where necessary.
13.0 | TESTING & COMMISSIONING
13.0.1 | On completion of the entire installation or any completed section thereof, tests shall be carried out in accordance with Part 6 of BS 7671: 2008. The Contractor shall supply all necessary instruments and labour for these tests and if necessary, he shall at his own expense prove the accuracy of the instruments.
13.0.2 | Upon completion of the works, the Contractor shall hand over 3 No. Copies of an operating and maintenance manual which shall contain, but not be limited to, the following information:
- | Emergency contact numbers
- | Procedures for fault finding
- | Emergency procedures.
- | System description.
- | Manufacturer’s maintenance instructions and contact details.
- | As fitted drawings.
- | Revised and new distribution board charts.
- | NICEIC completion certificate
- | Emergency Lighting Certification
- | Fire Detection Certification
- | BS 6701 certificate.
- | Category 6 data cabling test results.
- | All test results.
| SUBTOTAL |  |  | 0

## (E1) Handover
Activity Schedule for:
Earlsdon Park, Coventry, Office Refurbishment
Suppliers, please note: You only need to complete the cells in Blue, all Blue cells must be completed.
Ref | Work Description | Quantity | Rate (£/P) | Total Cost (£/P) exc. OHP and VAT Please note: If £0.00, please state the Item that this cost has been allowed within e.g. Section 1C, A etc.
E | HANDOVER
1.0.0 | GENERAL ITEMS
1.0.1 | On completion of the entire installation or any completed section thereof, tests shall be fully tested and commissioned in accordance CIBSE commissioning codes and relevant guidance documentations and industry standards.
1.0.2 | The contractor shall supply all necessary instruments and labour for these tests and shall, at his own expense, prove the accuracy of the instruments.
1.1.0 | VERTIFICATION OF THE TESTING AND COMMISSIOING BY THE PM
1.1.1 | The contractor shall include for all necessary attendance for the verification of testing & commissioning results by the PM
1.2.0 | DEMONSTRATION TO CLIENT
1.2.1 | The contractor shall allow for carrying out verification of the installed systems to the project manager and / client(s) representative and demonstration of the installed system to client / end user including all necessary training.
1.3.0 | CLEANING UP ON COMPLETION
1.3.1 | All areas are to be thoroughly deep cleaned upon completion of the works, care is to be taken around the existing floor
2.0.0 | OPERATION AND MAINTENANCE MANUALS
2.0.1 | The record information shall be prepared in accordance with the requirements of the specification and all services shall be treated as if new. Therefore, the installation being retained shall be provided with operating and maintenance instructions and detailed on the record drawings.
2.0.2 | Record drawings shall be prepared using Auto CAD computer software and a CD containing the O&M’s.
2.0.3 | The complete documentation required at handover, shall include all certificates and incorporate all services.
2.0.4 | The contractor shall provide operating and maintenance manuals which incorporate all the elements of the electrical and mechanical installations as detailed in this specification.
2.0.5 | Unless otherwise agreed, the whole or part of the Contract Works will only be deemed to be complete when the Contractor has issued to the Engineer three copies of all manuals and operating and maintenance instructions in stiff backed ring binders.
2.0.6 | Two proof copies of the manuals shall be issued to the Engineer for comment of format and general content, before the above-mentioned final issue. The proofs for comment shall be sent to the Engineer in sufficient time to allow him fourteen days for comments.
2.0.7 | The operating manuals shall contain the following sections. The bullet pointed details are intended to provide direction as to each sections content and are not an exhaustive lists:-
2.1.0 | Front Cover/Title Page
2.1.1 | Site Details, Contractor details, handover date, defects period details.
The front cover and title page should not contradict each other.
Contents list.
An overall contents/index list for the file.
If sub sections with a lot of elements have indexes, ensure these elements be easily referenced and found.
2.2.0 | Introduction
2.2.1 | This shall include an overview of the main stakeholders (client, contractor, main sub-contractors).
This shall include an overview of the installations, sufficient to identify what kind of systems are installed.
Terms of appointment shall be detailed.
Contact details
The contact details for all the stakeholders shall be listed as should the details for any sub-contractors, suppliers and/or manufacturers (if not located elsewhere).
Details shall include, name, address, tel and Email.
2.3.0 | Operation Instruction
2.3.1 | This shall provide the full detail as to how the installations are operated and should be aimed at the FM staff. Typically this will be the manufacturer’s booklet.
2.4.0 | Maintenance Schedule/service guide
2.4.1 | A schedule of what maintenance is required and how frequently should be provided for each item/installation. I.e. daily, weekly, monthly yearly.
2.4.2 | It shall also include the detail around what is included in each maintenance activity.
2.5.0 | Equipment Schedule
2.5.1 | This is a list of the entire installed plant, detailing, make, model, serial No, quantity etc.
2.6.0 | Technical/Manufacturers literature
2.6.1 | This is the literature supplied by the manufacturers.
2.7.0 | Basic Fault finding
2.7.1 | The detail for this should be sufficient to allow FM staff to fault find to a reasonable level without needing to call in specialists.
2.8.0 | Emergency Procedures
2.8.1 | These procedures are around actions to be done to the installation and how staff should react in certain circumstances. And is not first aid details.
2.9.0 | Testing/Commissioning sheets/certificates
2.9.1 | There shall be testing certification and/or commissioning details for every installation.
2.10.0 | Spare Parts Lists
2.10.1 | A list of what spares will be required for 12months of operation. This may include a requirement for additional spares if detailed in the specification. It shall include a brief overview of the HSAW act.
2.11.0 | Log Books – Fire/Lighting, Electrical
2.11.1 | Details of the requirements for the respective log books and how they should be completed.
2.11.2 | Applicable standards/regulations/codes of practice.
2.11.3 | A list of all relevant standards and regulations, split by installation.
2.12.0 | As-Installed Record Drawings
2.12.1 | Record drawings shall be completed in accordance with the relevant technical memorandum and standards.
2.12.2 | Unless otherwise agreed, the whole or any part of the Contract Works will only be deemed to be complete when the Contractor has issued to the Engineer the final "as-installed" drawings and diagrams. These shall consist of three paper prints and one black line negative and two sets of discs for CAD.
2.12.3 | All record drawings shall be produced on CAD using AutoCAD dwg format.
2.12.4 | Two paper prints of the "as-installed" drawings and diagrams shall be issued to the Engineer for approval of format and general content, before the above-mentioned final issue. The prints for approval shall be sent to the Engineer in sufficient time to allow him fourteen days for comment. The "as-installed" drawings and diagrams shall show the following in as far as they are the subjects of the Contract Works:-
2.12.5 | The location, including level if buried, of public Authority Supplies provided within this Sub-Contract whether carried out by the Sub-Contractor or by the appropriate Authority together with the points of origin and termination.
2.12.6 | Single line and schematic wiring diagrams for the whole of the Contract Works showing all terminal references and cable sizes.
2.12.7 | The layout, location and extent of all electrical plant, cable, cable tray, cable trunking, conduit, distribution board, switches, outlets and luminaires which form part of the Contract Works, including dimensioned layout of all concealed work.
2.12.8 | The layout, location and extent of all plant, cable, cable tray trunking, conduit, switches, outlets terminals and indicators, and alarms of all ancillary communication, detection alarm and control installations, which form part of the Contract Works, including, dimensioned layouts of all concealed work.
2.12.9 | The location and identity of each room or space housing plant machinery or apparatus.
2.12.10 | The detailed general arrangement, to one twentieth scale, of all boiler houses, machinery spaces, air handling plants, tank rooms, switch rooms, meter rooms and other plant spaces, including the location, identity, size and details of each piece of plant and equipment.
2.13.0 | Manufacturer's internal wiring diagrams for each piece of electrical equipment supplied under the Contract, together with physical arrangement drawings where necessary to locate and identify the component parts.
2.13.1 | The record drawings shall be prepared to the following scales:-
2.13.2 | Floor plans – 1:50/1:100
Floor sections – 1:50
Plant rooms – 1:20
Site plans – 1:200
Ductwork – 1:50 or 1:20
3.0.0 | HANDOVER DOCUMENTAITON
3.0.1 | Upon completion of the works, the Contractor shall hand over 3 No. Copies of an operating and maintenance manual which shall contain, but not be limited to, the following information:
3.0.2 | Emergency contact numbers
Procedures for fault finding
Emergency procedures.
System description.
Manufacturer’s maintenance instructions and contact details.
As fitted drawings.
Revised and new distribution board charts.
NIC/EIC completion certificate
COSHH Documentation
Laboratory Water Test Report
As fitted drawings
All test results.
3.0.3 | A copy of the manual and record drawings shall be provided electronically on CD-ROM.
| SUBTOTAL |  |  | 0