STP and associated pumps

Annual costs

Site No 	3			
Site Name: 5 The Crescent
Properties served: 1

Descriptions in this listing are abbreviated forms of the full description in paragraph 10 of Schedule 1 of the Conditions of Contract – The Services; the numbering also relates to that section.

| No | Description | Unit | Quant’y | Rate | £ | P |
| --- | --- | --- | --- | --- | --- | --- |
| 1) | Safety: Follow safety requirements specified and all other good working practices at all times. |  |  |  |  |  |
| 3(b) 4 (II) 4 (I) (c) 6) 4) (III) (b) | Six monthly: Inspect fencing and access roads for security and condition. Alert the Contract Administrator about any issues found. Check for rodents. Isolate electricity supply and remove covers: (i) Check appearance of internals and ensure that all retaining fittings are present and secure. (ii) Clear any debris from the inlet and outlet pipes and other areas of the mechanism where they may cause malfunction. (iii) Check the condition of any media mats, remove and clean as necessary. (iv) Reseed the plant as necessary (seeding media to be provided at the Association’s cost) (v) Replace covers and make secure. (vi) Reinstate electricity supply. (vii) Check noise of operation. Mechanical maintenance to be carried out as described in this section and in the datasheets and in accordance with the plant manufacturers’ recommendations where provided. Control Kiosk (a) All equipment must be isolated before any maintenance work is carried out. (c) Check and reset overloads. (e) Alert the Contract Administrator to recurrent issues, particularly, but not limited to, repeated needs to reset equipment and recurrent overloads. Pumps Pump pits to be opened and checked and pumps should be checked visually and audibly, pumps should be run manually to check operation and then be returned to auto mode, check hoses and pipework for wear and tear or damage. | Per visit Per visit Per visit Per visit Per visit | 2 2 2 2 2 |  |  |  |
| 4) (I) (b) 5) 4) (III) 6) | Quarterly: Oil all locks. Meter reading (a) Read and record the electricity meter. (b) Advise the Contract administrator of the latest meter reading, the previous quarter meter reading and the units consumed, drawing attention to excessively high or low consumption. Pumps (c) Lift floats as appropriate, clean and return. (d) Check greasers and replace as necessary. Control Kiosk (b) Inspect all cables and fittings. Check heater and thermostat setting where present. Check operation of indicators, lamps, lights and security of earthing straps. | Per visit Per reading Per Pump Per kiosk | 4 4 4 4 |  |  |  |
| 2) (a) 4) (I) (a) 6 (d) | Six monthly: The Contractor shall test earth continuity every six months in accordance with the plant manufacturers’ requirements and current IEE Regulations. Any electrical faults found that require urgent attention must be reported to the Contract Administrator the same day. Cleaning, washing down of exterior of plant and associated equipment housings. Clean the control kiosk, remove cobwebs and dirt and wash down exterior | Per test Per clean Per Clean | 2 2 2 |  |  |  |
| 3) (a) | Annually: Where rough cut grass is shown this shall be cut once a year in the autumn. All arisings are to be removed from the site and disposed of at a recognised tip and costs included in above items. | Per cut | 1 |  |  |  |
| 2) (b) | Three yearly: The Contractor shall arrange for periodic inspection and testing of all electrical installations (BS 7671:1992 as amended) and for issuing a copy of the Test Certificate to the Contract Administrator. This shall be undertaken in the third year of the contract. Certificates relating to the electrical installations at the commencement of the contract shall be available from the Contract Administrator. (Enter annual equivalent – 1/3 total cost) | 3 yearly inspection | 1/3 |  |  |  |
| 4) (II) (c) (i) 4) (II) (c) (ii) 4) (II) (c) (iii) | Desludging: Wastewater treatment work tanks are to be emptied by tanker at the frequencies indicated in the site datasheets and in accordance with the manufacturers recommendations. Annual volume shown. Emptying includes assessing general condition of tanks as far as is practicable from the surface through the following actions: (a) Carrying out all necessary safety precautions. (b) Checking condition of covers and frames. (c) Reporting any defects found to the Contract Administrator. (d) Break up surface crust, cleaning walls, weirs and channels. (e) Cleaning up any spillages and ensuring covers are replaced and any locking devices are in place before leaving site. Tanks are to be left with sufficient media to allow natural reseeding of the plant when put back into use. | Per litre Per inspection | 6800 2 |  |  |  |
| 4) (II) (c) (iv) | Jetting and refilling: Following emptying Sewage Treatment Plant the plant is to be jetted, washed down and partially refilled in accordance with manufacturer’s recommendations. | Per clean | 2 |  |  |  |
| 4) (II) (d) | Sampling (i) The Contractor shall undertake a programme of sampling and testing of final effluent discharged from wastewater treatment works (no sampling shall be undertaken within 48 hours of tank emptying). (ii) Samples shall be submitted for analysis to a laboratory accredited by the United Kingdom Accreditation Service (UKAS). (iii) Copies of test results shall be forwarded to the Contract Administrator within 3 working days of receipt by the Contractor. (iv) Attention should be drawn to any adverse test results or other results that may indicate a potential problem (v) Carry out onsite Palin test for clarity and alert The Contract Administrator to arising issues at the frequencies indicated in the site datasheets (or as directed by the Contract Administrator as an additional cost item). (vi) Repaint sample cover (every three years). (Enter annual equivalent – 1/3 total cost) | Per lab sample Per sample Per sample As required As required 3 yearly repaint | 4 4 4 1/3 |  |  |  |