## GENERAL
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item |  | Description | Quantity | Units | Rate
PART ONE - GENERAL SITE INFORMATION & PROTECTION
1.1 |  | General
1.1.1 |  | Programme: Construction period is to be 20 weeks.
1.1.2 |  | This project is notifiable under the Construction (Design and Management) Regulations 2015.
1.1.3 |  | All works described in this schedule of works to be read in conjunction with other requirements listed in the foregoing preliminaries, general conditions, material and workmanship clauses and specifications produced by other parties, which include:
| a) | Langley / Eco Green Roofs Green Roof Specification dated 12 January 2022.
| b) | Langley / Eco Green Roofs PV Specification dated 18 January 2022.
| c) | Langley Roof & Walkway & Balcony Specification Rev. 2 dated 25 February 2022.
| d) | Dulux Paint Specification dated 15 Feb 2021.
| e) | Sika Anti-Carbonation Specification dated 17 January 2022.
| f) | RBKC Lighting Specification - Employers Requirements Communal & Emergency Lighting General Specification
| g) | Langley / Eco Green Roofs Irrigation Specification Requirements.
1.1.4 |  | Where approximate quantities are stated, the price shall be deemed to have been computed pro rata to the quantity stated and unless stated otherwise in the description to include for executing the work in large or small quantities and difficult or easy situations in isolated areas or otherwise. Approximate / provisional quantities will be re-measured and may be omitted in whole or in part if not required.
1.1.5 |  | The contractor is to price all sections of this specification. No costs will be accepted on the basis of works being omitted.
1.1.6 |  | The scope for painting and redecoration work to include for all preparation (including filling cracks, making good indentation, sanding out imperfections to existing paintworks etc.) and cleaning work as specified within the works.
1.1.7 |  | The contractor is to ensure that all works are installed in accordance with all current regulations.
1.1.8 |  | The design, materials and workmanship are to be in accordance with good building practice, up to a standard appropriate to the works and shall meet the general standards indicated below:
1.1.9 | a) | British Standards and BS Codes of Practice, Latest Editions and/or Amendments.
| b) | Building Regulations and Local Authority Building Control Requirements.
| c) | Fire Officers Requirements.
| d) | Conditions of the Planning Approval issued by the Local Authority.
| e) | The Construction (Design & Management) Regulations COSHH and any other Public Health and Health & Safety Executive Requirements.
| f) | Design Guides and Technical memoranda published by the Chartered Institute of Building Services Engineers.
| g) | The Institute of Electrical Engineers Wiring Regulations 17th Edition (BS 7671) including all amendments to date.
| h) | All other enactments or local Bylaws issued or relevant to the construction at the prescribed date.
1.1.10 |  | The duration of the current working restrictions are subject to change, and the Contractor is to fully follow all government COVID-19 guidelines and to take additional precautions and guidance as outlined relevant to the work scope, allowing for costs that may arise relative to pricing of issues associated with the site welfare and working practices, including the Construction Leadership Council - Sie Operating Procedures guidance document contained within Appendix G of the Tender Document, or any later version that has since been published.
1.1.11 |  | The Contractor may propose an 'equal' product for consideration by the project team for approval (equal and approved). No products differing from the schedule of works / specification shall be installed without the prior formal instruction by the Contract Administrator.
1.1.12 |  | The Contractor is reminded of their responsibility to recycle waste materials where possible, utilise licensed land fills to dispose of non-recyclable waste and generally perform in a manner which considers the natural environment and sustainability. Waste transfer notes are to be provided to the Contract Administrator at the end of the project.
1.2 |  | Existing Site, Procedures & Site Set Up
1.2.1 |  | The site comprises a single block of flats. The building will be occupied throughout the construction period and therefore works will need to be coordinated throughout in order to ensure that access is maintained for occupiers, council workers and emergency workers.
1.2.2 |  | The Contractor should make himself aware of the uses of the adjacent buildings, particularly in relation to delivery and removal of materials/waste from the site and works being undertaken.
1.2.3 |  | The Contractor is to make his own assessment of additional facilities, site storage required and to verify the proposals for the site set up when submitting the tender.
1.2.3 |  | All areas accessed by, used by and worked in must be kept clean and tidy by the Contractor.
1.2.4 |  | The Contractor is to allow for all temporary signage, protection, barriers and the like as deemed necessary to carry out the works in a safe manner.
1.2.5 |  | The Contractor is to install weighted 2m high Herras fencing in front of the entire site to prevent unauthorised access to the site.
1.2.6 |  | The Contractor to allow for all temporary lighting as required to ensure the works are undertaken in a safe manner.
1.2.7 |  | The Contractor is to allow for necessary temporary supports during the works.
1.2.8 |  | The Contractor is able to use the existing hard standing areas (the courtyard) for deliveries and/or siting of site accommodation to incorporate a site compound. The landscaped areas must not be used. The Contractor is to provide proposals for the location of site accommodation, welfare, materials, compounds, hoardings, scaffolding and any major plant. The locations proposed must ensure that safe access is maintained to all residents' car parking areas and pedestrian footpaths etc. The compound area is to also be secured with 2m high Herras fencing and kept secure to prevent unauthorised access.
1.2.9 |  | The Contractor is required to bring portable toilet facilities to the site and position within the agreed site compound. Facilities are to be regularly cleaned/emptied no less than prescribed in BS6465-1-2006.
1.3 |  | Working Hours & Noisy Works
1.3.1 |  | The works are to be completed during normal working hours of 8:00am - 5:00pm Monday to Friday. The Contractor must confirm to the Contract Administrator if they need to work outside of these hours and is to give 48 hours notice and receive Contract Administrator approval before commencing any weekend works. The Contractor is to adopt that all noisy works must comply with all local authority restrictions and should familiarise themselves with these rules.
1.3.2 |  | Noisy works are only permitted between the hours of 9.00am to 12.00 midday and 2.00pm to 4.00pm. Refer to RBKC Code of Construction Practice document for guidance on permissible noise and parameters for noise and vibrations alike. NOTE: - Document Link: https://www.rbkc.gov.uk/environment/advice-builders/code-construction-practice
1.4 |  | References & Measurements
1.4.1 |  | The Contractor is to reference the items of work scheduled herein, and all information contained in the Appendices.
1.4.2 |  | All dimensions stated in herein are approximate measurements only and must be confirmed on site by the Contractor when pricing works based upon this information. The Contractor should check floor areas and any dimensions shown on drawings.
1.5 |  | Schedule of Condition
1.5.1 |  | Prior to the commencement of the works, the Contractor is to prepare a detailed Written and Photographic Schedule of Condition of all areas internally and externally including areas of access, site welfare, materials storage, etc. and forward a copy to the Contract Administrator. This is to be provided to the Contract Administrator a minimum of 1 week before the works commence.
1.6 |  | Statutory Approval
1.6.1 |  | The Contractor is to arrange all Building Control applications as per the required intervals to be provided. The Contractor is to ensure that all information is provided along with access for any inspections. It will be the Contractors duty and responsibility to procure and comply with any other statutory consents that may be required for the completion of the works.
1.6.2 |  | The Contractor must make all allowances for safeguarding the work areas, including preventing access to the scaffolding, whilst maintaining sufficient safe access for pedestrians in accordance with the Local authority guidelines, including any application for any Licences as may be required and for payment of charges associated.
1.7 |  | Asbestos
1.7.1 |  | Before any Works commence, the Contractor must make themselves familiar with the content of the asbestos survey reports contained within Appendix I and subsequent Refurbishment/Demolition Survey which will be provided prior to the works and in due course. If required, the Contractor is to provide a cost to safely remove any asbestos identified.
1.7.2 |  | The Contractor should be aware that the Employer will directly appoint a Specialist Asbestos Contractor to strip out all ACM’s throughout the property, including all common areas and the individual flats. Contractor Note: All occupants will remain in occupation during the works and the Contractor should be aware that the asbestos removal works will be undertaken at the same time as the repair & redecoration works. A Specialist Asbestos Consultant directly employed by the RBKC will be responsible for overseeing the works carried out by specialist asbestos Contractor and for ensuring that they are carried out as per their specifications including the provision of all necessary paperwork and certificates etc.
1.8 |  | Health & Safety
1.8.1 |  | The Contractor is required to provide a copy of the Construction Phase Health & Safety Plan, two weeks prior to commencement of the works, for Principal Designer approval and to update as the works progress.
1.8.2 |  | The Contractor is to review existing electrical certificates and ensure that the distribution board is in a safe and maintained condition before carrying out any electrical works.
1.8.3 |  | The Contractor shall ensure that adequate Health & Safety precautions, complete with suitable signs and notices, are maintained throughout the duration of the works to protect the existing staff, visitors and public and to keep them away from the works.
1.8.4 |  | The Contractor is to fully consider the potential existence of lead based paint and is to allow for all necessary precautions to ensure health and safety of occupants, workers and neighbouring parties. All included additional costs are to be priced within this item or broken down as required by the Contractor under respective pricing items.
1.9 |  | PPE
1.9.1 |  | The Contractor will be required to wear PPE to include hard hat, high visibility vest and safety boots. Additional PPE to be used when required based upon risk assessments.
1.9.2 |  | On site PPE for the Client & CA is to be provided by the Contractor. Allow to provide for minimum of 5no. visitors at any one time.
1.1 |  | High Level Access
1.10.1 |  | The Contractor is to allow for high level access equipment to undertake the scheduled works. Ladders are not considered as a working platform and may only be used for access.
1.10.2 |  | The Contractor is to make himself aware of the general working of the site, adjacent users, particularly in relation to delivery and removal of the materials/waste form site. The Contractor is to provide a method statement for all high level works.
1.10.3 | a) | Scaffolding - Provide and erect all necessary scaffolding to enable the works to be carried out in accordance with NASC TG20:13. Provide suitable compliance sheets or otherwise confirm detailed design of scaffold proposals to the Contract Administrator a minimum of two weeks prior to the works which must be designed by a competent person, by bespoke calculation and in accordance with BS EN 12811-1:2003.
| b) | All scaffold lifts are to be double boarded with polythene sheeting between.
| b) | Install a fire resistant monarflex sheeting to all elevations of scaffold.
| c) | Install a suitable lighting system and as required to be in accordance with Chapter 8 the local authority and a security alarm by Panthera Group, which is to be manned/monitored 24/7 by the appropriate monitoring station.
| d) | Allow for any and all required Chapter 8 signage and lighting for scaffolding that affects any roads or footways.
| e) | When installing scaffolding, ensure a banksman is appointed and appropriate diversion signage along pathway (where appropriate) is provided. Allow for any local authority licences for any road or path closures for the duration of the scaffold installation.
1.11 |  | Meter Readings
1.11.1 |  | The Contractor is to record the meter readings prior to works commencing and again on completion (including electrical, water and gas where applicable).
1.12 |  | New Installations
1.12.1 |  | The Contractor is to check the availability and adequacy of all specified works during the period between instruction and start on site and advise the Contract Administrator of any specified products which: - Have been discontinued. - Have long lead in periods. - Cannot be installed due to site confinements. NOTE: No claims will otherwise be supported in these respects.
1.13 |  | Manufacturers Instructions / Recommendations
1.13.1 |  | In all cases where products and manufacturers have been specified the Contractor is to install these products in accordance with the manufacturers instructions and recommendations. It is the Contractors responsibility to liaise with the representatives of the specified companies to ensure that they are fully familiar with the product and the requirements together with appropriate tolerances for installation. The Contractor should obtain 'approvals' or similar certification of works where available.
1.13.2 |  | In the event of any discrepancies existing between the manufacturers recommendations, British Standards and this tender document such discrepancies are to be brought to the attention of the Contract Administrator immediately and the more onerous requirements deemed to be included. The works must also comply with the Building Regulations whether or not a formal application is required.
1.13.3 |  | The Contractor is responsible for registering any product guarantees or manufacturers warranties in favour of the employer.
1.13.4 |  | In the event of any confusion regarding the specification or installation of a manufacturers product the Contractor is to seek the advice of the Contract Administrator.
1.14 |  | Resident Communication
1.14.1 |  | A Resident Liaison Officer (RLO) will be assigned to the project and the Contractor is required to have regular communication between the RLO, the CA & RBKC to ensure the works and issues raised are communicated between the residents and the RLO and the Contractor in a timely manner. At no point is the Contractor to take formal instructions from the RLO. The Contractor will be required to attend regular meetings with the RLO.
1.14.2 |  | The Contractor will be required to provide a 1-page letter drops every Friday, briefly explaining: - works completed this week. - works scheduled for following week. - pictures of works progressing.
1.14.3 |  | An application for the residents will be in place during the work. The Contractor is asked that they be a part of the application to upload relevant (non-sensitive) project information during the project. Any uploads will need to be prior vetted by RBKC for approval.
1.15 |  | Schedule of Amendments
1.15.1 |  | Contractor is to make full due allowance for the Schedule of Amendments supplied as part of the tender documents, which will form the contract particulars.
1.16 |  | Collateral Warranties
1.16.1 |  | Contractor is to make full due allowance for providing collateral warranties for both main contractor and sub-contractor, refer to specimen supplied as part of the tender documents, which will form the contract particulars.
1.17 |  | Parent Company Guarantee
1.17.1 |  | Contractor is to make full due allowance for providing a Parent Company Guarantee, refer to specimen supplied as part of the tender documents, which will form the contract particulars.
1.18 |  | Bonds
1.19.1 |  | Contractor is to make full due allowance for providing a Performance Bond. An RBKC specimen is provided in the tender documents and will form part of the tender documents, therefore forming the contract particulars. Contractor is to stipulate the cost of obtaining a Performance Bond.
1.18.2 |  | Contractor is to make full due allowance for providing an Advance Payment Bond. The bond is required if advance payment for placing order of windows is deemed required. The bond value will need to amount to £400,000.00. The Contractor is to stipulate the cost of obtaining a Advance Payment Bond.
1.19 |  | Maintenance Aftercare
1.19.1 |  | The Contractor is to include a 12 months maintenance programme for the Green Roof & Solar PV install as part of the tender bid. They will be required to carry out full maintenance works in line with the manufacturers / suppliers guidance. Details of this aftercare cover is to be documented in their tender bid and covering letter. An example of he maintenance requirements and further Guarantee of Function of system is outlined in Appendix T.
1.19.2 |  | It is noted that the following maintenance is provided by Langley / EGR with their systems listed:
| a) | Langley TA30 Roofing System - Free 5-year maintenance aftercare included.
| b) | Langley / EGR Sedum Green Roof System - Free 1-year maintenance aftercare included.
| c) | Langley / EGR Solar PV System - Free 2-year maintenance aftercare included.
1.2 |  | Firm Costs
1.20.1 |  | The Contractor is to ensure all costs provided are firm costs and no sums provide are to be provisional sums, unless otherwise already included as a provisional sum. No provisional sums will be permitted to be included and may result in a non compliant tender bid.
1.21 |  | Fire Engineer - Construction Phase Fire Strategy Plan
1.21.1 |  | The Contractor is to allow to engage directly with the Employers Fire Engineer, Trigon Fire Safety. Contractor is required to subsequently appoint Trigon Fire Safety to prepare together a suitable Construction Phase Fire Strategy Plan, considering how the works are being completed, in line with the exiting Fire Strategy, that Trigo Fire Safety are preparing for the building. NOTE: Please acknowledge this requirement and all above general conditions and preliminaries, which will form the Contract.
TOTAL PRELIMINARIES |  |  |  |  | 0

## External Elevations & Areas
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item |  | Description | Quantity | Units | Rate
PART TWO - THE WORKS
2 |  | General
2.0.1 |  | In broad terms, the works are as detailed below: 1. New SBS Roof. 2. New Sedum Green Roof. 3. New PV System. 4. New Windows & Doors. 5. Repair masonry, including brickwork replacement, crack repairs and mortar repairs. 6. Install proprietary movement joints to parapets. 7. Replace damaged lintels. 8. Repair concrete with anti-carbonation coatings. 9. Decorations to communal areas. 10. New lighting to communal areas. 11. Drainage repairs.
2.0.2 |  | The below are considered the Contractors Design Portion elements:
a) |  | Basement Staircase Structural Plate Repair
b) |  | Mastic Asphalt Works
b) |  | Lintels
c) |  | Windows & Doors
d) |  | Concrete Roof Tower Slabs
e) |  | Solar PV
f) |  | Communal Lighting
g) |  | Tarmac Pathway Extension & Accessible Ramp.
EXTERNAL ELEVATIONS
2.1 |  | Masonry Repairs
General
2.1.1 |  | Brickwork that is being replaced is to match the existing bricks in size, colour and style. The Contractor is to allow to supply the Contract Administrator with a sample brick for approval prior to the works. NOTE: The Contract Administrator is to be fully satisfied with the match and will consult with the Employer for their approval.
2.1.2 |  | Prepare Mortar Joints - Prepare existing brickwork by raking out loose and defective areas or missing mortar, ready for repointing. Raking out must be by hand tools and to a depth of between 20mm (absolute minimum) and must be to the whole width/height of the joint. Allow 600m2 of brickwork throughout, including all access required. Any further repointing works is to be calculated on a pro rata basis.
2.1.3 |  | New Mortar - Rake out and repoint as above to all affected loose, eroding or missing areas. Use a 1:1:6 pre-mixed Type S mortar in pointing style to match existing with below mix: - 1 part OPC (Ordinary Portland Cement - 1 part fresh Hydrated Lime - 6 parts aggregate made up of 3 parts coarse and 3 parts fine sand. Note: All aggregate must be washed (do not use ordinary unwashed soft builders sand). Mortar must not be used too wet and must not be smeared over the arris or face of the bricks. Joints should be slightly brushed back to expose the aggregate. Note: Colour to match existing mortar finish on main elevations. The colour of mortar should only be achieved by the colour of sand and not by artificial colouring agents. Note: The pointing style is to be shown on a sample panel in a discreet location should be chosen. Allow to repoint 600m2 of brickwork throughout, including all access required. Any further repointing works is to be calculated on a pro rata basis.
a) |  | Allow to carry out a small sample patch re-pointing repair, in a discreet location to be agreed with the Contract Administrator. The pointing is to cure and be reviewed to satisfied with the repointing style and colour match.
2.1.4 |  | Cleaning Brickwork: Water and brush clean all existing brickwork; building complete including inside face of walkways; stair towers; chimney stacks etc.
2.1.5 |  | Repair Damaged Brickwork: Carefully cut out defective or spalled bricks; replace with reclaimed facing bricks in mortar; pointing; all to match existing as above mortar. Allow to replace 800Nr of bricks throughout, in various locations; including all access and temporary works required. Any further replacement brickwork is to be calculated on a pro rata basis. Contractor will be required to mark on elevation plans the areas where brickwork are proposed to be replaced
2.1.6 |  | Stitching Cracked Brickwork: Central Roof Tower: Where there is thermal cracking to the central roof tower, repair with austenitic Helifix Helibar stainless steel bars, Stitches are to be chased in 500mm either side of cracking and to be stainless steel Grade 304 bars. Chase grooves for repair with either twin-bladed cutter with vacuum attachment or angle grinder or hammer and mortar chisel. Use HeliBond grout to secure steel bars. Install in accordance with Helifix manufacturers instructions. On completion, carry out repointing as described above.
2.1.7 |  | Stitching Cracked Brickwork: 1st Floor Communal Balcony: Where there is thermal cracking to the following: - Flat 15 side of archway. - Flat 15 between windows at slab joint over. - Flat 16 between windows at slab joint over. Repair with austenitic Helifix Helibar stainless steel bars, Stitches are to be chased in 500mm either side of cracking and to be stainless steel Grade 304 bars. Chase grooves for repair with either a twin-bladed cutter with vacuum attachment or angle grinder or hammer and mortar chisel. Use HeliBond grout to secure steel bars. Install in accordance with Helifix manufacturers instructions. On completion, carry out repointing as described above.
2.1.8 |  | Repair Cracked Brickwork: Where there is cracking, particularly at parapet level; replace brickwork by stitching in new facing bricks of a type that match existing; repoint; all to match existing; various areas throughout the building. Allow to replace 200Nr of bricks, in various locations; including all access and temporary works required. Any further replacement brickwork is to be calculated on a pro rata basis.
2.1.9 |  | Coping Stone Repairs - Allow to cut out and remove sections of concrete coping stones to balconies where spalling. Allow to replace 6no. corner coping details, which will include careful removal around metal handrails. Provide new concrete copings to match existing dimensions. As required cut coping stoned around embedded steel posts and reseal. Allow to carry out localised repairs / corrosion treatment works to the embedded steel upright sections below coping junctions.
PARAPET WALLS
2.2 |  | Raising the Parapets
2.2.1 |  | Raising Brick Courses - Preparation - Prior to raising parapet walls, allow to carefully remove concrete coping stones and storing for reinstatement. Clean off bedding joints, leaving ready to receive new brick courses.
2.2.2 |  | Raising Brick Courses - Lay new brickwork to raise parapet heights approx. 230mm on all parapets to the roof areas. Contractor is to assess and ensure the parapet heights are 1.1m from finish floor level as per the requirements of Building Regulations. The Contractor is not to raise the parapet height more than 250mm and where this may be required, first consult with the Contract Administrator for consideration by the Structural Engineer on loading issues.
2.2.3 |  | Pointing Raised Parapet - Repoint raised parapet areas and refer to item 2.1.3 above for repointing requirements.
2.2.4 |  | Coping Stones - Lift all copings and on completion of the above, lay DPC and lay over support, whether cavity tray/closer or other. Supply and install a stainless still anchoring dowel system with sealant. Provide continuous sealant and coping joints. Rebed coping stones with Type S bedding mortar to base and sides of copings.
2.2.5 |  | Coping Stones over Movement Joints - At all existing and newly created movement joints, lift copings and as required, replace any copings required to form and terminate over movement joints. Relay new and existing copings with new DPC to base. Supply and install a stainless still anchoring dowel system with sealant. Provide continuous sealant and coping joints. Rebed coping stones with Type S bedding mortar to base and sides of copings.
2.3 |  | Parapet Repairs
2.3.1 |  | Prepare Movement Joints - At all areas of displaced brickwork, where post-installed movement joints are present and where cracking has occurred at the re-entrant corners, carefully remove brickwork to allow to rebuild with soft joint and debonded movement wall ties. At 2no. re-entrant corners, create new vertical movement joint where cracking has occurred, ensuring all movement joints are 10mm wide.
2.3.2 |  | Install Movement Joints - Supply and install Ancon PPS, 225mm wall tie with debonding sleeve to the following locations; - Courtyard South, - Courtyard East x 3 (included 2no. re-entrant corners), - Courtyard North, - West x 4Nr. Ancon PPS, 225mm wall ties with debonding sleeves are to be installed at 450mm vertical centres. Debonding sleeves are to be pulled back 10mm to allow expansion as well as contraction of brickwork. Debonded ties to have 100mm embedment.
2.3.3 |  | Soft Movement Joint - Supply and install Sika SikaHyflex®-250 Façade high performance movement joint to parapet joints. Ensure the substrate is clean, dry, sound and homogeneous, free from oils, grease, dust and loose or friable particles and prepare joints as required. After the necessary substrate preparation, insert a suitable backing rod/compressible filler to the required depth and apply any primer if necessary. Insert a foil pack or cartridge into the sealant gun and extrude SikaHyflex®-250 Facade into the joint making sure that it comes into full contact with the sides of the joint and avoids any air entrapment. SikaHyflex®-250 Facade must be firmly tooled against the joint sides to ensure adequate adhesion. Use masking tape where exact joint lines or neat lines are required. Remove the tape within the skin time. Use a compatible tooling agent (e.g. Sika® Tooling Agent N) to smooth the joint surfaces. Do not use tooling products containing solvents.
SLABS, BALONIES, SOFFITS & WALKWAYS
2.4 |  | Concrete Repairs - Sika
2.4.1 |  | Refer to Sika Specification found in Appendix J.
a) |  | Contractor is also to refer to damage observed and noted in Structural Engineers report and therefore application of repairs are limited to those areas of damage which are identified. The Contractor is to confirm if there are any additional areas of damage and include with the below repair methodology.
2.4.2 |  | General - Repair and Protective Material Selection/Compliance In all cases the Contractor shall provide manufacturers’ evidence to verify that they meet the requirements set out in BS EN1504 and as such all materials where relevant should be ‘CE’ marked. All materials must be compatible and shall not have any effects on long term durability and bond. The materials must be supplied from a BS EN 1504 approved manufacturing plant and supplied from a single manufacturer to ensure compatibility and ensure long term durability. For individual product application requirements refer to current Product data sheet.
2.4.3 |  | Preparation - CONCRETE SUBSTRATE QUALITY AND PREPARATION
a) |  | Coated Concrete Surfaces (Remain) If it is deemed that existing coatings are to be overcoated rather than removed, then compatibility testing between existing coating and new Sika® coating system together with additional tests outlined below should be undertaken prior to proceeding with the works. However, it should be borne in mind that failure to remove existing coatings may lead to an increased risk of technical compromise. Before proceeding, trial results must be interpreted by the Contract Administrator. Sika Limited is not responsible for failures related to the underlying coating.
b) |  | Existing Coatings Existing coatings must be tested to confirm their suitability. For existing coatings to be considered for overcoating with Sika® coating, all test criteria from the Dry Cross- Cut Tests & Adhesion Tests shall be satisfied as stated below.
c) |  | Dry Cross-Cut Test Carried out in accordance with BS EN ISO 2409 At least 2 cross-cut tests need to be performed for each zone to be assessed. The results shall be interpreted as acceptable if they achieve: GT O, 1 or 2.
d) |  | Adhesion Test Carried out in accordance with BS EN 1542 At least 5 pull off tests shall be performed per zone. The results shall be considered as acceptable if they achieve the following: Crack-Bridging/Flexible Systems: Adhesion test average > 0.8 N/mm2 ( MPa) with no single value below 0.5 N/mm2 (MPa) or cohesive failure in the substrate. Rigid Systems: Adhesion test average > 1.0 N/mm2 ( MPa) with no single value below 0.7 N/mm2 (MPa) or cohesive failure in the substrate. All testing shall be carried out using an accredited testing house.
e) |  | Existing Coatings and new Sika® Coating System Wait at least 2 weeks prior to conduct Dry Cross-Cut Test and Adhesion Tests. All acceptance criteria mentioned for existing coatings apply for the existing coatings and new Sika® coating system. Thickness of existing coating shall also be assessed to ensure full system of existing and new coatings do not exceed requirements for permeability to water vapour SD< 5.0m to prevent water vapour build up, condensation issues and possible coating system failure.
f) |  | Failure to carry out any of the above compatibility, cross cut and adhesion tests will invalidate any guarantee. By suitable means, remove all delaminating coatings (and exposed laitance) back to a firmly adhering edge to the approval of the Contract Administrator. Remaining coatings must be cleaned by high pressure water jetting or blast cleaning to remove all surface contaminants such as grease, dirt, etc, prior to overcoating. The resultant surface should be sound, clean and stable, with all defective locations exposed for attention. Prior to the application of Sikagard coatings, to improve adhesion, use one coat of Sikagard®-552 W Aquaprimer applied by brush or roller at a consumption rate of not less than 0.2 ltr/m² on top of water based coatings or Sikagard®-551S applied by brush or roller at a consumption rate of not less than 0.2 kg/m² on top of solvent based coatings. If original type of coating is unknown, conduct trials with primers and Sikagard® coating to ensure compatibility and acceptable cross cut and adhesion values. A trowel applied re- profiling mortar of Sikagard®-545W Elastofill and 20% by weight of 0.1- 0.3 mm kiln dried quartz sand should be used to re-profile and fill any remaining blowholes on the concrete coated surface prior to using a water based Sikagard® Anti – Carbonation coating.
2.4.4 |  | CONCRETE REMOVAL
a) |  | After removal of defective concrete, the prepared area shall be free from dust, loose material, surface contamination and materials which reduce bond or prevent suction or wetting by repair materials. Delaminated, weak, damaged and deteriorated concrete and where necessary sound concrete shall be removed by suitable mechanical or very high pressure water blasting (up to 110 MPa / 16500 psi) techniques. Tying wire fragments, nails and other metal debris embedded in the concrete should be removed where possible. The edges where concrete is removed should be cut at a minimum angle of 90o to avoid undercutting and a maximum angle of 135o to reduce the possibility of debonding with the top surface of the adjacent sound concrete and should be roughened sufficiently to provide a mechanical key between the original material and Sika concrete repair mortar. Ensure sufficient concrete is removed from around the reinforcement to allow application of the reinforcement corrosion protection coating and compaction of the repair material.
2.4.5 |  | PREPARATION OF STEEL REINFORCEMENT
a) |  | Rust, scale, mortar, concrete, dust and other loose and deleterious material which reduces bond or contributes to corrosion shall be removed to a minimum standard of SA2 or SA2½ depending on the reinforcement corrosion protection coating used. The whole circumference of the exposed reinforcement shall be uniformly cleaned, except where structural considerations prevent it. Unless the cleaning is carried out immediately before application of the reinforcement corrosion protection coating, the reinforcement shall be protected against further contamination. Surfaces should be prepared using abrasive blast cleaning techniques or high pressure water blasting techniques. Method and choice of cleaning shall take into account bar congestion, contact between bars, proximity to concrete substrate and other factors which prevent access for cleaning. Where exposed reinforcement is contaminated with chloride or other material which may cause corrosion, the reinforcement shall be cleaned by low pressure water blasting techniques to wash away contaminants. If environmental constraints preclude the use of abrasive or water blasting preparation techniques and where corrosion has been induced by carbonation and ingressed chlorides are not present. The following preparation maybe adopted.
b) |  | Rust, scale, mortar, concrete, dust and other loose and deleterious material which reduces bond or contributes to corrosion shall be removed to a minimum standard of C St 3 as defined in BS 7079: Part A1.The whole circumference of the exposed reinforcement shall be uniformly cleaned except where structural considerations prevent it. Final surface condition should have a faint metallic sheen finish. Unless the cleaning is carried out immediately before application of the reinforcement corrosion protection coating, the reinforcement shall be protected against further contamination. Steel preparation maybe carried out by removing loose rust by very thorough scraping, hand or machine wire brushing, abrasive paper/cloth, grinding or other appropriate techniques to achieve the required final surface condition. Method and choice of cleaning shall take into account bar congestion, contact between bars, proximity to concrete substrate etc. After removal of the rust to the required standard. Clean the steel reinforcement with a dry clean brush. Where a guarantee is required for the project. Sika® Galvashield XP Compact galvanic anodes should be installed into repair areas where the above preparation has been undertaken.
2.4.6 |  | REINFORCEMENT CORROSION PROTECTION COATING APPLICATION
a) |  | (BS EN 1504-7 Classification) Immediately after preparation to Sa 2 or other specified preparation standard specified in this document, apply to the whole exposed circumference of reinforcement, two coats of Sika MonoTop 1010. Wait until the first layer has dried before applying second layer. Allow to harden before applying repair mortars.
2.4.7 |  | REPAIR MORTAR APPLICATION
a) |  | Structural repairs Hand Applied (BS EN 1504-3 Classification R4) Before applying the concrete repair mortar, apply a bonding primer of Sika® MonoTop-610/1010. Pre-wet the surface of the prepared repair area. The surface should not be allowed to dry before application of the bonding primer. The pre-wetted surface should achieve a dark matt appearance without glistening and surface pores and pits should not contain water. Apply the pre-mixed Sika® MonoTop-610/1010 to pre-dampened repair substrate at a thickness of >1.0mm.
b) |  | Apply pre-mixed Sika® MonoTop-4012 repair mortar “wet on wet” onto the bonding primer between the minimum and maximum layer thicknesses and compacted without inclusion of entrapped air pockets using a trowel or gloved hand. Where layers are to be built up to prevent sagging or slumping, each layer should be allowed to harden and exothermic reaction of the material completed. The first layer shall be at ambient temperature before applying the second layer. Do not smooth the first layer before applying a second layer. The first layer should have sufficient roughness to provide a mechanical key for subsequent mortar layers. Finishing of the applied repair mortar should be carried out to the required surface texture as soon as the mortar has started to stiffen. To prevent surface cracking, do not apply water or overwork the surface with finishing tools. Site adhesion values to comply with BS EN 1504-3: Structural Repairs: Class R4 > 2.0 N/mm2 (MPa). Class R3 > 1.5 N/mm2 (MPa). Non Structural repairs: Class R1 & R2 > 0.8 N/mm2 (MPa)
2.4.8 |  | CURING TREATMENT
a) |  | It is essential to cure the repair mortar immediately after application for a minimum of 3-7 days depending on site exposure and weather conditions, to ensure full cement hydration and to minimise cracking. Use polythene sheeting taped down at the edges or other approved method. Curing compounds shall not be used if subsequent smoothing coats/pore filling or protective coatings are to be used.
2.4.9 |  | SMOOTHING COAT APPLICATION
a) |  | Surface preparation should have been carried out in accordance with concrete substrate quality & preparation clause prior to application. Apply one coat of Sikagard® 552W Aquaprimer by brush or roller at a consumption rate of not less than 0.12 ltr/m² prior to applying Sikagard® 545W Elastofill. Tight trowel 1 coat of Sikagard® 545W Elastofill to ensure that all blowholes and other surface imperfections are filled. Apply a smoothing coat of Sikagard® 545W Elastofill by short piled roller or trowel to achieve a minimum dry film thickness of 1.0mm to achieve the required surface texture in preparation for over coating with Sikagard® 550W Elastic or Sikagard® 675W Elastocolor. Site adhesion values to comply with BS EN 1504-2. Adhesion test average for smoothing coat must be >0.8 N/mm2 (MPa) with no single value below 0.5 N/mm2 (MPa) for crack bridging coatings.
2.4.10 |  | PROTECTIVE COATING SYSTEM: PRIMER APPLICATION
a) |  | Following application of Sika MonoTop® 3020 or Sikagard® 545W Elastofill smoothing coat/pore filler (if applicable), apply by brush or roller one coat of Sikagard® 552W Aquaprimer at a consumption rate of not less than 0.12 ltr/m².
2.4.11 |  | PROTECTIVE COATING SYSTEM: COATING APPLICATION
a) |  | (BS EN 1504-2 Classification) Following application of the Sika MonoTop® 3020/Sikagard® 545W Elastofill smoothing coat/pore filler (if applicable) and primer, apply by brush, spray or roller 2-3 coats of Sikagard® 550W to achieve a minimum total dry film thickness (dmin) of 340 microns. To ensure the final (dmin) values are achieved wet film gauge measurements should be carried out by the applicator during application using comb gauge or wheel gauge as defined in EN ISO 2808. Dry film thickness readings can be determined by methods stated in EN ISO 2808. Where required, the applicator will be responsible for arranging this testing with an appropriate testing body.
b) |  | Site adhesion values to comply with BS EN 1504-2 Adhesion test average for coating must be >0.8 N/mm2 (MPa) with no single value below 0.5 N/mm2 (MPa) for crack bridging coatings. A coating primer may not be required if the above coating adhesion values can be achieved by the coating on the smoothing coat/pore filler finish. To be confirmed by trials prior to full coating application. If a guarantee is required a primer shall always be used. It is recommended that samples of the coating are applied to areas of the structure as controls before application to the complete structure for adhesion tests, and agreement of colour and surface finish.
2.5 |  | WALKWAYS & PRIVATE BALCONIES
2.5.1 |  | General
2.5.1.1 |  | Contractor is to ensure the below Schedule of Works details takes full precedence over the Langley Specification Document. It is noted that the below includes changes or refinements, with further comments also added. The Contractor is to ensure they price in full accordance with the below.
2.5.1.2 |  | A full assessment of repairs to substrate is required by the Contractor prior to pricing. It is anticipated that all required proprietary works are carried out. It is assumed that all walkway and stair landing substrates can receive the PMMA coating. The Contractor is to let the Contract Administrator know if there is any limitations on application at the tender stage.
2.5.1.3 |  | The Contractor is to allow to temporarily remove and reinstate the upper stair nosings to facilitate the works. Reinstate on completion of redecoration and repair works.
2.5.1.4 |  | The Contractor is to allow to phase the walkway coating works in stages to allow for maximum occupancy use and safe access around the building. The Contractor is to allow to complete PMMA works as per an agreed programme with the Contract Administrator. It is envisaged that up to 4no. flats can be preventing access at one time only.
2.6 |  | SPECIFICATION REQUIRMENTS
2.6.1 |  | Guarantee: The following PR-25-C specification is to be covered by the Langley Waterproofing Systems Ltd, single-premium, pre-paid independently-insured workmanship and materials guarantee for a period of 25 years from the date of practical completion. In order to meet this requirement only roofing contractors that participate in this guarantee scheme may be used. The eligibility of proposed roofing contractors should be confirmed with Langley Waterproofing Systems Ltd, Tel: 01327 704778 prior to inviting tenders.
2.6.2 |  | Projects Under CDM: In relation to this project, under Construction (Design and Management) Regulations 2015 (CDM 2015), it is the responsibility of the Contractor to appoint any, or all, relevant "CDM duty-holders".
2.6.3 |  | Design Note - Existing Falls: Overlay of any existing roof system or deck. The new system will follow the existing falls and any deviations will be replicated. As a result, some areas of standing water may occur. However, please note the accumulation of ice, snow or ponding water will not have an adverse effect on the Langley products specified. This applies to both the life expectancy and / or long-term performance of the system specified and will not affect, in any way, the guarantee status.
2.6.4 |  | Design Note: Unless otherwise stated, all Pararapide PMMA products are solvent free.
2.6.5 |  | Design Note - Mixing: Mixing of all Pararapide PMMA products must be carried out with a power driven spiral mixing paddle (see Fixing Instructions for details).
2.6.6 |  | Design Note - Adhesion Testing: Before work commences contractor must establish that a secure bond can be achieved. Peel strength tests to be carried out to both main area and details (see ‘Fixing Instructions’ for details).
2.6.7 |  | Design Note - Changes & Adjustments: Variations 'A' (general): Any variations must be agreed in writing by both the contract administrator and Langley Waterproofing Systems Ltd. These must be costed and authorised by the client but not be implemented until instructed by the client. Variations 'B' (minor): During work in progress, Langley Waterproofing Systems Ltd must be informed immediately of any proposed change/s and operatives must not implement any change/s until agreed by Langley (minor changes are deemed to be any item not falling within the scope of section a). Unauthorised Changes 'C' (general): Langley Waterproofing Systems Ltd will not be responsible for any changes of which they are unaware or have not authorised, nor will they accept any liability or associated costs due to system failure, i.e. labour, materials, design or programme delays, etc., resulting from said changes. NOTE: The Contractor is required to be in compliance with a fully Langley approved product and will be bound by their requirements in doing so.
2.6.8 |  | Design Note - Approved Document Part B Building Regulations - Compartmented Walls: Removal of Existing Structural Deck and/or Waterproofing: Where the Langley Waterproofing system bridges a compartmented wall, the system must be laid on a substrate or deck rated class A2-s3, D2 or better (non-combustible) to BS EN 13501-1. Buildings below 15m high, the substrate or deck can be rated class B-s3, D2 or worse (combustible), such as timber boarding and battens but they must be fully bedded on mortar (or other no less suitable material) across the full width of the compartmented wall. Double-skinned insulated roof sheeting, such as standing seam or profile metal sheet roofing, should incorporate a band of material rated class A2-s3, D2 or better, a minimum of 300mm in width, centred over the wall. Note: Proposed specification and design will be subject to LABC (Local Authority Building Control) approval before works can commence on-site. Where appropriate, Langley Waterproofing can offer support and guidance to assist application.
2.6.9 |  | Electronic Roof Integrity Test (Compulsory For Buried Systems) - Disclaimer: Prior to the installation of any proposed roof finishes, an electronic leak detection test must be carried out by a WITA approved contractor to ensure the integrity of the newly installed waterproofing system and to meet Langley Waterproofing Systems Ltd guarantee requirements.
2.6.10 |  | Fire Risk - Drying Out: In the event of the roof becoming wet and drying out is necessary, the use of gas torches is not recommended and should be avoided. In all cases Safe2Torch guidelines should be followed. Standing water should be swept to the nearest outlets with a broom or squeegee (care must be taken to avoid debris blocking outlets). The remaining moisture should be soaked up using mops or dry rags and the surface left to dry out naturally. To speed up the process, specialist equipment is commercially available, see ‘General Guidance & Requirements’ in the appendices of this specification.
2.6.11 |  | Langley Detailed Drawings: This specification is to be read in conjunction with the detailed drawings issued and supplied by Langley Waterproofing. Should the contractor at any point find discrepancies between the issued specification and issued drawings, it is required that the specification takes precedence in all cases, unless otherwise notified and approved. No additional costs or liability arising from failure to follow specification or notifying Langley Waterproofing Systems Ltd of any discrepancies found in good time prior to commencement of works will be considered. NOTE: Drawings supplied are considered general drawings and likely to differ slightly as noted above.
2.7 |  | SCOPE OF APPLICATION
2.7.1 |  | Overlay of Existing Asphalt: This specification is based on an overlay of an existing asphalt covering and tiles, where relevant.
2.7.2 |  | Deck and Substrates - Existing Asphalt on Screeded Concrete: This specification is suitable for application to a substrate of an existing prepared asphalt system on a screeded concrete roof deck, not exceeding 5° from the horizontal.
2.7.3 |  | Day / Night Joints: The contractor must ensure at the end of each working day or period, that any reinforcing fleece is not left exposed. It must be completely covered and sealed with the specified Pararapide waterproofing system. In addition, any substrates that are susceptible to damage through water ingress are sealed to ensure complete water tightness. No loose laid membranes or other such covers are permitted.
2.8 |  | PREPARATION
2.8.1 |  | Contractor Preparation Note: The contractor is to carry out his own inspection to satisfy himself with regard to the extent of works involved in the preparation of the existing roof coverings and substrates. No claims arising from failure to do so will be considered by Langley Waterproofing Systems Ltd.
2.8.2 |  | Contractor Note - Expansion Joints: All works to expansion joints (detailed elsewhere) to be completed prior to applying the Pararapide waterproofing system.
2.8.3 |  | Rainwater Downpipes from Higher Levels - Temporary Removal: To facilitate the re-roofing work. As required, temporarily remove all rainwater downpipes, shoes and supporting pipe brackets etc. Set aside and securely store for re-fixing on completion of waterproofing works.
2.8.4 |  | Existing Outlets - Refurbish with ParaFurb Outlets: Make ready to accept new ParaFurb Refurbishment Outlets (detailed elsewhere). Where necessary, cut back and remove sufficient existing waterproofing from around the outlets and as required from the surrounding area to allow for correct installation. Important Note: ParaFurb Outlets must not be installed to outlet positions that already have an existing refurbishment outlet in place. Prior to ParaFurb Outlets being installed, any existing refurbishment outlets or lead sleeve inserts must first be removed and surrounding substrates made good.
2.8.5 |  | Contamination - Remove: Remove any contamination that could impair system adhesion. All affected areas should be swept or power washed. Note: Power Washing (max. 2000 psi) Care must be taken to avoid penetrating the existing waterproofing system through any existing defects.
2.8.6 |  | Painted Surfaces: Coats of Paint: Completely remove.
2.8.7 |  | Substrate - Metal: All metal surfaces (including outlets & pipes where applicable). Abrade to a bright finish and wipe clean with Pararapide Cleaner 3mm beyond surface to be treated. Prime with Pararapide Metal Primer (detailed elsewhere).
2.8.8 |  | Loose Coverings and/or Patch Repairs - Remove: All loose coverings, patch repairs, etc. must be removed and discarded to suitable waste containers.
2.8.9 |  | Existing Asphalt Surface - Preparation: Warm and smooth out all ridges and blisters. Where necessary, make good any damage to the asphalt surface.
2.8.10 |  | Existing Asphalt Surface - Walkways and Balconies - Additional Requirements: Contractor Requirement: Prior to application of any primer. Contractor to ensure that any undulations, deflections or poor falls that cannot be overcome by warming and smoothing are reported to both Langley and the CA for further inspection.
2.8.11 |  | Existing Asphalt Details - Remove / Repair: Check integrity of asphalt upstands, skirtings and details generally. Cut back or repair as appropriate to ensure a sound secure base for the new Pararapide waterproofing system.
2.8.12 |  | Redundant Chases - Make Good: Rake out and prepare any redundant chase lines. In-fill with sand and cement mortar, flush with wall face.
2.8.13 |  | Upstands to Brickwork - New Chase: In preparation of a new cover flashing the contractor is to cut a new chase to a minimum 25mm depth and at a minimum height of 150mm above the intended finished roof level surface. Brush clean and prime with appropriate primer to seal substrate.
2.8.14 |  | Door Thresholds - Existing Cill/s: Upstand to underside. Remove all loose and friable material back to a sound base. Prime substrate with the appropriate primer. Apply Pararapide Filler to make good all surfaces.
2.8.15 |  | Pipe Penetrations Generally - Extend: Extend where necessary. Collar or pipe sleeve/s must be a minimum of 150 mm above the finished roof surface. Note: Extension pipe/s must be fixed inside the existing.
2.8.16 |  | Substrate Preparation - General: All substrates must be: clean, dry, free of oil, grease, curing compounds, release agents, laitance, gross irregularities, loose, unsound or foreign material such as moss, algae growth, dirt, ice, snow, water or any other condition that would be detrimental to adhesion of the primer or and/or resin to the substrate. Some surfaces may require scarifying, sandblasting or grinding to achieve a suitable substrate.
2.8.17 |  | Minor Surface Repairs: Holes, splits, cracks etc. Fill with Pararapide Filler using a trowel to provide an even finish.
2.8.18 |  | Priming - Brickwork, Timber and Mortar: Absorbent surfaces generally. Surface must be dry. Prime with Pararapide Masonry Primer and allow to dry.
2.8.19 |  | Priming - Metal Substrates: All metal surfaces (including outlets & pipes). To prepared surface. Prime with Pararapide Metal Primer and allow to dry.
2.8.20 |  | Priming - Asphalt: All asphalt surfaces (including asphalt details). Sweep clean of all dirt, debris and loose material. Surface must be dry. Prime with Pararapide Asphalt Primer and allow to dry.
2.9 |  | WATERPROOFING - COVERINGS
2.9.1 |  | Details - Generally: All skirtings, details, penetrations, etc. to be waterproofed prior to the main area (see Detail Section).
2.9.2 |  | Main Field Area - Pararapide WP: To a prepared surface. Apply a liberal coating of the mixed resin with brush or roller at a minimum rate of 2 kg/m². Roll out the (dry) Pararapide Fleece onto the resin, smooth side uppermost, avoiding any folds or wrinkles and allowing the resin to saturate the fleece. Using the large roller or brush, work the resin into the fleece, eliminating any air bubbles or wrinkles etc. Once the fleece is saturated, immediately apply a second coat the mixed resin at a minimum rate of 1 kg/m². See ‘Fixing Instructions’ for correct mixing procedures. Pararapide Fleece. Side and end laps minimum 50mm.
2.9.3. |  | Main Field Area - Pararapide SL Mortar: To a prepared surface. Apply the mixed resin at a rate of approximately 4 kg/m². Application to be with a serrated trowel to achieve an even coat. Cover only one working area at a time (1.4 – 1.9 m²). Note: The mixed resin consists of 3 components. See ‘Fixing Instructions’ for correct mixing procedures.
2.9.4 |  | Main Field Area - Slip-Inhibiting Finish - Pararapide Quartz: Broadcast Pararapide Quartz Granules onto wet Pararapide SL Mortar. Coverage approximately 3 – 4 kg/m² (0.71 – 1.25mm granules). Allow mortar to cure then remove excess granules by sweeping or hoovering.
2.9.5 |  | Main Area & Details - Pararapide Sealer Coat: Colour Dark Grey (RAL 7043). To a prepared surface. Apply the mixed resin with a roller or brush at a rate of 0.4 – 0.8 kg/m². Cover See ‘Fixing Instructions’ for correct mixing procedures.
2.1 |  | DETAILS
2.10.1 |  | Detailing General Requirement - Pararapide WP Detailing: To prepared surface. Apply a liberal coating of Pararapide WP Detailing coating system with a brush or roller at a rate of 2.5 – 3.5 kg/m². Roll out and embed 260mm wide Pararapide Fleece. Immediately apply a second coat of Pararapide WP Detailing. See ‘Fixing Instructions’ for correct mixing procedures.
2.10.2 |  | Detail Skirtings - Requirement: All detail skirtings must be a minimum of 150mm above the finished roof surface level.
2.10.3 |  | Detailing Sealer Coat - Pararapide Sealer Coat: Colour Dark Grey (RAL 7043). To a prepared surface. Apply the mixed resin with a roller or brush at a rate of 0.4 – 0.8 kg/m². Cover See ‘Fixing Instructions’ for correct mixing procedures.
2.10.4 |  | Expansion Joint - Existing: NB: Work to be completed prior to the installation of the main coating. Rake out joint and remove all dirt, debris and loose material. Prime with the requisite Pararapide primer (where applicable). Infill joint gap with Pararapide Filler, forming a bucket handle profile along the length of the joint and allow to cure. Apply a liberal coating of the mixed Pararapide WP detailing resin with brush or roller at a rate of 2.5 - 3.5 kg/m2. Roll a pre-cut (dry) piece of Pararapide Fleece, 100mm wide, onto the resin (smooth side uppermost), allowing the resin to saturate the fleece. Using the roller or brush, work the resin into the fleece, ensuring it is fully bedded into the formed groove. Once the fleece is saturated, immediately apply a second coat the mixed resin. Repeat the process incorporating 150mm wide fleece. Apply a 20mm wide strip of masking tape equidistant along the centre of the joint, prior to applying the Pararapide SL Mortar layer (detailed elsewhere). Note: This must be removed before the mortar cures.
2.10.5 |  | Internal Drainage - ParaFurb Outlets: Install to suit diameter of fall pipes, ParaFurb Outlet. Fully bond bitumen flange membrane to previously installed Paratene carrier membrane or appropriate substrate. To a primed surface apply the full Pararapide system over the flange and dressed into the outlet opening.
2.10.6 |  | Where Design of Existing Outlets Preclude the Use of ParaFurb Outlets: Remove grating, clamping ring and existing waterproofing. Clean and prime flange and bowl. Fully bond waterproofing layers to the flanges and openings to form watertight seals. Secure with clamping rings and re-fit grating. Prior to work continuing a method of waterproofing must be demonstrated, on site, with a working example, one for each type of outlet, for approval by Langley Waterproofing Systems Ltd. Once approved, the same method must be used for all subsequent outlets.
2.10.7 |  | Proprietary Outlets - New: To primed surface. Apply a liberal coating of specified waterproofing system to the flanges and openings with a brush or roller at a rate of 2.5 – 3.5 kg/m². Embed 260 mm wide reinforcing fleece and immediately apply a second coat of waterproofing. See ‘Fixing Instructions’ for correct mixing procedures. On completion, fit clamping ring and leaf guards (if appropriate).
2.10.8 |  | Step Edge Protection - Pararapide Stair Nosing Existing stair nosings to be retained and reinstated. COST OPTION TO REPLACE ALL - Provide cost to cut Pararapide aluminium stair nosing to size and adhere to the substrate with Pararapide Filler.
2.10.9 |  | Hand Rail Stanchions: To a prepared and primed (if required) surface. Apply Pararapide WP Detailing, reinforced waterproofing. Coating should extend up the stanchion by a minimum of 150mm above the finished level of the roof surface. Protect with a weathering collar or secure with a stainless steel Jubilee clip and Langley Gap-Seal Mastic. All Jubilee clip tensioners should face away from any proposed access routes.
2.10.6 |  | Junction with Existing Waterproofing System: Over a minimum width of 300mm; surface finish to be removed. Clean and dry surface. Thoroughly prime existing substrate with appropriate primer (subject to adhesion test) and allow to dry. Lap onto the existing by minimum 150mm; sealer coat to extend a further 150mm beyond.
2.10.7 |  | Skirting to Chase: Existing Prepared Chases. The full Pararapide WP Detail system (including reinforcing fleece) to be dressed to the full depth (25mm) of the chase. Allow to cure and point with Langley Gap-Seal Mastic.
2.10.8 |  | Full Staircase Detailing - COST OPTION Continue the full Pararapide system to the edge of the top step. Apply fully reinforced Pararapide WP Detailing down each riser and tread encapsulating the full staircase. To a prepared surface. Apply Pararapide SL Mortar, fully mixed resin, at a rate of approximately 4 kg/m². Application to be with a serrated trowel to achieve an even coat. Cover only one working area at a time (1.4 – 1.9 m²). On all treads areas of the staircase only, whilst Pararapide SL Mortar is still wet, evenly broadcast a layer of Pararapide Quartz Granules at a rate of 3-4 kg/m². Once Pararapide SL Mortar has cured remove any residual Pararapide Quartz Granules by sweeping or vacuuming. Finally, apply Pararapide Sealer Coat at a rate of 0.4-0.8 kg/m² to the surface of the fully cured wearing course. Colour: RAL 7043 (Dark Grey). To terminate the Pararapide system at the base of any step, turn the system down the full face of the last riser, terminate to a taped edge and seal with Langley Gap-Seal Mastic sealant. Where required, cut Pararapide aluminium stair nosing to size and adhere to the edge of each tread with Pararapide Filler. Pararapide Quartz Granules and Pararapide Sealer Coat must be suitably set back to accommodate the application of the stair nosing Note: For mixing and installation requirements, please refer to the Fixing Instruction and Guidance sections of this specification.
2.10.9 |  | Skirting to Low Door Thresholds: To prepared substrate. Apply Pararapide WP Detail system (including reinforcing fleece). Dress to the underside of the overhanging threshold. Abutment with underside of threshold to be sealed with a bead of Langley Gap-Seal Mastic. Important Note: Details below 150mm will not be covered by the Langley Waterproofing guarantee.
2.11 |  | COMPLETION
2.11.1 |  | Guarantee Requirement - Final Inspection: In accordance with our guarantee requirements, Langley Waterproofing Systems Ltd are to be notified once all works are complete. A final inspection will then be undertaken by us and the contractor must ensure that safe working access is provided.
2.11.2 |  | Rainwater Downpipes - Existing: Re-fix all downpipes, supporting brackets and shoes upon completion of the new waterproofing system. Allow for any modifications / adaptations necessary to accommodate any raised levels presented by the new roofing system. Replace any broken or damaged items to match existing.
2.11.3 |  | Internal Rainwater Outlets - ParaFurb Refurbishment Outlets: Check for blockages. Clear if necessary and leave in a free-running condition. Ensure Ribseal is tightly secured to form correct pressure seal to pipe/s for applicable units. Ensure all supplied leaf guard / gratings are in place and tightly secured.
2.11.4 |  | Completed Roof Surface - General: Ensure visual inspection of all laps is undertaken to confirm integrity of system prior to final guarantee inspection. Sweep, clean and remove debris to suitable waste container.
2.11.5 |  | Arisings from Works: Remove from site all arisings for return to contractor storage or safe disposal
2.12 |  | Mastic Asphalt 1st Floor Balcony Overhanging Soffits
2.12.1 |  | Prepare - To the two overhanging soffit details to the 1st floor balconies on Blechynden Street, strip off all mastic asphalt coverings. Apply sand rubbed surface is necessary to reduce the incidence of surface crazing, with asphalt to be applied direct to the structural deck with no insulation.
2.12.2 |  | Contractors Design Portion - Supply and install a new mastic asphalt covering to overhanging soffit section at base of balcony parapet wall in accordance with BS 8218:1998. Allow to prepare substrate to receive new covering, to be even free from ridges, hollows and indentations. Roofing asphalt is to be laid in two coats, and a breaking joint, to a total thickness of 20mm on an underlay of black sheathing felt laid loose with 50mm lapped joints. The application of roofing asphalt is to be in accordance with BS 8218 and BS 8000: Part 4.
2.12.3 |  | Supply and install new lead flashings, chased and wedged into mortar joints with lead clips and dressed over asphalt to provide a min. 150mm upstand detail. Fill lead joints with suitable lead sealant. No flashing piece is to exceed 1.5m in length. Laps are to be 100mm minimum. Lead thickness is to be selected in line with BS EN 12588. Apply patination oil to new leadwork.
2.13 |  | Balconies
Modifications
2.13.1 |  | Fully prepare balcony handrails to all flats, allow to leave ready to receive welded sections.
2.13.2 |  | Supply and install new mild steel tubes (S235/S275) to all balcony handrails to flats in order to raise handrail by circa 200mm, to meet the 1100mm minimum height under Building Regulations. Tubes are to match existing dimensions, and to match existing style, with vertical sections in line with existing. Mild steel sections are to be welded to existing handrails with MIG welding technique, to be BS4872 MIG Compliant Welding, to be completed by a fully qualified welder, with NVQ Level 3 Award in MIG welding or similar approved.
2.13.3 |  | Horizontal return sections of tubular steel to incorporate a metal anchor base plate, which is to be secured and coach bolted to the existing masonry façade.
2.13.4 |  | Contractor is to allow to complete these works via the external scaffold and therefore access within the flats are not deemed to be required.
2.13.5 |  | On completion allow to paint all handrails and plates, including new sections in accordance with the below:
System code: M2368ALK Dulux Trade Metalshield Satin;
| a) | Preparation - Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and dust off.
| b) | Priming - Prime all bare metal with: 1 coats of Dulux Trade Metalshield Zinc Phosphate Primer applied to give a minimum wet film thickness of 150 microns per coat giving a minimum dry film thickness of 65 microns per coat.
| c) | Bring Forward - Bring forward all primed areas with: 1 coat of Dulux Trade Metalshield Satin applied to give a minimum wet film thickness of 80 microns giving a minimum dry film thickness of 40 microns.
| d) | Finishing System - Apply 2 coats of Dulux Trade Metalshield Satin each applied to give a minimum wet film thickness of 80 microns per coat, giving a minimum dry film thickness of 40 microns per coat. (Colour: Black).
EXTERNAL AREAS
2.14 |  | Basement Staircase
2.14.1 |  | Contractors Design Portion: To the basement staircase on Bramley Road side courtyard, allow to cut out lower corroded and damaged section of stringer. Provide a welded 20mm thick mild steel plate (BS EN:10025 S275JR) to existing stringer, complete with matching brackets to fix and support into adjacent masonry wall and concrete floor. Supply proposals to Contract Administrator for review by Structural Engineer and approval.
2.15 |  | Doors to Rooftop
2.15.1 |  | Allow to overhaul all doors to rooftop, including all upper stair entrance doors which are below rooftop level and accessible to the main communal upper floors. Contractor is to ease and adjust each door, greasing hinges to ensure doors are smoothly operating, does not bind and is not heavy to open. If doors are not serviceable, Contractor is to inform the Contract Administrator prior to carrying out the below repair and overhaul works.
2.15.2 |  | As part of overhauling doors to rooftop, Contractor is to remove and replace all chicken mesh over doors with new Steel Expanded Metal Perforated Metal Screen Door Mesh, in Twill Weave to be of quality and smooth finish, 2mm. Steel mesh it to be cut to door size, with all sharp edges removed and chamfered where required. Allow to prepare and MIG weld to doors. To arched sections over the doors, cut further bespoke sections, remove sharp edges and chamfer where required. Weld these further sections to arched sections of railings above doors.
2.15.3 |  | Replace all existing latch/locks for new locks, on a suite key. Contractor is to source correct latch/locks required to suit doors.
2.15.4 |  | On completion of the above, full prepare and paint all doors, mesh and associated metal panels and areas in accordance with the below:
System code: M2368ALK Dulux Trade Metalshield Satin;
| a) | Preparation - Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and dust off.
| b) | Priming - Prime all bare metal with: 1 coats of Dulux Trade Metalshield Zinc Phosphate Primer applied to give a minimum wet film thickness of 150 microns per coat giving a minimum dry film thickness of 65 microns per coat.
| c) | Bring Forward - Bring forward all primed areas with: 1 coat of Dulux Trade Metalshield Satin applied to give a minimum wet film thickness of 80 microns giving a minimum dry film thickness of 40 microns.
| d) | Finishing System - Apply 2 coats of Dulux Trade Metalshield Satin each applied to give a minimum wet film thickness of 80 microns per coat, giving a minimum dry film thickness of 40 microns per coat. (Colour: Black).
2.16 |  | Tarmac
2.16.1 |  | Carry out isolated repair to tarmac pothole within the entrance courtyard to entrance on Blechynden Street. Allow to carry out with pre-mixed Watco Concrex Asphalt Repair or similar approved.
2.16.2 |  | Carefully jet wash down tarmac pathway to building perimeter, removing all moss build up and algae and rake away all loose aggregates from surface. Sweep clean and apply a Resincoat Pro Tarmac Sealer paint or similar approved to finished surfaces.
2.17 |  | Eastern Boundary Wall
2.17.1 |  | Option Cost - Provide option cost to demolish and rebuild the wall to a length that is 5m either side of major cracking. Allowance to reconstruct the wall with 2m deep foundations, including all necessary coping details and render finish to match existing. Prior to works, carry out CAT scan of the ground and confirm it is safe and suitable to excavate. NOTE: Option Cost not to be carried through to total.
2.18 |  | Pigeon Spikes
2.18.1 |  | Option Cost - Provide option cost to install pigeon spikes on all external window sills NOTE: Option Cost not to be carried through to total.
2.18.2 |  | Option Cost - As above, provide option cost to install 1 l/m of pigeon spikes on external window sills and costs to be included and calculated on a pro-rata basis. NOTE: Option Cost not to be carried through to total.
2.19 |  | Redundant Holes
2.19.1 |  | Option Cost - Provide option cost to remove infill materials to redundant holes, such as foam and the like and infill a 200mm diameter hole with new brickwork to match existing finishes. Repairs to include replacing brickwork, repointing and making good. Provide cost to carry out 1no. repair and costs to be included and calculated on a pro-rata basis. NOTE: Option Cost not to be carried through to total.
TOTAL EXTERNAL ELEVATIONS & EXTERNAL AREAS |  |  |  |  | 0

## Windows & Doors
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item | Description | Quantity | Units | Rate
PART THREE - THE WORKS
WINDOWS & DOORS - CONTRACTORS DESIGN PORTION
3.1 | Installers
3.1.1 | The installation of the windows and doors must be completed by a Trustmark & PAS2030 certified installer. The works are to be completed in full compliance with PAS 2030 and PAS 2035, in order to secure relevant funding.
3.1.2 | For the Main Contractor’s guidance only a quotation for the new window and door works have been obtained from 'Nica Design Ltd'. If used; the Contractor should allow for all costs in connection therewith, including profit, attendances, management etc. In no circumstances is the Contractor to classify 'Nica Design Ltd' as a nominated subcontractor. All risk associated will be attained to the Main Contractor. Refer to Appendix P for quotation for consideration.
3.1.3 | The Main Contractor is to utilise Nica Design Ltd design specified or equal approved. Submit full proposals and details with tender bid including details of supplier / sub-contractor proposed.
3.1.4 | Any other suggested windows will need to be as installed as per Flat 1, which is a pilot flat and quality and style of finish is to be matched.
3.1.5 | It is noted that the residents will need to approve any other equal approved windows, including the Contract Administrator and Employer.
3.2 | General
3.2.1 | All window and door works are to be completed as a Contractor Design Portion and to supply details of design including fabrication drawings for Contract Administrator approval, prior to all units going into production.
3.2.2 | The Contractor is to refer to Appendix Q - Planning Consents for full details of approvals and to ensure compliance in design and any conditions stipulated.
3.2.3 | Allow to strip out all windows and doors and dispose accordingly in skips to be provided. Provide every effort to sort and recycle materials in separate skips.
3.2.4 | Any windows and doors removed are to be replaced with new units on the same day. If for any reason a unit is not able to be installed, the Contractor is to appropriately frame and board up openings internally, ensuring properties are safe and secure.
3.2.5 | Windows and doors are to be replaced in coordination with the lintel replacement works and to be phased so to not cause unnecessary damage and disruption.
3.2.6 | The Contractor is to allow for window and door replacement works to be carried out while flats are fully occupied. Liaison between occupiers, Employer and Contract Administrator will be necessary to ensure windows and doors are replaced in a timely manner. A minimum of 1-week notice is required to occupier on replacing windows. Contractor will be required to supply a separate programme for occupiers on the window/door replacement works, which will be shared in advance with the occupiers.
3.2.7 | Contractor is to allow for reasonable making good works internally to seal all gaps, make good around window board and linings etc. but not to include internal redecorations.
3.2.8 | It is anticipated that some occupiers may be elderly on unable to move furniture. Contractor is to allow for general moving of furniture within flats, such as beds, tables, chairs etc.
3.2.9 | Windows and doors to be fully sealed and airtight, ensuring all backing rods and foam used around framing fills all areas and with suitable coverage.
3.2.10 | As required, allow to install all flashing tapes and DPC's around openings.
3.2.11 | The windows and doors are all to be triple glazed, unless otherwise stated to have areas of double glazed fire rated glazing units.
3.2.12 | The triple glazing for the windows and doors are to have a minimum U-value rating of 0.7 W/(m2·K). Units are to be argon filled with warm spacer-white, laminated where required.
3.2.13 | The double glazing (fire rated type) for the windows are to have a minimum U-value rating of 1.2 W/(m2·K).
3.2.14 | The non fire rated windows and doors are to be engineered pine. The part fire rated windows are to be made of hardwood, Meranti or similar approved.
3.2.15 | All windows and doors are to incorporate all ironmongery required, including but not limited to stainless steel finger pulls, mig stops, push locks, Brighton lock fasteners, stainless steel hinges to doors, 5-lever mortice lock, SOX Delta 316 Stainless Steel 92mm Door Handle - Polished Chrome (or similar approved).
3.2.16 | All doors are to as with windows to incorporate Georgian glazing bars to profiles as shown in drawings and as per Flat 1. The doors are to include a lower timber panel to terminate at height of lower side/flag window. Panel is to be an engineered timber panel, with chamfered door panels, as shown.
3.2.17 | All windows and doors are to be fully primed and then sprayed in RAL 9016 Sikkens microporous paint with two full coats.
3.3 | Lintels - Contractors Design Portion
3.3.1 | Ensure lintels that are removed and replaced to be considered in the Contractors window design and methodology of works. Ensure that any lintels replaced shall not compromise the window installation and vice-versa.
3.3.2 | Fully cut out existing corroded lintels to 4th floor communal balconies. Allow to temporarily prop openings, before installing new galvanised steel lintels to be sized in accordance with BS EN 845-2 and to have the correct end bearings. Allow to rebuild the end bearings in these locations. Full details of lintels to be installed are to be first submitted to the Contract Administrator and to be reviewed by the Employers appointed Structural Engineer. Lintels included: - Flat 23 over door. - Flat 23 over door. - Flat 23 over window. - Flat 25 over door. - Flat 34 over door. - Flat 34 over window.
3.3.3 | Rake out and repoint areas surrounding lintels with a 1:1:6 pre-mixed Type S mortar, noted above. Pointing style and colour to match existing. Note: All aggregate must be washed (do not use ordinary unwashed soft builders sand). Mortar must not be used too wet and must not be smeared over the arris or face of the bricks. Joints should be slightly brushed back to expose the aggregate. Note: Raking out must be by hand tools and to a depth of between 20mm (absolute minimum) and must be to the whole width/height of the joint.
3.4 | New Doors with Flag Windows - Contractors Design Portion
3.4.5 | Supply and install all new balcony doors to existing openings, complete with side flag windows. Supply and install new sash windows and frame in engineered pine to existing openings, windows to be triple glazed Georgian style sash in pine with Sikkens microporous paint finish, using RUBBOL WP 198 primer to required film thickness and WF 3311-03/04 2no. top coats to required film thickness. Refer to Tender Drawings for Employers requirements and refer to planning consents in Appendix Q. RAL Colour: 9016 Standard White Contractor to provide a schedule of costs, listing individual cost for each existing door with flags being replaced and submit with tender bid. IMPORTANT NOTE: Drawing above does not show all windows, refer to site visit for additional windows on returning elevation walls.
a) | Flat 3 Balcony Door with flags.
b) | Flat 4 Balcony Door with flags.
c) | Flat 6 Balcony Door with flags.
d) | Flat 9 Balcony Door with flags.
e) | Flat 10 Balcony Door with flags.
f) | Flat 13 Balcony Door with flags.
g) | Flat 14 Balcony Door with flags.
h) | Flat 15 Balcony Door with flags.
i) | Flat 17 Balcony Door with flags.
j) | Flat 20 Balcony Door with flags.
k) | Flat 22 Balcony Door with flags.
l) | Flat 23 Balcony Door with flags.
m) | Flat 24 Balcony Door with flags.
n) | Flat 28 Balcony Door with flags.
o) | Flat 29 Balcony Door with flags.
p) | Flat 31 Balcony Door with flags.
q) | Flat 32 Balcony Door with flags.
r) | Flat 33 Balcony Door with flags.
s) | Flat 34 Balcony Door with flags.
t) | Flat 35 Balcony Door with flags.
u) | Flat 38 Balcony Door with flags.
v) | Flat 39 Balcony Door with flags.
x) | Flat 40 Balcony Door with flags.
y) | Flat 41 Balcony Door with flags.
z) | Flat 42 Balcony Door with flags.
aa) | Flat 43 Balcony Door with flags.
ab) | Flat 44 Balcony Door with flags.
ac) | Flat 45 Balcony Door with flags.
3.4.6 | Following window/door installation, supply and install painted timber architrave/window board details to all internal sections of window and door openings. Contractor is to allow for a window board to a max. depth of 200mm on each window and to a max. depth of 70mm for side and top lining sections.
3.4.7 | Contractor to provide an extra over option cost for reveal liners from +70mm - 200mm depth, although cost not to be carried forward to tender sum.
3.5 | New Windows (Standard Triple Type) - Contractors Design Portion
3.5.1 | To all windows, except those which are listed as 'Hybrid Type' below, supply and install new sash windows and frame in pine to existing openings, windows to be triple glazed Georgian style sash in pine with Sikkens microporous paint finish, using WP 198 primer to required film thickness and WF 3311-03/04 2no. top coats to required film thickness. Refer to Tender Drawings for Employers requirements and refer to planning consents in Appendix Q. RAL Colour: 9016 Standard White Contractor to provide a further schedule of costs, listing individual cost for each existing window being replaced and submit with tender bid. Refer to Drawing 21/0555/002 REV.A. concerning window types. IMPORTANT NOTE: Drawing above does not show all windows, refer to site visit for additional windows on returning elevation walls.
a) | Flat 3 All Standard Triple Types.
b) | Flat 4 All Standard Triple Types.
c) | Flat 6 All Standard Triple Types.
d) | Flat 9 All Standard Triple Types.
e) | Flat 10 All Standard Triple Types.
f) | Flat 13 All Standard Triple Types.
g) | Flat 14 All Standard Triple Types.
h) | Flat 15 All Standard Triple Types.
i) | Flat 17 All Standard Triple Types.
j) | Flat 20 All Standard Triple Types.
k) | Flat 22 All Standard Triple Types.
l) | Flat 23 All Standard Triple Types.
m) | Flat 24 All Standard Triple Types.
n) | Flat 28 All Standard Triple Types.
o) | Flat 29 All Standard Triple Types.
p) | Flat 31 All Standard Triple Types.
q) | Flat 32 All Standard Triple Types.
r) | Flat 33 All Standard Triple Types.
s) | Flat 34 All Standard Triple Types.
t) | Flat 35 All Standard Triple Types.
u) | Flat 38 All Standard Triple Types.
v) | Flat 39 All Standard Triple Types.
x) | Flat 40 All Standard Triple Types.
y) | Flat 41 All Standard Triple Types.
z) | Flat 42 All Standard Triple Types.
aa) | Flat 43 All Standard Triple Types.
ab) | Flat 44 All Standard Triple Types.
ac) | Flat 45 All Standard Triple Types.
3.5.2 | Following window/door installation, supply and install painted timber architrave/window board details to all internal sections of window and door openings. Contractor is to allow for a window board to a max. depth of 200mm on each window and to a max. depth of 70mm for side and top lining sections.
3.5.3 | Contractor to provide an extra over option cost for reveal liners from +70mm - 200mm depth, although cost not to be carried forward to tender sum.
3.6 | New Windows (Hybrid Type -Triple & Double) - Contractors Design Portion
3.6.1 | To the 40no. windows identified on Drawing 21/0555/002 REV.A, supply and install new sash windows and frame in hardwood to existing openings, windows to be have a triple glazed Georgian style sliding upper sash in hardwood, with a fixed double glazed lower sash with a fire rated (EC30) glass (double glazing unit) with Sikkens a fire retardant paint finish with RUBBOL WP 112 primer coats to required film thickness and RUBBOL WF 33CC 2no. top coats to required film thickness. Refer to Tender Drawings for Employers requirements and refer to planning consents in Appendix Q. RAL Colour: 9016 Standard White Contractor to provide a schedule of costs, listing individual cost for each existing window being replaced and submit with tender bid. Refer to Drawing 21/0555/002 REV.A concerning window types. IMPORTANT NOTE: Drawing above does not show all windows, refer to site visit for additional windows on returning elevation walls.
a) | Flat 3 All Hybrid Fire Safety Types.
b) | Flat 4 All Hybrid Fire Safety Types.
c) | Flat 6 All Hybrid Fire Safety Types.
d) | Flat 9 All Hybrid Fire Safety Types.
e) | Flat 10 All Hybrid Fire Safety Types.
f) | Flat 14 All Hybrid Fire Safety Types.
g) | Flat 17 All Hybrid Fire Safety Types.
h) | Flat 20 All Hybrid Fire Safety Types.
i) | Flat 23 All Hybrid Fire Safety Types.
j) | Flat 29 All Hybrid Fire Safety Types.
k) | Flat 31 All Hybrid Fire Safety Types.
l) | Flat 33 All Hybrid Fire Safety Types.
m) | Flat 35 All Hybrid Fire Safety Types.
n) | Flat 38 All Hybrid Fire Safety Types.
o) | Flat 39 All Hybrid Fire Safety Types.
p) | Flat 40 All Hybrid Fire Safety Types.
q) | Flat 41 All Hybrid Fire Safety Types.
r) | Flat 42 All Hybrid Fire Safety Types.
s) | Flat 43 All Hybrid Fire Safety Types.
t) | Flat 44 All Hybrid Fire Safety Types.
u) | Flat 45 All Hybrid Fire Safety Types.
3.6.2 | Following window/door installation, supply and install painted timber architrave/window board details to all internal reveals of window and door openings. Contractor is to allow for a window board to a max. depth of 200mm on each window and to a max. depth of 70mm for side and top lining sections.
3.6.3 | Contractor to provide an extra over option cost for reveal liners from +70mm - 200mm depth, although cost not to be carried forward to tender sum.
TOTAL WINDOWS & DOORS |  |  |  | 0

## Decorations & Repairs
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item |  | Description | Quantity | Units | Rate
PART FOUR - THE WORKS
DECORATION & REPAIR WORKS
4.1 |  | Repairs
4.1.1 |  | To the staircase entrance at the central courtyard area, providing access to Flats on Blechynden Street, there are sections of cracked concrete to the edge of the concrete staircase. Allow to break out locally, removing all loose sections of concrete.
4.1.2 |  | Allow to carry out localised repairs / corrosion treatment works to the embedded steel upright sections concealed within stairs.
4.1.3 |  | Fully prepare with Sika primer in readiness to receive Sika Monotop-4012 repair mortar.
4.1.4 |  | Apply pre-mixed Sika® MonoTop-4012 repair mortar “wet on wet” onto the bonding primer between the minimum and maximum layer thicknesses and compacted without inclusion of entrapped air pockets using a trowel or gloved hand. Where layers are to be built up to prevent sagging or slumping, each layer should be allowed to harden and exothermic reaction of the material completed. The first layer shall be at ambient temperature before applying the second layer. Do not smooth the first layer before applying a second layer. The first layer should have sufficient roughness to provide a mechanical key for subsequent mortar layers. Finishing of the applied repair mortar should be carried out to the required surface texture as soon as the mortar has started to stiffen. To prevent surface cracking, do not apply water or overwork the surface with finishing tools. Site adhesion values to comply with BS EN 1504-3: NOTE: Structural Repairs: Class R4 > 2.0 N/mm2 (MPa). Class R3 > 1.5 N/mm2 (MPa).
4.1.5 |  | All riser panels to all communal stairs have standard fixings. Allow to replace all fixings to all riser panels throughout with non-tamper new Clutch Head Round Self Tapping Security Screws to the required lengths.
4.2 |  | General Decorations
2.11.1 |  | Please note that existing windows are being replaced and therefore are to be excluded from the scope of redecoration works.
2.11.2 |  | All staircase redecoration works are also to include basement levels.
2.11.3 |  | Preparations are to include for removal of graffiti; treating moss; fungi; lichen or mould where required and for removing all loose or flaking paint.
2.11.4 |  | Ensure proper preparation is made for surfaces, allowing for successful application of flame retardant systems as per Dulux Painting Systems Specification in Appendix J.
2.12 |  | External Elevations and Walkways; Balconies; Boundary Railings
2.12.1 |  | Walkway and balcony soffits and edges, and concrete window sills.
System code: D3041 Dulux Trade Weathershield Smooth Masonry Paint; previously painted areas.
| a) | Preparation - Thoroughly clean down the surfaces to remove all dirt grease and surface contaminants. Allow to dry. Remove all blistered, poorly adhering or otherwise defective coatings. Remove all loose or powdery material by vigorously brushing down with suitable stiff brushes and dust off.
| b) | Making Good - Cut out and make good cracks, holes and other imperfections with a good quality/compatible materials and follow the manufacturers' recommendations for use, even if at variance with this system. Allow to set and dry out thoroughly. Where appropriate, rub down the surface.
| c) | Priming - If surfaces remain powdery and friable after thorough preparation, they must be sealed with: 1 coat of Dulux Trade Weathershield Stabilising Primer to penetrate the surface and avoid leaving a glossy film. Prime all sound bare areas and areas exposed by the removal of coatings with: 1 coat of Dulux Trade Weathershield Smooth Masonry Paint of appropriate shade thinned up to 1 part Water to 5 parts of product as appropriate.
| d) | Bring Forward - Bring forward all areas which, during preparation, were either taken back to bare substrate or disfigured/exposed by the removal of the previous coating with: 1 coat of Dulux Trade Weathershield Smooth Masonry Paint of selected shade.
| e) | Finishing System - Apply 2 coats of Dulux Trade Weathershield Smooth Masonry Paint of selected shade.
2.12.2 |  | Woodwork; including communal doors and frames; service area and roof access doors and frames etc (Not windows)
System code: D4038WC+G Dulux Trade Weathershield Exterior High Gloss; previously painted areas
| a) | Preparation - Cut out and replace areas of decayed wood and/or seal any open joints using the appropriate Repair Care International Ltd repair method. Thoroughly clean down all surfaces with soap and water, detergent solution or suitable solvent, to remove all dirt, grease and surface contaminants. Remove all blistered, poorly adhering or otherwise defective coatings. Where flaking has occurred or coatings are defective, the entire member or section must be stripped back to the nearest joint. Open up all joints which are not tight fitting and rake out thoroughly. Rub down to 'feather' broken edges and *dust off. Abrade overall in the direction of the grain to remove any grey denatured timber, raised grain and round sharp edges (a radius of 1 mm to 2 mm f Apply two thin coats of an appropriate knotting solution to all knots and resinous areas and allow to harden. Ensure all surfaces are fully dry before proceeding.
| b) | Glazing - All glazing compounds and glazing repairs must comply with BS8000: Part 7: 1990 (Code of practice for glazing). Renew or replace defective glazing compounds or glazing beads using the appropriate Repair Care International Ltd repair method. All bare rebates and replacement beading are to be primed with: 2 coats of Dulux Trade Weathershield Preservative Primer.
| c) | Priming - Spot prime any bare metal, metal fixings nail heads etc with: 1 coat of Dulux Trade Metalshield Zinc Phosphate Primer. Prime all sound bare areas and areas exposed by the removal of coatings with: 2 coats of Dulux Trade Weathershield Preservative Primer. NOTE: Do not apply Dulux Trade Weathershield Preservative Primer over existing surfaces that are in good condition or any areas repaired with Repair Care International Ltd resin replacement products. All areas that have been spliced in or replaced should be base coated in the normal way. Any excess basecoat should be wiped away using a clean lint free cloth.
| d) | Making Good - Make good all cracks, nail-holes, open joints and other imperfections with Dulux Trade Weathershield Exterior Flexible Filler. When set carefully rub down and dust off.
| e) | Bring Forward - Bring forward all primed and/or filled areas to match existing system build with: 1 coat of Dulux Trade Weathershield Exterior Flexible Undercoat of appropriate shade.
| f) | Finishing System - Apply 1 coat of Dulux Trade Weathershield Exterior Flexible Undercoat of selected shade. Apply 1 coat of Dulux Trade Weathershield Exterior High Gloss of selected shade.
2.12.3 |  | Metalwork; railings; gates; mesh screens; decorative screens; service and roof access doors and frames; rainwater goods; service pipes etc.
System code: M2368ALK Dulux Trade Metalshield Satin; previously painted areas.
| a) | Preparation - Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and dust off.
| b) | Priming - Prime all bare metal with: 1 coats of Dulux Trade Metalshield Zinc Phosphate Primer applied to give a minimum wet film thickness of 150 microns per coat giving a minimum dry film thickness of 65 microns per coat.
| c) | Bring Forward - Bring forward all primed areas with: 1 coat of Dulux Trade Metalshield Satin applied to give a minimum wet film thickness of 80 microns giving a minimum dry film thickness of 40 microns.
| d) | Finishing System - Apply 2 coats of Dulux Trade Metalshield Satin each applied to give a minimum wet film thickness of 80 microns per coat, giving a minimum dry film thickness of 40 microns per coat.
2.12.4 |  | Woodwork; including balcony balustrading etc.
System code: D4064 Dulux Trade Ultimate Wood stain; previously stained areas
| a) | Preparation - Thoroughly clean down the surfaces with soap and water, detergent solution or suitable solvent, to remove all dirt, grease and surface contaminants. Remove all blistered, poorly adhering or otherwise defective coatings. Where flaking has occurred or coatings are defective, the entire member or section must be stripped back to the nearest joint. Open-up all joints which are not tight fitting and rake out thoroughly. Rub down to 'feather' broken edges and *dust off. Abrade overall in the direction of the grain to remove any grey denatured timber, raised grain and round all sharp edges (a radius of 1 mm to 2 mm for timber other than sills and thresholds; 3mm for sills and thresholds) and dust off.
| b) | Glazing - All glazing compounds and glazing repairs must comply with BS 8000: Part 7: 1990 (Code of practice for glazing). Hack out all cracked or defective glazing putties. Remove all defective or loose beading. Clean the rebates and apply: 2 coat(s) of Dulux Trade Weathershield Preservative Primer to all bare areas. Similarly, treat beading and any new wood which is to be spliced-in on all faces and edges, i.e. rub down and prime. REPLACEMENT OF GLAZING COMPOUNDS WHERE NECESSARY: When dry, re-glaze with appropriate glazing compound and allow to harden before further treatment. The compound manufacturer's recommendations must be adhered to, even if at variance with this system. REPLACEMENT OF BEADING WHERE NECESSARY: Bed in a suitable external quality mastic in accordance with the manufacturer's instructions and screw down tightly using non-ferrous fixings.
| c) | Priming - Prime all sound bare areas and areas exposed by the removal of coatings with: 2 coats of Dulux Trade Weathershield Preservative Primer. If required, touch in any primed areas with Dulux Trade Ultimate Wood stain to match the surrounding timber for colour and build. Allow to dry.
| d) | Making Good - Make good all cracks, nail holes, open joints and other imperfections with a suitable stopper / filler designed for use with a wood stain system. Allow the material to set before rubbing down and *dusting off. Fillers & Stoppers Use only good quality/compatible materials and follow the manufacturers' recommendations for use, even if at variance with this system.
| e) | Finishing System - Apply 2 coats of Dulux Trade Ultimate Wood stain of selected shade.
2.13 |  | Stair Towers
2.13.1 |  | Previously painted staircase ceiling/soffit areas etc
System code: D172W Dulux Trade Pyro shield Durable Matt; previously painted areas.
| a) | Preparation - Thoroughly clean down the surfaces to remove all dirt grease and surface contaminants. Remove all blistered, poorly adhering or otherwise defective coatings. Powdery and friable surface coatings should be completely removed by scraping, brushing and washing. Allow the surface to fully dry before proceeding. Where appropriate, rub down sound areas to produce the necessary 'key' for good adhesion and 'feather' broken edges of existing coatings.
| b) | Priming - Any water stains or surfaces that remain powdery and friable after thorough preparation must be sealed with: 1 coat of Dulux Trade Stain Block Primer. Prime all sound bare areas and areas exposed by the removal of coatings with: 1 coat of Dulux Trade Pyro shield Durable Matt of appropriate shade thinned up to 1 part Water to 5 parts of product as appropriate.
| c) | Making Good - Make good cracks, holes and other imperfections with Polycell Trade Easy Sand Interior Filler. Allow such making good to dry out thoroughly. Rub down smooth to match surrounding area and dust off.
| d) | Bring Forward - Bring forward all making good with: 1 coat of Dulux Trade Pyro shield Durable Matt of selected shade thinned up to 1 part Water to 5 parts of product as appropriate.
| e) | Finishing System - Apply 2 coats of Dulux Trade Pyro shield Durable Matt of selected shade. Note: In order to achieve fire classification, apply 2 coats at 12 square metres per litre (this equates to 2 coats at a wet film thickness of 85 microns per coat, dry film thickness 30 microns per coat). Do not thin. Over some (sealed) surfaces it may not be possible to achieve the recommended spreading rate on the first coat, and more than two coats may be required to achieve sufficient film build.
2.13.2 |  | Previously painted wall areas within staircases etc.
System code: D196W Dulux Trade Pyro shield Durable Eggshell; previously painted areas.
| a) | Preparation - Thoroughly clean down the surfaces to remove all dirt grease and surface contaminants. Remove all blistered, poorly adhering or otherwise defective coatings. Powdery and friable surface coatings should be completely removed by scraping, brushing and washing. Allow the surface to fully dry before proceeding. Where appropriate, rub down sound areas to produce the necessary 'key' for good adhesion and 'feather' broken edges of existing coatings.
| b) | Priming - Any water stains or surfaces that remain powdery and friable after thorough preparation must be sealed with: 1 coat of Dulux Trade Stain Block Primer. Prime all sound bare areas and areas exposed by the removal of coatings with: 1 coat of Dulux Trade Pyro shield Durable Eggshell of appropriate shade thinned up to 1 part Water to 5 parts of product as appropriate.
| c) | Making Good - Make good cracks, holes and other imperfections with Polycell Trade Easy Sand Interior Filler. Allow such making good to dry out thoroughly. Rub down smooth to match surrounding area and dust off.
| d) | Bring Forward - Bring forward all making good with: 1 coat of Dulux Trade Pyro shield Durable Eggshell of selected shade thinned up to 1 part Water to 5 parts of product as appropriate.
| e) | Finishing System - Apply 2 coats of Dulux Trade Pyro shield Durable Eggshell of selected shade. Note: In order to achieve fire classification, apply 2 coats at 12 square metres per litre (this equates to 2 coats at a wet film thickness of 85 microns per coat, dry film thickness 30 microns per coat). Do not thin. Over some (sealed) surfaces it may not be possible to achieve the recommended spreading rate on the first coat, and more than two coats may be required to achieve sufficient film build.
2.13.3 |  | Previously painted brickwork to low level wall areas within staircases
System code: D1053S Dulux Trade High Gloss (Black); previously painted areas.
| a) | Preparation - Completely remove all blistered, poorly adhering or otherwise defective coatings. Rub down overall to provide a 'key' and 'feather' broken edges of existing coatings.
| b) | Priming - Prime all bare areas and areas exposed by the removal of coatings with: 1 coat of Dulux Trade Alkali resisting Primer.
| c) | Making Good - Make good all holes with mortar.
| d) | Finishing System - Apply 1 coat of Dulux Trade Undercoat of selected shade. Apply 1 coat of Dulux Trade High Gloss of selected shade.
2.13.4 |  | Staircase areas; all woodwork; including communal doors and frames; riser doors and panels etc
System code: D4038WC+G Dulux Trade Weathershield Exterior High Gloss; previously painted areas.
| a) | Preparation - Cut out and replace areas of decayed wood and/or seal any open joints using the appropriate Repair Care International Ltd repair method. Thoroughly clean down all surfaces with soap and water, detergent solution or suitable solvent, to remove all dirt, grease and surface contaminants. Remove all blistered, poorly adhering or otherwise defective coatings. Where flaking has occurred or coatings are defective, the entire member or section must be stripped back to the nearest joint. Open up all joints which are not tight fitting and rake out thoroughly. Rub down to 'feather' broken edges and *dust off. Abrade overall in the direction of the grain to remove any grey denatured timber, raised grain and round sharp edges (a radius of 1 mm to 2 mm f Apply two thin coats of an appropriate knotting solution to all knots and resinous areas and allow to harden. Ensure all surfaces are fully dry before proceeding.
| b) | Glazing - All glazing compounds and glazing repairs must comply with BS8000: Part 7: 1990 (Code of practice for glazing). Renew or replace defective glazing compounds or glazing beads using the appropriate Repair Care International Ltd repair method. All bare rebates and replacement beading are to be primed with: 2 coats of Dulux Trade Weathershield Preservative Primer.
| c) | Priming - Spot prime any bare metal, metal fixings nail heads etc with: 1 coat of Dulux Trade Metalshield Zinc Phosphate Primer. Prime all sound bare areas and areas exposed by the removal of coatings with: 2 coats of Dulux Trade Weathershield Preservative Primer. NOTE: Do not apply Dulux Trade Weathershield Preservative Primer over existing surfaces that are in good condition or any areas repaired with Repair Care International Ltd resin replacement products. All areas that have been spliced in or replaced should be base coated in the normal way. Any excess basecoat should be wiped away using a clean lint free cloth.
| d) | Making Good - Make good all cracks, nail-holes, open joints and other imperfections with Dulux Trade Weathershield Exterior Flexible Filler. When set carefully rub down and dust off.
| e) | Bring Forward - Bring forward all primed and/or filled areas to match existing system build with: 1 coat of Dulux Trade Weathershield Exterior Flexible Undercoat of appropriate shade.
| f) | Finishing System - Apply 1 coat of Dulux Trade Weathershield Exterior Flexible Undercoat of selected shade. Apply 1 coat of Dulux Trade Weathershield Exterior High Gloss of selected shade.
2.13.5 |  | Staircase areas; all metalwork; including balustrades; handrails; brackets; mesh screens; decorative screens; roof access doors and frames; refuse chute doors and frames; service pipes etc.
System code: M2368ALK Dulux Trade Metalshield Satin; previously painted areas
| a) | Preparation - Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and dust off.
| b) | Priming - Prime all bare metal with: 1 coats of Dulux Trade Metalshield Zinc Phosphate Primer applied to give a minimum wet film thickness of 150 microns per coat giving a minimum dry film thickness of 65 microns per coat.
| c) | Bring Forward - Bring forward all primed areas with: 1 coat of Dulux Trade Metalshield Satin applied to give a minimum wet film thickness of 80 microns giving a minimum dry film thickness of 40 microns.
| d) | Finishing System - Apply 2 coats of Dulux Trade Metalshield Satin each applied to give a minimum wet film thickness of 80 microns per coat, giving a minimum dry film thickness of 40 microns per coat.
INTERNAL FINISHES
2.14 |  | Tiling within Staircases
2.14.1 |  | Carry out deep clean of all tiling, including all grouting with a warm water and mild detergent, using stiff-bristled brush.
2.14.2 |  | Report any damage to the Contract Administrator for consideration.
2.14.3 |  | Carry out tiling repairs to walls to match within staircases. Allow for 10m2.
2.14.4 |  | Carry out regrouting repairs to match within staircases. Allow for 10m2.
2.15 |  | Miscellaneous
2.15.1 |  | Jet wash down all external paths and paviours prior to the completion of the works.
2.15.2 |  | Make good to match existing damaged or missing areas of non-slip finish to treads and nosings. Allow to ensure upper flight of stairs have non-slip finishes.
2.16 |  | Signage
2.16.1 |  | Contractor is to supply signage to every stair entrance, to adjacent masonry wall. Signage to be a Black glossy acrylic printed sign (3mm), complete with 4 aluminium wall spacers and fixed to wall at height to be decided. Writing is to label 1st, 2nd and 3rd floors, with identification of each flat on floor. Contractor is to confirm fonts, sizing etc. and wording/layout with Contract Administrator prior to being fabricated.
TOTAL DECORATIONS & REPAIRS |  |  |  |  | 0

## Roof Works. Langley
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item | Description | Quantity | Units | Rate
PART FIVE - THE WORKS
ROOF WORKS
5.1 | Roof Tower Repairs
5.1.1 | Break out and remove all roof tower concrete cover slabs and dispose of all concrete. Note: Slabs which have felt coverings are not to be replaced, although Contractor is to also refer to repairs in regards to these areas.
5.1.2 | Contractors Design Portion - Supply and install new 150mm thick precast reinforced concrete cover slabs, over stair tower roofs. Crane slabs into place with suitable lifting equipment, allowing to provide lifting eyes on the slabs. Reinforcement to have minimum 50mm of cover. Requirements for fire resistance are to be as per BS EN 1992-1-2.
MAIN ROOF
5.2 | General
5.2.1 | Contractor is to ensure the below Schedule of Works details takes full precedence over the Langley Specification Document. It is noted that the below includes changes or refinements, with further comments also added. The Contractor is to ensure they price in full accordance with the below.
5.3 | SPECIFICATION REQUIRMENTS
5.3.1 | Guarantee: The following TA-30-W specification is to be covered by the Langley Waterproofing Systems Ltd, single-premium, pre-paid independently-insured workmanship and materials guarantee for a period of 30 years from the date of practical completion. In order to meet this requirement only roofing contractors that participate in this guarantee scheme may be used. The eligibility of proposed roofing contractors should be confirmed with Langley Waterproofing Systems Ltd, Tel: 01327 704778 prior to inviting tenders. Note: This system includes a 5 year annual maintenance programme where the roof area(s) will be inspected by the manufacturer. To deliver this annual maintenance programme for the first 5 years of guarantee, the client or building owner must supply suitable and safe access as per Langley T&Cs.
5.3.2 | Projects Under CDM: In relation to this project, under Construction (Design and Management) Regulations 2015 (CDM 2015), it is the responsibility of the Contractor to appoint any, or all, relevant "CDM duty-holders".
5.3.3 | Design Note - Warm Roof: This specification is based on a warm roof construction. The principal thermal insulation is above the structural deck.
5.3.4 | Tapered Insulation: When preparing a tapered scheme, a flat and level deck is assumed and,- the tapered scheme is intended to provide adequate drainage.
5.3.5 | Design Note - Changes & Adjustments: Variations 'A' (general): Any variations must be agreed in writing by both the contract administrator and Langley Waterproofing Systems Ltd. These must be costed and authorised by the client but not be implemented until instructed by the client. Variations 'B' (minor): During work in progress, Langley Waterproofing Systems Ltd must be informed immediately of any proposed change/s and operatives must not implement any change/s until agreed by Langley (minor changes are deemed to be any item not falling within the scope of section a). Unauthorised Changes 'C' (general): Langley Waterproofing Systems Ltd will not be responsible for any changes of which they are unaware or have not authorised, nor will they accept any liability or associated costs due to system failure, i.e. labour, materials, design or programme delays, etc., resulting from said changes. NOTE: The Contractor is required to be in compliance with a fully Langley approved product and will be bound by their requirements in doing so.
5.3.6 | Design Note - Approved Document Part B Building Regulations - Compartmented Walls: Removal of Existing Structural Deck and/or Waterproofing: Where the Langley Waterproofing system bridges a compartmented wall, the system must be laid on a substrate or deck rated class A2-s3, D2 or better (non-combustible) to BS EN 13501-1. Buildings below 15m high, the substrate or deck can be rated class B-s3, D2 or worse (combustible), such as timber boarding and battens but they must be fully bedded on mortar (or other no less suitable material) across the full width of the compartmented wall. Double-skinned insulated roof sheeting, such as standing seam or profile metal sheet roofing, should incorporate a band of material rated class A2-s3, D2 or better, a minimum of 300mm in width, centred over the wall. Note: Proposed specification and design will be subject to LABC (Local Authority Building Control) approval before works can commence on-site. Where appropriate, Langley Waterproofing can offer support and guidance to assist application.
5.3.7 | Roof Structure - Disclaimer: It is deemed the responsibility of the Client Representative, Contractor and / or Property Owner to give due consideration towards the ability of the existing roof deck accepting any additional loadings imposed by the application of the new waterproofing system proposed within this specification. Langley Waterproofing Systems Ltd will not be held responsible or accept any liability or associated costs should structural defects or structural failure occur. NOTE: Refer to Structural Report confirming additional loading. Contractor to ensure any issues with roof deck are to be re-laid to the Contract Administrator.
5.3.8 | Electronic Roof Integrity Test (Compulsory For Buried Systems) - Disclaimer: Prior to the installation of any proposed roof finishes, an electronic leak detection test must be carried out by a WITA approved contractor to ensure the integrity of the newly installed waterproofing system and to meet Langley Waterproofing Systems Ltd guarantee requirements. NOTE: Refer to completion requirements for pricing.
5.3.9 | Fire Risk - Drying Out: In the event of the roof becoming wet and drying out is necessary, the use of gas torches is not recommended and must be avoided. In all cases Safe2Torch guidelines should be followed. Standing water should be swept to the nearest outlets with a broom or squeegee (care must be taken to avoid debris blocking outlets). The remaining moisture should be soaked up using mops or dry rags and the surface left to dry out naturally. To speed up the process, specialist equipment is commercially available, see ‘General Guidance & Requirements’ in the appendices of this specification.
5.3.10 | Safe2Torch - Flame-free Zones: This specification has been compiled in accordance with the NFRC Safe2Torch guidance and includes areas that have been identified as presenting a risk of fire if gas torches are used. This requires the substitution of membranes in these areas.
5.3.11 | Flame-free Zones - Definition: A Flame-free Zone is defined as being within 900mm of a combustible substrate / material. Note: If combustible material forms part of an overhang then the Flame-free Zone starts from the extremity of the overhang.
5.3.12 | Risk Assessment - Fire - Installing Contractor: In line with their own Risk Assessment and Method Statement, the installing contractor is to identify any areas where the use of a naked flame is deemed too great a risk. This matter should be raised at the pre-start / pre-commencement meeting or stated in writing to Langley & the Contract Administrator, in order that an alternative flame free method can be adopted and specified.
5.3.13 | Flame-free Zones - Identified Risk Areas: In accordance with Safe2Torch guidance the following area/s have been designated as ‘flame-free’ zone/s: Detail Noted: Chimney Stack Upstand - Full SA Detail Noted: Skirting to Tank/Plant Rooms - Full SA Detail Noted: Door Cill - Full SA Detail Noted: Vertical Expansion Joints to Brick Upstands - Full SA Detail Noted: Exposed Timber - SA AVCL Only Whilst these area/s have been identified, they may not be definitive. Due allowance must be made so that at any stage of this project, should any additional areas be designated a fire risk by any of the parties involved, they must be logged, all parties informed, and the appropriate measures employed.
5.3.14 | Fire Accreditation: Unless otherwise stated, the full waterproofing system and/or products contained within this specification have been tested for external fire exposure (both with and without insulation) in accordance with BS EN 13501-5: 2005 (European Test) and are accredited as Broof(t4).
5.3.15 | Langley Detailed Drawings: This specification is to be read in conjunction with the detailed drawings issued and supplied by Langley Waterproofing. Should the contractor at any point find discrepancies between the issued specification and issued drawings, it is required that the specification takes precedence in all cases, unless otherwise notified and approved. No additional costs or liability arising from failure to follow specification or notifying Langley Waterproofing Systems Ltd of any discrepancies found in good time prior to commencement of works will be considered. NOTE: Drawings supplied are considered general drawings and likely to differ slightly as noted above.
5.3.16 | Guarantee Requirement - Torch-on Membranes: Applicable to all layers. A 5-10mm bead of bitumen must be exuded from all laps.
5.4 | SCOPE OF APPLICATION
5.4.1 | Existing Waterproofing System - Removal: This specification is based on a full strip-up of the existing waterproofing system.
5.4.2 | Deck and Substrates - Screeded Concrete: This specification is suitable for application to a screeded concrete roof deck not exceeding 5° from the horizontal.
5.4.3 | Removal of Existing Waterproofing System: Existing coverings must not be stripped at a rate greater than can be safely re-waterproofed during that working day so as to reduce risk of water ingress to the property. NOTE: A phased programme of work is to be identified, with the Contractor taking due precautions in achieving the above. In this case, it is necessary and required to mark out a roof plan, identifying areas of work in sections, demonstrating how the works will be staged.
5.4.4 | Day / Night Joints: The contractor must ensure at the end of each working day or period, that any exposed membranes or substrates that are susceptible to damage through water ingress are sealed with a Langley system compatible membrane to ensure complete water tightness. No loose laid membranes or other such covers are permitted.
5.4.5 | U-value - Tapered Insulation: To comply with Part L of the current Building Regulations, the average thickness of the scheme included in this specification is calculated in accordance with Annex C of BS EN ISO 6946: 2007. This is to ensure that the effective thickness of the scheme is sufficient to meet the target U-value of 0.12 W/m²K. Contractor must comply fully with the requirements of the June 2022 updated Building Regulations requirements and to check the materials and thermal performance meets or exceeds this requirement.
5.4.6 | Contractors Note - Tapered Insulation: The specified tapered insulation scheme is based on the assumption that the contours of the underlying substrate reflects that of the existing roof coverings. In the event of any abnormalities being uncovered, it is the responsibility of the Roofing Contractor to report these immediately to Langley and the Contract Administrator so that any amendments to the insulation scheme that may be necessary can be made. This may result in a delay. No claims arising from any additional costs incurred from such delays will be entertained by Langley Waterproofing Systems Ltd.
5.5 | PREPARATION
5.5.1 | Contractor Preparation Note: The contractor must take his own roof core samples to satisfy himself with regard to the existing roof build-up and ascertain the extent of the work involved in stripping up the existing roof coverings. No claims arising from failure to do so will be considered by Langley Waterproofing Systems Ltd. It is assumed that the existing core sample and structural report supplied by the Structural Engineer and appended to the Specification of Works can be used, although it may be necessary to carry out additional core samples to verify other areas. The Contractor is to consult with Langley Waterproofing Systems Ltd if they are deemed to only rely on the Structural Engineers report and to verify this is accepted with them prior to commencing the roofing works.
5.5.2 | TV Aerials and / or Satellite Dish Arrays: Any TV aerials and / or satellite dish arrays that will impede roofing works are to be temporarily removed, raised, etc. to facilitate the works. The contractor must liaise with the client and contract administrator directly in relation to how best serve the property so that minimal disturbance of services is achieved throughout the contract period. The Contractor is to ensure the relocation positions are to be prior agreed with the Contract Administrator although to make such allowances required to install the new roof, complete with parapet wall modifications. Contractor is to be aware of the finishing detail as per the drawings and make due consideration to relocate these pipes, satellite dishes, aerials etc.
5.5.3 | Lightning Conductor Tapes - Discard: Remove and dispose of to suitable waste facilities. The contractor must allow for temporary alternative protection throughout the contract period until such time as a new system is installed.
5.5.4 | Wall Mounted Plant, Cable Trays / Conduits etc - Reposition (above skirting height): All wall mounted services and/or plant that will prevent facilitation of the works or will penetrate the new skirting heights. Raised and/or relocate. Allowance must be made for the following items as necessary: 1. Disconnection, de-gassing and re-connection, adaptation of all pipework, supports, connections, electrical connections and cabling. 2. Reposition (above skirting height) or relocate to suitable locations as required. Allow for all adaptions/adjustments and fixings required and re-connection. All in accordance with client’s detailed requirements. 3. Certify as fully serviceable on completion.
5.5.5 | Cables - Temporarily Remove: All cables must be carefully raised and / or temporarily supported clear of the roof surface to facilitate the works. Contractor is to allow to decommission as required and recommission on completion. Ensure Contractor fully has fully assessed the required works prior to submitting tender bid.
5.5.6 | Pipe Penetrations – New Boxing: Box out existing pipe penetrations with A1 non-combustible (EN 13501-1) Paradeck Cement Board, 20mm thick, magnesium oxide cement board. The contractor must include for all necessary metal top hats / metal stud and metal levelling shims, etc. Secure with substrate specific non-corroding alkali resistant fixings (wood or gypsum screws are not recommended) along all relevant supports. Interlocking joints between the boards to be glued. Any butt joints should be taped with pre-cut 200mm wide strips of Paradiene SA underlay. Before application of Paradiene SA, prime area with Langley Spray-on Primer and allowed to dry. Pipe penetrations require a Code 5 Lead sleeve, finishing a minimum of 150mm from the finished surface of the new boxing and terminated with a weathering collar or secured with a stainless steel Jubilee clip and sealed with a bead of gap seal mastic. Plastic pipe collars must be solvent welded. Finish base of vertical sleeve as previously stated. Note: Ensure that boxing is suitably insulated to prevent cold bridging / cold voids. Note: If any existing pipe insulation is removed when undertaking these works it must be replaced / renewed when recommissioned.
5.5.7 | External Rainwater Goods - Discard: Remove all existing gutters and associated downpipes, brackets, fittings, etc. and dispose of to suitable waste facilities.
5.5.8 | Tank Room Overflows / Scupper Outlets - Raise: Raise existing positions so they discharge above the new waterproof skirting height which must be a minimum of 150mm high. Block off redundant hole/s, prior to installing the new waterproofing system details. Allow for all modifications/adaptations to pipe work. Allow for raising and making good any internal bunding as necessary. Note: The contractor must not block off overflows or scupper outlets by detailing over with any new waterproofing membranes without prior approval from the Client Contract Administrator or Langley Waterproofing Systems Ltd.
5.5.9 | Existing Rainwater Chutes - Discard: Carefully remove and dispose of to suitable waste container.
5.5.10 | Existing Waterproofing System - Remove: Strip and remove to suitable waste containers all component layers of the existing waterproofing system including any insulation and or vapour control layers that may be found, back to but not including the original deck / substrate.
5.5.11 | Existing Edge Trims - Remove: Carefully remove all existing perimeter edge trims and dispose of to suitable approved waste containers / facilities or return to contractors premises for safe disposal.
5.5.12 | Existing Flashings - Remove: Carefully remove all existing secondary cover flashings and dispose of to suitable approved waste containers / facilities or return to contractors premises for safe disposal.
5.5.13 | Water Checks - Existing - Raise: Raise perimeter check kerbs to accommodate any presented increased height of the new waterproofing system. The contractor must ensure that a 50mm minimum height is achieved above the finished level of the new roofing system.
5.5.14 | Perimeters - Raising - Cover of External Faces: Where the height of external faces are to be increased, for whatever reason, any exposed timber or voids must be covered with new fascia boards or cladding. This must align with the top of the timber hard edge prior to fixing any drip batten or edge trims. The contractor must liaise with, and seek separate instruction from, the contract administrator as to the method, type and colour of materials, etc. to cover these external raised details. Claims arising from failure to seek client instruction prior to commencement of works or provide suitable cost provision for this item will not be entertained by Langley Waterproofing Systems Ltd.
5.5.15 | Redundant Chases - Make Good: Rake out and prepare any redundant chase lines. In-fill with sand and cement mortar, flush with wall face.
5.5.16 | Upstands to Brickwork - New Chase: In preparation of a new cover flashing the contractor is to cut a new chase to a minimum 25mm depth and at a minimum height of 150mm above the intended finished roof level surface. Brush clean and prime with appropriate primer to seal substrate.
5.5.17 | Parapet Wall & Coping Stones - Non-Combustible Construction - Overclad with Paradeck Cement Board: Overclad existing parapet wall top and inner face of parapet wall with A1 non-combustible (EN 13501-1) Paradeck Cement Board, 20mm thick, magnesium oxide cement board. The contractor must include for all necessary metal top hats / metal stud and metal levelling shims, etc. Secure with substrate specific non-corroding alkali resistant fixings (wood or gypsum screws are not recommended) along all relevant supports. Interlocking joints between the boards to be glued. Any butt joints should be taped with pre-cut 200mm wide strips of Paradiene SA underlay. Before application of Paradiene SA, prime area with Langley Spray-on Primer and allowed to dry.
5.5.18 | Over-cladding Parapets - Mitigate Cold Bridge Voids: The contractor must ensure, when over-cladding parapet details, that any voids formed between the back of the new vertical cladding and the inner face of the parapets, are infilled with insulation. The insulation infill must be a minimum thickness of 25mm and achieve a minimum height of 300mm vertically from any deck substrate. It is not a requirement to insulate the entire void unless specified to do so elsewhere within this document.
5.5.19 | Door Threshold/s - Raise Existing (ParaFlash B3): The threshold/s must be raised to allow a minimum skirting height of 150mm above the finished level of the main roof surface. Door/s and frame/s to be adapted as necessary and to include all decorative and security finishings. Install new ParaFlash B3, lead-free cover flashing/s, prior to re-fitting the threshold/s. The height of the threshold/s is to be such that the skirting / flashing height is the same as that on either side of the threshold/s. The contractor must confirm with the client / contract administrator the method and materials to be used to facilitate the raising of door threshold/s. Claims arising from failure to seek client instruction prior to commencement of works or provide suitable cost provision for this item will not be entertained by Langley Waterproofing Systems Ltd.
5.5.20 | Soil Vent Pipe/s - Extend: Extend where necessary. Collar or pipe sleeve/s must be a minimum of 150mm above the finished roof surface. Note: Extension pipe/s must be fixed inside the existing pipe/s.
5.5.21 | Flues - Extend: Extend where necessary. Collar or pipe sleeve must be minimum 150mm above the finished roof surface. Important Notes: a) Flues are controlled services as defined in Building Regulations Part J. b) Any work to flues may be notifiable building work. c) Flue extension must be of the correct material and same diameter or correct cross-sectional area to match the existing. d) Must be securely fixed and sealed to the existing so as to comply with either Gas Appliances Safety Regulations 1995 or relevant regulatory body.
5.5.22 | Existing Screed - Inspect and Repair: Upon exposure, contractor must thoroughly inspect for signs of damage or failure. Immediately inform Langley and / or the CA of findings for further instruction before proceeding to install the new waterproofing system. Any issues arising from failing to report defects will not be considered by Langley Waterproofing Systems Ltd. Where required, repair or renew any defective areas found and allow to dry to the application of the new waterproofing system. Note: Should screed removal be necessary, the contractor must consider the presence of underlying cables or conduits contained within the screed that may hamper remedial works.
5.5.23 | Priming Deck & Detail Substrates: All deck and detail substrate surfaces. Prime with Langley Spray-on (synthetic rubber) Primer and allow to dry.
5.5.24 | Flame-free Zones - Priming Requirement - All Surfaces (Inc Insulation if applicable): Prime all flame-free zone surfaces with Langley Spray-on (synthetic rubber) Primer and allow to dry (bituminous primer must not be used).
5.5.25 | Flame-free Zones - Self-adhesive Membranes - Additional Priming: Adhesion issues may arise when applying membranes with a hot-air gun. Langley Spray-on Primer can be applied to the surface Paradiene SA underlay to enhance adhesion of the Parafor Solo SA cap sheet. This ‘additional priming’ is also recommended when the Langley SA Membrane Detailing System is specified as the primary roof covering or over large areas. This will ensure a consistent bond across larger roof areas and improve application times
5.5.26 | Paradeck Cement Board Panel Joints - Tape: Cover panel joints with pre-cut 200mm wide strips of Paradiene SA underlay. Before application of Paradiene SA, prime area with Langley Spray-on Primer and allowed to dry. Butt joint at roll ends and perpendicular intersections.
5.6 | AIR AND VAPOUR CONTROL
5.6.1 | Air and Vapour Control Layer - Torch-on - Field Area: Install Parevapo SBS metal-lined, double reinforced, elastomeric air and vapour control layer. Top Face: Sanded. Underside: Macro perforated fusible film. Fully bond to prepared surface by torch-on method. Side and end laps to overlap by a minimum of 75mm and must be fully sealed by torch-on method.
5.6.2 | Flame-free Zones - Air and Vapour Control Layer - Change of Membrane - Flat Exclusion Area: Install Parevapo SA, double reinforced, metal-lined, self-adhesive SBS elastomeric bitumen air and vapour control layer. Fully bond to a prepared and primed substrate by means of the heat activated, self-adhesive face, applying pressure with a weighted roller. Side laps, minimum 75mm, end laps, 100mm, fully bond by heat welding and applying pressure with a seam roller. Priming of substrate must be with Langley Spray-on (synthetic rubber) Primer (bituminous primer must not be used). All heat activation and welding within the flame-free zone must be carried out with a hot-air gun. Note: All laps with main area AVCL, (outside the flame-free zone) must be minimum 150mm and torch bonded.
5.6.3 | Air and Vapour Control Layer - Detail Skirtings: Extend the air and vapour control layer as a separate flashing piece cut from full width of roll to the skirting. Fully bond by torch-on method to a fully prepared surface to a minimum height of 100mm past the finished proposed line of the new insulation level. A minimum of 100mm lap must be achieved to main field return. Side laps to be a minimum of 75mm and must be fully sealed by torch-on method.
5.6.4 | Flame-free Zones - Air and Vapour Control Layer - All Upstands, Skirtings & Details Generally: Extend Parevapo SA air and vapour control layer to the skirting / details as a separate flashing piece, cut from the width of a roll. Fully bond to a prepared and primed substrate by means of the heat activated self-adhesive face. Minimum height, 100mm above the finished height of the new insulation (or the full girth of details). Priming of substrate must be with Langley Spray-on (synthetic rubber) Primer, (bituminous primer must not be used). Lap to main field return, minimum 100mm, side laps minimum 75mm. Application method as per the main area. Detailing arrangements all as main specification.
5.7 | INSULATION
5.7.1 | Pararock Tapered Board Insulation - Field Area: Install Pararock stone wool tapered roof insulation boards. Lay with branded side uppermost. Boards to be laid close butted with staggered joints. Set out in accordance with tapered scheme drawings supplied by Langley Waterproofing Systems Limited.
5.7.2 | Pararock Tapered Insulation - Sumps to Outlets: Sumps to be a minimum of 500mm x 500mm square around outlet position. Form with Pararock flat board insulation. Board thickness in accordance with Tapered Scheme drawing. A Langley Metal Hard Edge to be fixed to all exposed insulation edges. Bond to insulation with either low foaming PU adhesive or strapping with suitable fully bonded underlay membrane.
5.7.3 | Pararock Insulation - PU Attachment: To prepared surface. Bond Pararock insulation with Lang-Stik Solvent Free PU Adhesive. Surface of substrate must be swept clear of all dirt, debris and loose material, prior to application of the adhesive. Boards to be laid close butted with staggered joints. Important Note: Please be aware of the additional fixing requirements and coverage rates for Pararock insulation. Refer to 'Fixing Instructions' and 'Schedule of Products' sections of this specification.
5.7.4 | Pararock Insulation - Dual Layer Applications: Where thicknesses in excess of 150mm are specified the contractor must allow for the installation of a second layer of boards and the additional adhesive required. Underlay boards to be fixed first, branded side uppermost. Fleece faced boards to be laid with the fleece uppermost. All boards to be laid close butted with staggered joints with the top layer off-set from the preceding one.
5.7.5 | Insulation - PU Attachment - Flame-free Zones: When using Parevapo SA, in designated flame-free zones, the insulation to these areas must be bonded with LangStik Solvent Free PU Adhesive. Surface substrate must be swept clear of all dirt, debris and loose material, prior to application of the PU adhesive.
5.7.6 | Insulation - Changes of Levels - Metal Hard Edge: Langley Metal Hard Edge to be fixed to all exposed insulation edges. Bond to insulation with either low foaming PU adhesive or strapping with suitable fully bonded underlay membrane.
5.7.7 | Priming - Hard Edges to Insulation: All hard edges, metal and / or timber, must be primed with Langley spray-on (synthetic rubber) primer and allow to dry.
5.8 | WATERPROOFING - UNDERLAYS
5.8.1 | Detail Reinforcing Strip - Requirement in Lieu of Angle Fillets: Paradiene (35) S R4 detail reinforcing strips must be installed at the base of all upstands prior to subsequent membranes being installed. At a minimum of 250mm width cut from roll, apply 125mm to the horizontal and 125mm to vertical prepared surfaces. Fully bond by torch-on method.
5.8.2 | Flame-free Zone - Detail Reinforcing Strip - Change of Membrane: Paradiene SA detail reinforcing strips must be installed at the base of all upstands, prior to subsequent membranes being installed. Strips to be minimum 250mm wide in pieces cut from roll, applied 125mm to the horizontal and 125mm to vertical surfaces. Fully bond to a prepared (and primed if applicable) substrate by means of the heat activated self-adhesive face, applying pressure with a seam roller. Where priming is required, it must be with Langley Spray-on (synthetic rubber) Primer, (bituminous primer must not be used).
5.8.3 | Underlay - Self-Adhesive - Field Area: Adepar JS composite reinforced, SBS elastomeric bitumen membrane. Top Face: fusible film. Underside: sanded between self-adhesive strips with siliconised peel-off film over self-adhesive selvedge. Fixing: by means of factory-applied self-adhesive strips. Perimeters and Openings: 500mm wide, fully bond by torching. Side Lap: 80mm determined by selvedge. End Lap: minimum 120mm. The siliconised film is not fusible. Fixing Method: See Fixing Instructions. Note: 5-10mm bead of bitumen must be exuded from all laps.
5.8.4 | Flame-free Zone - Underlay - Change of Membrane - Flat Exclusion Area: Install Paradiene SA, polyester reinforced, self-adhesive SBS elastomeric bitumen membrane. Fully bond to a prepared and primed substrate by means of the heat activated self-adhesive face, applying pressure with a weighted roller. Side laps, minimum 75mm; end laps, minimum 100mm; fully bonded by heat welding and applying pressure with a seam roller. Priming of substrate (including insulation if applicable) must be with Langley Spray-on (synthetic rubber) Primer (bituminous primer must not be used). All heat activation and welding within the flame-free zone must be carried out with a hot-air gun. Note: All laps with main area underlay, (outside the flame-free zone) must be minimum 150mm and torch bonded.
5.8.5 | Underlay to Outlet Sumps & Internal / Integral Gutters: Paradiene (35) SR4 underlay (fully bonded) must be used (detailed elsewhere). Extend onto main field area by minimum 150mm.
5.8.6 | Underlay - Upstands & Skirtings: To be formed separately using Paradiene (35) S R4 underlay, cut from the width of the roll and torch applied fully bonded to base membrane by a minimum of 100mm. Both surfaces being bonded are heated with a required bead (5-10mm) of bitumen to be extruded from all head and side laps.
5.8.7 | Flame-free Zone - Underlay - Upstands & Skirtings - Change of Membrane: To be formed separately with Paradiene SA underlay, in pieces cut from the width of a roll. Fully bond to a prepared and primed substrate (or AVCL if applicable) by means of the heat activated self-adhesive face, applying pressure with a roller. Minimum height, 150mm above the finished height of the new insulation (or the full girth of details). Where applicable, priming of substrate must be with Langley Spray-on (synthetic rubber) Primer (bituminous primer must not be used). Lap to main field return, minimum 100mm; Side laps, minimum 75mm. Application method as per the main area. Detailing arrangements all as main specification.
5.9 | WATERPROOFING CAP SHEETS
5.9.1 | Cap Sheet - Torch-on - Field Area: Install Graviflex root resistant cap sheet. Graviflex is a torch-on polyester-reinforced, SBS-modified, elastomeric bitumen cap sheet with root-resistant additive for roof garden waterproofing. Lay: Fully bonded by torching 75mm minimum side lap widths as determined by the selvedge and minimum 150mm end laps. This layer is to be laid parallel to the under layer, breaking joints by at least 300mm. Both surfaces being bonded must be heated and a bead of bitumen exuded from all laps.
5.9.2 | Flame-free Zone - Cap Sheet - Change of Membrane - Flat Exclusion Area: Install Parafor Solo SA, polyester reinforced, self-adhesive, SBS elastomeric bitumen, dark grey granule faced cap sheet. Fully bond to the underlay by means of the heat activated self-adhesive face, applying pressure with a weighted roller. Side laps to suit selvedge (minimum 75mm); end laps, minimum 150mm; fully bond by heat welding and applying pressure with a seam roller. A 5-10mm bead of bitumen must be extruded from all laps. All heat activation and welding within the flame-free zone must be carried out with a hot-air gun. Note: All laps with main area cap sheet, (outside the flame-free zone) must be minimum 150mm and torch bonded.
5.1 | DETAILS
5.10.1 | Detail Skirtings - Requirement: All detail skirtings must be a minimum of 150mm above the finished roof surface level.
5.10.2 | Cap Sheet - General Detailing: Detail flashings. Form separately with Graviflex Cap Sheet cut from width of roll. Colour to match main field membrane. Fully bond by torching to the specified detail underlay membrane. Both surfaces being bonded must be heated and a 5-10mm bead of bitumen extruded from all head and side laps. Cap sheet detail must extend to a minimum of 150mm onto the main field area. Upstand heights must be a minimum of 150mm above the finished roof level.
5.10.3 | Flame-free Zone - Cap Sheet - General Detailing - Change of Membrane: Detail flashings to be formed separately using matching colour Parafor Solo SA Cap Sheet, in pieces cut from width of roll. Fully bond to the specified detail underlay by means of the heat activated self-adhesive face, applying pressure with a roller. Minimum height, 150mm above the finished height of the new system (or the full girth of details). Side laps to suit selvedge; end laps, minimum 150mm, bond by heat welding and applying pressure with a seam roller. A 5-10mm bead of bitumen is to be extruded from all laps. Lap to main field return, minimum 150mm.
5.10.4 | Underlay Details - Outlet Sumps: Install Paradiene (35) S R4. To extend onto main field area by minimum 150mm in all directions. Fully bond to substrate.
5.10.5 | Lead Chutes (new): Code 5 lead. Form full-height lining to sides of opening/s with a 25mm turn-in under the bridging. Return onto outer wall face with step flashing wings dressed into chases in brickwork. Prime both surfaces of flange and fully bond between underlay or soaker and cap sheet. Both layers to be lapped onto the lead by at least 150mm.
5.10.6 | Lightning Conductor Tapes: Secure with straps of matching polyester reinforced cap sheet 50mm wide, bonded to roof surface. Straps to be at max. 1m centres (or as otherwise directed).
5.10.7 | Counter Flashing - ParaFlash B3: Install and protect detail abutment skirtings with ParaFlash B3 lead-free counter flashings 150mm wide. Dress into prepared chase and wedge at 450mm centres with stainless steel clips provided. Point with Langley Gap-Seal Mastic. Side laps to be a minimum of 100mm and sealed with Langley Lap Adhesive.
5.10.8 | Exposed Edges - Adapted Counter Flashing - Langley TB62 GRP Termination Bar: For protection of exposed vertical and horizontal waterproofing details (as required to suit site conditions). Install an adapted Langley TB62 GRP face-fixed Termination Bar. Modify by removing the bottom return section by cutting. Fixing modified bar over the membrane: Apply a continuous bead of Langley Gap-Seal Mastic along the edge of the membrane and another along the surface of the membrane (approximately 40mm from, and parallel to, the exposed edge). Position bar over the membrane with the angled return facing the substrate and protecting the exposed edge of the membrane. Once aligned, secure in place by mechanically screwing and plug fixing with dome or pan head non-corroding screws at maximum 300mm centres.
5.10.9 | Skirting to Threshold / Cill - ParaFlash B3: Install and protect detail abutment skirtings with ParaFlash B3 lead-free counter flashings 150mm wide. Dress into prepared chase below threshold / cill and wedge at 450mm centres with stainless steel clips provided. Point with Langley Gap-Seal Mastic. Side laps to be a minimum of 100mm and sealed with Langley Lap Adhesive.
5.10.10 | Skirtings - Vertical Waterproofing Over 400mm in Height Additional Mechanical Fixing Required: Additionally secure with concealed fixings either by nailing or with screws and pressure plates. Laps must be a minimum of 160mm. Nailing: Large headed galvanised steel clout nails set at 75mm centres in two rows 50mm apart. Screws: Maximum 200mm centres with 5 No. minimum per sheet width.
5.10.11 | Paradeck Cement Board Clad Parapets - ParaTrim GRP Edge Trim: Parapets are to be clad in Paradeck Cement Board (as specified above). Base layer and detail cap sheet layer of new waterproofing system must be carried up the vertical inner face and across the top of the parapet detail, which must be, in all cases, fully supported. Terminate to leading edge with a new ParaTrim GRP edge trim of an appropriate profile for the site conditions applied over the base layer membrane. Where required, at the ends of parapets, the waterproofing must be turned up and to the side, to allow weathering with new horizontal and vertical cover flashings. Screw fix at maximum 300mm centres into firm grounds. Butt straps are to be inserted at all joints. Surfaces of trim in contact with membranes must be wiped clean and primed with Langley Primer and allowed to dry.
5.10.12 | Soil Vent Pipe - Cast Iron: Soil vent pipes must be a minimum of 150mm high from the finished level of waterproofing. Install new Code 5 Lead pipe sleeves with integral lead flange. Sleeves must be a minimum of 30mm higher than pipe. Flange must be a minimum of 100mm wide. Prime both surfaces of the flange. Fully bond to the underlay or soaker, prior to fully bonding the cap sheet membrane. Sleeves to be turned into top of pipe by 25mm. Colour: Black. Note: Soil vent pipes greater than 300mm require a Code 5 Lead sleeve finishing a minimum of 150mm high above the finished level of the new waterproofing system and terminated with a weathering collar. Finish base of vertical sleeve as previously stated.
5.10.13 | Vent Pipes - Refurbish with LangVent: Install LangVent refurbishment vent pipe sleeves. Select correct size to suit the diameter of the existing pipe. Fix in accordance with Langley Fixing Instructions with flexible flange fully bonded between underlay or soaker and cap sheet membranes. Base of vertical sleeve, seal with a fillet of Langley Gap-Seal Mastic against the cap sheet membrane and the sleeve base. Colour: Black.
5.10.14 | Penetrations - Vertical Pipes General: Install new Code 5 Lead pipe sleeves with integral flange. Sleeve minimum 150mm high with flange base at a minimum of 100mm wide. Prime both surfaces of flange and fully bond between underlay or soaker and cap sheet. At top of sleeve protect as follows; Up to 200mm high, turn lead into top of pipe by approximately 25mm. Over 200mm high, install suitable weathering collars or secure with a stainless steel Jubilee clip and seal with a bead of gap seal mastic. Plastic pipe collars must be solvent welded.
5.10.15 | Horizontal Pipe Penetrations (Turned In) - General: Install new Code 5 Lead pipe sleeves with integral flange. Sleeve minimum 150mm high with flange base at a minimum of 100mm wide. Prime both surfaces of flange and fully bond between underlay or soaker and cap sheet. At top of sleeve protect as follows; Up to 200mm high, turn lead into top of pipe by approximately 25mm. Over 200mm high, install suitable weathering collars. Plastic pipe collars must be solvent welded.
5.10.16 | Horizontal Pipe Penetrations (Clip and Mastic) - General: New Code 5 lead pipe sleeve with integral flange. Flange to be minimum 100mm wide, prime both surfaces. Prepare surrounding wall face. To a primed surface, fully bond the specified underlay (or soaker), which must extend minimum 100mm (in all directions) beyond the lead flange. Fully bond lead flange to the underlay (or soaker), prior to fully bonding the specified cap sheet over the flange. Cap sheet to extend minimum 50mm beyond the underlay. Secure top and sides of waterproofing with a TB62 Termination Bar. Secure sleeve to pipe with a stainless-steel jubilee clip and a bead of Gap-Seal mastic.
5.11 | GREEN ROOF APPLICATIONS
5.11.1 | Electronic Roof Integrity Test: Prior to the installation of any green roof components, an electronic leak detection test must be carried out by a WITA approved contractor to ensure the integrity of the newly completed waterproofing system and to meet guarantee requirements.
5.11.2 | Installation Note: Installation of the green roof waterproofing and components can only be carried out by a Langley approved contractor whose workmanship is regularly checked during the contract by authorised Langley technical personnel.
5.11.3 | Green Roof Installation: Refer to Eco Green Roofs detailed green roof specification.
5.12 | SAFETY SYSTEMS
5.12.1 | OMITTED FROM SPECIFICATION
5.13 | COMPLETION
5.13.1 | Guarantee Requirement - Final Inspection: In accordance with our guarantee requirements, Langley Waterproofing Systems Ltd are to be notified once all works are complete. A final inspection will then be undertaken by us and the contractor must ensure that safe working access is provided.
5.13.2 | TV Aerials and / or Satellite Dish Arrays: Reinstate to original locations or new positions as instructed by the client contract administrator all TV aerials and / or satellite dish arrays.
5.13.3 | External Rainwater Goods - New: Upon completion of roofing works, install new external rainwater goods. The contractor must allow for any modifications / adaptations necessary to accommodate any raised levels presented by the new roofing system. The contractor must further confirm with the client / contract administrator the type, style and colour of the new rainwater goods. No claims arising from failure to do so will be considered.
5.13.4 | Sacrificial Layers - Free-standing Plant / Handrails etc: All freestanding items. Install a sacrificial layer of cap sheet (granule surface down) under all load spreading supports / pads.
5.13.5 | Cables - Reinstate: Collate and support on cable trays if necessary. Secure cables to tray or to original locations and secure with plastic cable ties. If cable trays are used then they are to be rested on load-spreading bases on sacrificial pieces of cap sheet. Securely fasten trays to bases as required.
5.13.6 | Completed Roof Surface - General: Ensure visual inspection of all laps is undertaken to confirm integrity of system prior to final guarantee inspection. Sweep clean and remove debris to suitable waste container.
5.13.7 | Lightning Conductor System - New: Install new system all in accordance with client contract administrators requirements. The new system must be tested and certified operational by an approved specialist contractor. The roofing contractor must provide and install all necessary Langley Lightning Conductor Retention Clips to roof surface to secure the lightning conductor tape. Clips are to be set at no more than 1 metre centres to secure the tape. At lightning conductor corner intersection plates, clips are to be spaced away from the plates at not less than 150mm but no greater than 200mm.
5.13.8 | Arisings from Works: Remove from site all arisings for return to contractor storage or safe disposal.
TANK ROOM & STAIRWELLS
5.14 | SPECIFICATION REQUIRMENTS
5.14.1 | Guarantee: The following SA-30-C specification is to be covered by the Langley Waterproofing Systems Ltd, single-premium, pre-paid independently-insured workmanship and materials guarantee for a period of 30 years from the date of practical completion. In order to meet this requirement only roofing contractors that participate in this guarantee scheme may be used. The eligibility of proposed roofing contractors should be confirmed with Langley Waterproofing Systems Ltd, Tel: 01327 704778 prior to inviting tenders. Note: This system includes a 5 year annual maintenance programme where the roof area(s) will be inspected by the manufacturer. To deliver this annual maintenance programme for the first 5 years of guarantee, the client or building owner must supply suitable and safe access as per Langley T&Cs.
5.14.2 | Projects Under CDM: In relation to this project, under Construction (Design and Management) Regulations 2015 (CDM 2015), it is the responsibility of the client / contractor to appoint any, or all, relevant "CDM duty-holders".
5.14.3 | Design Note - Changes & Adjustments: Variations 'A' (general): Any variations must be agreed in writing by both the contract administrator and Langley Waterproofing Systems Ltd. These must be costed and authorised by the client but not be implemented until instructed by the client. Variations 'B' (minor): During work in progress, Langley Waterproofing Systems Ltd must be informed immediately of any proposed change/s and operatives must not implement any change/s until agreed by Langley (minor changes are deemed to be any item not falling within the scope of section a). Unauthorised Changes 'C' (general): Langley Waterproofing Systems Ltd will not be responsible for any changes of which they are unaware or have not authorised, nor will they accept any liability or associated costs due to system failure, i.e. labour, materials, design or programme delays, etc., resulting from said changes. NOTE: The Contractor is required to be in compliance with a fully Langley approved product and will be bound by their requirements in doing so.
5.14.4 | Roof Structure - Disclaimer: It is deemed the responsibility of the Client Representative, Contractor and / or Property Owner to give due consideration towards the ability of the existing roof deck accepting any additional loadings imposed by the application of the new waterproofing system proposed within this specification. Langley Waterproofing Systems Ltd will not be held responsible or accept any liability or associated costs should structural defects or structural failure occur. NOTE: Refer to Structural Report confirming additional loading. Contractor to ensure any issues with roof deck are to be re-laid to the Contract Administrator.
5.14.5 | Fire Risk - Flame-free System: This specification has been formulated on the basis that minimal hot works are required. Should the contractor / installer have reservations about any aspect of the specification proposal, or if during the course of the works any unforeseen items are discovered that present an actual or potential fire risk, they should contact the system manufacturer / supplier immediately so that safer methods can be agreed and implemented which do not compromise the integrity of the specification and / or its guarantees. Notwithstanding the foregoing, the contractor / installer is reminded that they have a duty of care and responsibility to carry out their own assessment of the proposed works with regard to the potential fire risk, and introduce working practices that takes any such risks into account.
5.14.6 | Fire Risk - Drying Out: In the event of the roof becoming wet and drying out is necessary, the use of gas torches is not recommended and should be avoided. In all cases Safe2Torch guidelines should be followed. Standing water should be swept to the nearest outlets with a broom or squeegee (care must be taken to avoid debris blocking outlets). The remaining moisture should be soaked up using mops or dry rags and the surface left to dry out naturally. To speed up the process, specialist equipment is commercially available, see ‘General Guidance & Requirements’ in the appendices of this specification.
5.14.7 | Fire Accreditation: Unless otherwise stated, the full waterproofing system and/or products contained within this specification have been tested for external fire exposure (both with and without insulation) in accordance with BS EN 13501-5: 2005 (European Test) and are accredited as Broof(t4).
5.14.8 | Langley Detailed Drawings: This specification is to be read in conjunction with detailed drawings issued and supplied by Langley Waterproofing. Should the contractor at any point find discrepancies between the issued specification and issued drawings, it is required that the specification takes precedence in all cases, unless otherwise notified and approved. No additional costs or liability arising from failure to follow specification or notifying Langley Waterproofing Systems Ltd of any discrepancies found in good time prior to commencement of works will be considered. NOTE: Drawings supplied are considered general drawings and likely to differ slightly as noted above.
5.14.9 | Guarantee Requirement - Torch-on Membranes: Applicable to all layers. A 5-10mm bead of bitumen must be exuded from all laps.
5.15 | SCOPE OF APPLICATION
5.15.1 | Overlay of Existing Felt: This specification is based on the overlay of an existing, prepared felt waterproofing system.
5.15.2 | Deck and Substrates - Existing BUR on Screeded Concrete: This specification is suitable for application to a prepared existing BUR felt system on a screeded concrete roof deck not exceeding 5° from the horizontal.
5.15.3 | Day / Night Joints: The contractor must ensure at the end of each working day or period, that any exposed membranes or substrates that are susceptible to damage through water ingress are sealed with a Langley system compatible membrane to ensure complete water tightness. No loose laid membranes or other such covers are permitted.
5.16 | PREPARATION
5.16.1 | Felt Drip Flashings - Discard: Carefully remove all existing felt drip flashings and associated timber drip battens and dispose to a suitable waste container / facilities or return to contractors premises for safe disposal.
5.16.2 | Existing Outlets - Refurbish with ParaFurb Outlets: Make ready to accept new ParaFurb Refurbishment Outlets (detailed elsewhere). Cut back and remove sufficient existing waterproofing from around the outlets and as required from the surrounding area to allow for correct installation. Important Note: ParaFurb Outlets must not be installed to outlet positions that already have an existing refurbishment outlet in place. Prior to ParaFurb Outlets being installed, any existing refurbishment outlets or lead sleeve inserts must first be removed and surrounding substrates made good.
5.16.3 | Loose Coverings and/or Patch Repairs - Remove: All loose coverings, patch repairs, etc. must be removed and discarded to suitable waste containers.
5.16.4 | Existing BUR Felt Surface - Flame-free System - Preparation: All ridges and blisters in the existing waterproof membranes must be star cut, heated with a hot-air gun only and smoothed out. Seal cut areas with pieces of the specified underlayer, which must extend beyond the damaged area in any direction by a minimum of 100mm. Fully bond with a hot-air gun only to a prepared primed surface.
5.16.5 | Existing BUR Felt Details - Remove: Remove all existing BUR felt skirtings, drips, flashings to pipes, etc. to expose the substrate beneath. All waste to be disposed of to suitable approved waste facilities.
5.16.6 | Existing Edge Trims - Remove: Carefully remove all existing perimeter edge trims and dispose of to suitable approved waste containers / facilities or return to contractors premises for safe disposal.
5.16.7 | Existing Lead Flashings - Remove: Carefully remove all existing lead secondary cover flashings and dispose of to suitable approved waste containers / facilities or return to contractors premises for safe disposal.
5.16.8 | Water Checks - Existing - Raise - If Necessary: Raise perimeter check kerbs to accommodate any presented increased height of the new waterproofing system. The contractor must ensure that a 50mm minimum height is achieved above the finished level of the new roofing system.
5.16.9 | Perimeters - Raising - Cover of External Faces: Where the height of external faces are to be increased, for whatever reason, any exposed timber or voids must be covered with new fascia boards or cladding. This must align with the top of the timber hard edge prior to fixing any drip batten or edge trims. The contractor must liaise with, and seek separate instruction from, the contract administrator as to the method, type and colour of materials, etc. to cover these external raised details. Claims arising from failure to seek client instruction prior to commencement of works or provide suitable cost provision for this item will not be entertained by Langley Waterproofing Systems Ltd.
5.16.10 | Fascia's and Soffits - New Rockpanel: Install new Rockpanel® fascia's (and soffits if required). The contractor must liaise with, and seek separate instruction from the client contract administrator as to the method of fixing, type and colour of materials to be used. Claims arising from failure to seek client instruction prior to commencement of works or provide suitable cost provision for this item will not be entertained by Langley Waterproofing Systems Ltd.
5.16.11 | Redundant Chases - Make Good: Rake out and prepare any redundant chase lines. In-fill with sand and cement mortar, flush with wall face.
5.16.12 | Upstands to Brickwork - New Chase: In preparation of a new cover flashing the contractor is to cut a new chase to a minimum 25mm depth and at a minimum height of 150mm above the intended finished roof level surface. Brush clean and prime with appropriate primer to seal substrate.
5.16.13 | Soil Vent Pipe/s - Extend: Extend where necessary. Collar or pipe sleeve/s must be a minimum of 150mm above the finished roof surface. Note: Extension pipe/s must be fixed inside the existing pipe/s.
5.16.14 | Flues - Extend: Extend where necessary. Collar or pipe sleeve must be minimum 150mm above the finished roof surface. Important Notes: a) Flues are controlled services as defined in Building Regulations Part J. b) Any work to flues may be notifiable building work. c) Flue extension must be of the correct material and same diameter or correct cross-sectional area to match the existing. d) Must be securely fixed and sealed to the existing so as to comply with either Gas Appliances Safety Regulations 1995 or relevant regulatory body.
5.16.15 | Flues and Hot Pipes Insulating Double Skin: Independent non-ferrous metal sleeves with integral flange. Sleeve must be a minimum 150mm above finished roof surface, flange must be a minimum 100mm wide. Fix to roof deck. Sleeve must provide a minimum 25mm air gap. Note: The gap can be filled with a non-combustible insulation. See Details section for weathering detail. Important Notes: a) Flues are controlled services as defined in Building Regulations Part J. b) Any work to flues may be notifiable building work. c) Flue extension must be of the correct material and same diameter or correct cross-sectional area to match the existing. d) Must be securely fixed and sealed to the existing so as to comply with either Gas Appliances Safety Regulations 1995 or relevant regulatory body.
5.16.16 | Drip Battens - New: Install new 25mm x 50mm treated timber battens. Screw fix at max. 300mm centres.
5.16.17 | Priming - Felt Surfaces & Detail Substrates: Felt surfaces and substrates for details must be swept clean of all dirt, debris and loose material. In addition, all surfaces must be dry. Prime with Langley Spray-on (synthetic rubber) Primer and allow to dry.
5.16.18 | Flame-free System - Priming Requirement - All Surfaces (Inc Insulation if applicable): All surfaces receiving self-adhesive membranes. Prime with Langley Spray-on (synthetic rubber) Primer and allow to dry (bituminous primer must not be used).
5.16.19 | Flame-free System - Self-adhesive Membranes - Additional Priming Requirements: Langley Spray-on Primer should be applied to the surface Paradiene SA underlay (detailed elsewhere) to enhance adhesion before the application of the Parafor Solo SA cap sheet (ensure the primer is allowed to dry for a minimum of 30mins). This will ensure a consistent bond across larger roof areas and improve application times.
5.17 | WATERPROOFING - UNDERLAYS
5.17.1 | Flame-free System - Detail Reinforcing Strip: Paradiene SA detail reinforcing strips must be installed at the base of all upstands, prior to subsequent membranes being installed. Strips to be minimum 250mm wide in pieces cut from roll, applied 125mm to the horizontal and 125mm to vertical surfaces. Fully bond to a prepared (and primed if applicable) substrate by means of the heat activated self-adhesive face, applying pressure with a seam roller. Where priming is required, it must be with Langley Spray-on (synthetic rubber) Primer, (bituminous primer must not be used).
5.17.2 | Flame-free System - Underlay - Field Area (2 Layers): Install Paradiene SA, polyester reinforced, self-adhesive SBS elastomeric bitumen membrane. Fully bond to a prepared and primed substrate by means of the heat activated self-adhesive face, applying pressure with a weighted roller. Side laps, minimum 75mm; end laps, minimum 100mm; fully bonded by heat welding to base membrane with a minimum 100mm lap and applying pressure with a seam roller. Priming of substrate (including insulation if applicable) must be with Langley Spray-on (synthetic rubber) Primer (bituminous primer must not be used). All heat activation and welding must be carried out with a hot-air gun.
5.17.3 | Flame-free System - Underlay - Upstands & Skirtings: To be formed separately with Paradiene SA underlay, in pieces cut from the width of a roll. Fully bond to a prepared and primed substrate (or AVCL if applicable) by means of the heat activated self-adhesive face, applying pressure with a roller. Minimum height, 150mm above the finished height of the new insulation (or the full girth of details). Where applicable, priming of substrate must be with Langley Spray-on (synthetic rubber) Primer (bituminous primer must not be used). Lap to main field return, minimum 100mm; Side laps, minimum 75mm.
5.18 | WATERPROOFING CAP SHEETS
5.18.1 | Flame-free System - Cap Sheet - Field Area: Install Parafor Solo SA, polyester reinforced, self-adhesive, SBS elastomeric bitumen, dark grey granule faced cap sheet. Fully bond to the underlay by means of the heat activated self-adhesive face, applying pressure with a weighted roller. Side laps to suit selvedge (minimum 75mm); end laps, minimum 150mm; fully bond by heat welding and applying pressure with a seam roller. A 5-10mm bead of bitumen must be extruded from all laps. All heat activation and welding must be carried out with a hot-air gun.
5.19 | DETAILS
5.19.1 | Detail Skirtings - Requirement: All detail skirtings must be a minimum of 150mm above the finished roof surface level.
5.19.2 | Perimeter Kerb Detail - Requirement: All perimeter kerb details must be a minimum of 50mm above the finished roof surface level.
5.19.3 | Flame-free System - Cap Sheet - General Detailing: Detail flashings to be formed separately using matching colour Parafor Solo SA Cap Sheet, in pieces cut from width of roll. Fully bond to the specified detail underlay by means of the heat activated self-adhesive face, applying pressure with a roller. Minimum height, 150mm above the finished height of the new system (or the full girth of details). Side laps to suit selvedge; end laps, minimum 150mm, bond by heat welding and applying pressure with a seam roller. A 5-10mm bead of bitumen is to be extruded from all laps. Lap to main field return, minimum 150mm.
5.19.4 | Underlay Details - Outlet Sumps: Install Paradiene SA. To extend onto main field area by minimum 150mm in all directions. Fully bond to substrate.
5.19.5 | Internal Outlets - ParaFurb Refurbishment Outlets: ParaFurb Refurbishment Outlet: Stainless Steel spigot with expanding EPDM rubber seal and SBS membrane flange. Select outlet to suit diameter/s of fall pipes. Fully bond flange membrane to previously installed underlay or soaker. Fully bond cap sheet over and cut hole to suit diameter of pipe. Install leaf guard/grating supplied. Installation to be in accordance with Langley fixing instructions.
5.19.6 | Flues and Hot Pipes with Integral Insulating Double Skin: New, code 5 lead pipe sleeve/s with integral flange. Sleeve minimum 150mm high, flange minimum 100mm wide. Prime both surfaces of the flange and fully bond between underlay or soaker and cap sheet. Top of sleeve: Protect with a weathering collar, securely fixed to pipe Base of Sleeve. colour, black.
5.19.7 | Counter Flashing - ParaFlash B3: Install and protect detail abutment skirtings with ParaFlash B3 lead-free counter flashings 150mm wide. Dress into prepared chase and wedge at 450mm centres with stainless steel clips provided. Point with Langley Gap-Seal Mastic. Side laps to be a minimum of 100mm and sealed with Langley Lap Adhesive.
5.19.8 | Counter Flashing - Langley TB62 GRP Termination Bar - If Required: Where a chased counter flashing is impractical. Install and protect detail abutment skirtings with a Langley TB62 GRP face-fixed Termination Bar. Fixing: Position above the membrane skirting and apply two evenly spaced beads of Langley Gap-Seal Mastic to the rear surface of the termination bar before offering-up and positioning above the detail skirting. Once aligned, secure in place by mechanically screwing and plug fixing with dome or pan head non-corroding screws at maximum 300mm centres. Complete detail by applying a fillet of Langley Gap-Seal Mastic at 45° angle along the top edge of the bar to create a required water shed finish. Full contact of mastic must be maintained between the termination bar and substrate at all times.
5.19.9 | Exposed Edges - Adapted Counter Flashing - Langley TB62 GRP Termination Bar - If Required: For protection of exposed vertical and horizontal waterproofing details (as required to suit site conditions). Install an adapted Langley TB62 GRP face-fixed Termination Bar. Modify by removing the bottom return section by cutting. Fixing modified bar over the membrane: Apply a continuous bead of Langley Gap-Seal Mastic along the edge of the membrane and another along the surface of the membrane (approximately 40mm from, and parallel to, the exposed edge). Position bar over the membrane with the angled return facing the substrate and protecting the exposed edge of the membrane. Once aligned, secure in place by mechanically screwing and plug fixing with dome or pan head non-corroding screws at maximum 300mm centres.
5.19.10 | Kerbs - Welted Drip: Base layer and detail cap sheet layer of new waterproofing system must be carried up the vertical inner face and across the top of the kerb detail which must be, in all cases, fully supported. Welted Drips to be formed from detailing cap sheet (detailed elsewhere).
5.19.11 | Perimeter Edge - Welted Drip: At the perimeter edge, install new 25mm x 50mm treated timber drip battens. Screw fix at a maximum of 300mm centres. Welted Drips to be formed from detailing cap sheet (detailed elsewhere).
5.19.12 | Welted Drips: Form from detailing cap sheet membrane cut from the width of the roll. Form over 6mm exterior grade plywood (or alternatively 3mm hardboard) formers, mechanically fixed at 150mm centres to new treated timber drip battens. Fixings to be large headed galvanised clout nails set at 50mm centres, staggered vertically between 20-30mm. These must penetrate the drip batten by minimum 15mm. Membrane surfaces must be heated and a 5-10mm bead of bitumen must be extruded from all laps. Where required, at abutment junctions, the system must be turned up and to the side abutment, to allow weathering with new horizontal and vertical cover flashings. Note: Hardboard formers must be primed and allowed to dry prior to forming the drip detail.
5.19.13 | Soil Vent Pipe - Cast Iron: Soil vent pipes must be a minimum of 150mm high from the finished level of waterproofing. Install new Code 5 Lead pipe sleeves with integral lead flange. Sleeves must be a minimum of 30mm higher than pipe. Flange must be a minimum of 100mm wide. Prime both surfaces of the flange. Fully bond to the underlay or soaker, prior to fully bonding the cap sheet membrane. Sleeves to be turned into top of pipe by 25mm. Colour: Black. Note: Soil vent pipes greater than 300mm require a Code 5 Lead sleeve finishing a minimum of 150mm high above the finished level of the new waterproofing system and terminated with a weathering collar. Finish base of vertical sleeve as previously stated.
5.2 | COMPLETION
5.20.1 | Guarantee Requirement - Final Inspection: In accordance with our guarantee requirements, Langley Waterproofing Systems Ltd are to be notified once all works are complete. A final inspection will then be undertaken by us and the contractor must ensure that safe working access is provided.
5.20.2 | External Rainwater Goods - Reinstate - As Appropriate: Upon completion of roofing works, reinstate all original external rainwater goods. The contractor must allow for any modifications / adaptations necessary to accommodate any raised levels presented by the new roofing system and replace any broken or damaged items to match existing.
5.20.3 | External Rainwater Goods - New - As Appropriate: Upon completion of roofing works, install new external rainwater goods. The contractor must allow for any modifications / adaptations necessary to accommodate any raised levels presented by the new roofing system. The contractor must further confirm with the client / contract administrator the type, style and colour of the new rainwater goods. No claims arising from failure to do so will be considered.
5.20.4 | Internal Rainwater Outlets - ParaFurb Refurbishment Outlets: Check for blockages. Clear if necessary and leave in a free-running condition. Ensure bung is tightly secured to form correct pressure seal to pipe/s for applicable units. Ensure all supplied leaf guard / gratings are in place and tightly secured.
5.20.5 | Completed Roof Surface - General: Ensure visual inspection of all laps is undertaken to confirm integrity of system prior to final guarantee inspection. Sweep clean and remove debris to suitable waste container.
5.20.6 | Arisings from Works: Remove from site all arisings for return to contractor storage or safe disposal.
5.21 | SCHEDULE OF PRODUCTS
5.21.1 | Refer to Langley Specification, appended to the tender documents for full details of products specified/abbreviated, which are to be used as part of all of the above works.
TOTAL ROOF WORKS |  |  |  | 0

## Green Roof. EGR
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item | Description | Quantity | Units | Rate
PART SIX - THE WORKS
GREEN SEDUM ROOF WORKS
8.1 | Installers
8.1.1 | The installation of the green roof is to be completed by a Trustmark & PAS 2030 certified installer. The works are to be completed in full compliance with PAS 2030 and PAS 2035, in order to secure relevant funding.
8.1.2 | The installation of the green roof is to be completed by a Langley approved contractor.
8.1.3 | Refer to Eco Green Roofs, 3 Rays Farm Barn, Ingatestone Essex, CM49EH for details of design and clarification on design queries.
8.1.4 | It is expected that the works are to be completed by: Eco Green Roofs, 3 Rays Farm Barn, Ingatestone Essex, CM49EH or otherwise an equal and approved contactor/installer. Submit full details and clarification on proposed contractor/installer within tender bid.
8.1.5 | Refer to Eco Green Roofs detailed green roof specification found in Appendix J.
8.2 | Installations Generally
8.2.1 | Preparation: Clear all surfaces of debris Timing: After certification of waterproof membrane integrity. Surface condition: Visually inspect waterproof membrane, report any damage. Faults in waterproof membrane: Report prior to commencement of works. Contamination: Do not use materials detrimental to healthy growth of plants. Storage: Do not overload – point loads avoid. Outlets: Do not block. Outlet grilles: Installed.
8.3 | Adverse Weather
8.3.1 | Unfinished work: Secure for damage and wind uplift Conditions: Do not install or work with frozen materials
8.4 | Drainage Layer Installation
8.4.1 | Extent: Loose lay continuously over areas that will be vegetated. Fitting: Close butt-joint boards or rolls; staggering joints if applicable. Upstands: Cut to fit from penetrations and outlets, using a retractable knife.
8.5 | Filter Membrane Installation
8.5.1 | Extent: Loose lay continuously over entire roof area. Fitting: Loose laid (bonded to drainage board). Joints: Minimize. - Overlaps (minimum): 150mm overlap excess on drainage roll.
8.6 | Growing Medium Installation
8.6.1 | Handling: Minimize handling. Deliver to roof in small sacks, bulk bag, or pump, spreading the specified depth on to filter sheet, allowing for a settlement factor of 20% Conditions: Handle in the driest condition possible. Do not handle or install when wet or frozen. Layers: - Depth (Max): 60mm deep (sedum), 100mm (biodiverse) - Sequence: Gently firm each layer before spreading the next. Rake smooth and flat. Aerate before laying. Planting medium: Material: Lightweight crushed brick & expanded clay substrate. Inorganic and organic growing medium consisting of crushed brick, expanded clay and organic matter of composted bark fines. (Max. organic matter: 20%) Depth: 60mm (25mm within sedum blanket to total 85mm root zone) Declaration of analysis: Submit. - Porosity: 63% - Water Holding Capacity: 25-30% - Bulk Density DIN EN 1097-3: 850 T/m3 - Density at Max Water Holding Capacity: 1.25 T/m3 - PH Value: 7.0 – 8.0 Planting requirements: Various Sedum species on a pre-established blanket; Vegetation Coverage: 90% minimum.
8.7 | Vegetation Installation
8.7.1 | Handling Blankets - Extent: Continuous over area to be planted - Timing: Not to be installed if temperature is below 0˚C - Storage: Must be stored in a cool and shaded area; not to be stacked vertically or excessively Application - Sedum blankets to be installed within 48 hours of delivery. Roll out already grown blankets. Irrigate to saturation. - Watering: Thoroughly, after laying and account for climatic variation and seasonality - Seed: Hand Cast 3g/m2.
8.8 | Irrigation
8.8.1 | Irrigation is required for 8-10 weeks of the initial establishment and dry spells. Temporary irrigation system to be provided to support this.
8.8.2 | Option Cost (Contractors Design Portion) - Allow to supply and install a permanent irrigation system to the green roof as per Eco Green Roofs Performance Specification requirements, provided in Appendix G.4. Allow to provide bib tap or isolation valve 1" or 3/4" with a water pressure of 2.5-3.5 bar at the bib taps. Contractor is to assess and determine all modifications required to support this installation and where upgrades are necessary, to be included in this cost, which will be all BWIC with new supply, brought to roof level.
8.8.3 | P/S - Contractor to allow a provisional sum for obtaining a new water supply to the property to achieve between 2.5 bar - 3.5 bar pressure, as noted above. Contractor will be responsible for arranging and coordinating the new supply with the local water supplier. | P/S |  | 3000
8.9 | Edge Retaining Profile Installation
8.9.1 | Cutting: Neat, accurate and without spalling - Junctions: vertical, secured using proprietary connectors Position: True to line and level. Smooth continuous lines Fixing: Loose laid onto fleece with cobbles ballasting the horizontal leg Suitable for pitched roofs of 5 degrees or less
8.1 | SPECIFIC INSTALL REQUIREMENTS
8.10.1 | Edge Retention/Drainage Trim: Install to all perimeters Langley Retention Drainage Trim to match depth of green roof components above waterproofing finished level, It is a non-penetrative product and must be fully bonded by torching in 800mm lengths of Graviflex cap sheet cut from across the width of a roll. A space of 200mm is to be left between each Graviflex flashing along the flat run of the trim. Butt joint the Graviflex flashing to the internal angle fully covering the base plate (widths vary) of the retention trim and lap onto the main field cap sheet by a minimum 100mm (as per detail drawing). The retention drainage trims must be primed with Langley primer on the base plate top face only and allowed to dry prior to installation.
8.10.2 | Ballast Margins: Install Langley 20-40mm Washed Stone ballast is to all perimeter margins, up-stands, abutments and service penetrations to the corresponding depth of the total green roof build-up. This is to create a firebreak and also to keep root growth away from vulnerable detail points. Installation Guidance Notes; • Roof Areas above 50m² at perimeters this is to be a minimum of 500mm wide x by depth of adjacent system. • Roof Areas above 50m² at penetrations and abutments this is to be a minimum of 300mm wide x by depth of adjacent system.
8.10.3 | Ballast Margins: In line with the above, the Contractor is to ensure that the chimney stacks are considered a penetration and therefore to include the 300mm ballast margin around these stacks. It is noted that the tender drawings do not show these margins around stacks, although to be fully included in their costs. Hard edge trim details are required at this junction between the sedum blanket and ballast.
8.10.4 | Sedum Blanket: Install as a priority measure, immediately upon arrival to site, Langley Pre-Grown Sedum Mats. The mats are to be loose laid and tightly butt jointed in order to form a continuous landscape. Ensure that no vegetation is trapped between the joints. Contingency design measures may be necessary in areas of high wind uplift. Installation Guidance Notes: • The optimum time to install the Sedum Mats is late September through to early October or late March through to early April. • Do not install mats if frost is likely. • Watering-in is required during the first week post installation, however, Do not water in direct sunlight. • Under no circumstances are the Langley Sedum Blankets to be laid directly to the waterproofing finished surface. All Blankets must be installed to a Growing Medium Substrate.
8.11 | COMPLETION
8.11.1 | Inspection Timing: Prior to handover - Notice period (minimum): 3 working days
8.11.2 | General: Leave the works in a clean and tidy condition Surfaces: Clean immediately prior to handover Outlets: Clean and clear of any obstructions Completed green roofs: Protect from adjacent or high level working as best as possible
8.11.3 | Timing: Submit at handover Contents: - Growing Medium declaration of analysis - Manufacturer’s guarantees and warranties - Maintenance Procedures - Record Drawings showing the location of planting and associated features Number of copies: 2
TOTAL GREEN ROOF WORKS |  |  |  | 3000

## Solar PV
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item | Description | Quantity | Units | Rate
PART SEVEN - THE WORKS
MECHANCIAL, ELECTRICAL & PLUMBING
7 | SOLAR PV INSTALLATION
7.1 | General
7.1.1 | Contractors Design Portion - The Contractor is to provide a PV array in line with the outputs shown on the Solar Edge Designer Reports within Appendix J.5, which illustrates the arrays in sections, number of modules, inverters, optimisers, etc. The KWP power is to be achieved as outlined.
7.2 | Installers
7.2.1 | The installation of the green roof is to be completed by a Trustmark & PAS2030 certified installer. The works are to be completed in full compliance with PAS 2030 and PAS 2035, in order to secure relevant funding.
7.2.2 | The installation of the green roof is to be completed by a Langley approved contractor.
7.2.3 | Refer to Eco Green Roofs, 3 Rays Farm Barn, Ingatestone Essex, CM49EH for details of design and clarification on design queries.
7.2.4 | It is expected that the works are to be completed by: Eco Green Roofs, 3 Rays Farm Barn, Ingatestone Essex, CM49EH or otherwise an equal and approved contactor/installer. Submit full details and clarification on proposed contractor/installer within tender bid.
7.2.5 | Refer to Eco Green Roofs detailed green roof specification, including installation guidance documents, data sheets and technical information found in Appendix J.
7.3 | Flat Roof Mounting System for a Solar PV Installation
7.3.1 | 1. The measurements made on the site survey are checked, marks on the roof to indicate the planned positions of the panels as per the latest drawings. 2. Photograph the roof and the condition prior to commencement.
7.4 | Initial Mounting the Aluminium Bar and Solar PV Installation
7.4.1 | 1. The aluminium mounting system that make up the frame are set out into place. 2. Each bar is checked to make sure that it is straight and that all the bars are parallel to each other. 3. Safe pads to be put under mounting system to protect membrane. 4. Ensuring that the panels located to manufactures specifications. 5. If the length of the frame is longer than the aluminium bars supplied then they are spliced together using specially designed strips of aluminium and further bolts. 6. With the bars in place, and the frame complete the panels can start to be attached and clamped to the frame. A minimum of four clamps is used per solar panel, though in some cases extra clamps are used to aid the alignment of the rows. 7. The panels are either placed by row or by column depending upon which is the most practical in the specific situation.
7.5 | Panels Wiring for a Solar PV Installation
7.5.1 | Panels are wired by the manufacturer, meaning the rooftop connection is straightforward. See datasheet titled: TR JKM380-400N-6RL3-B-A2-EN and PDF titled Installation Method Jinko 1. Each panel is tested prior. 2. Each panels test result and serial number is recorded and the intended position as per the string design
7.6 | Panel Connecting Wires mounting the final PV Panel
7.6.1 | The DC isolator should first be fitted locked off and wires fed out through the sealed roof penetration to the required position on the roof. 1. Once all the panels have been installed and the final alignment checked the DC wiring for each string should be tested to insure continuity of the connections. 2. The PV array testing is done from the dc isolator and the test procedures strictly adhered too. 3. The AC supply is wired from the locked off inverter isolator. 4. The inverter is then connected to the ac isolator, and the dc isolator observing the correct polarity. 5. All cables will be neatly clipped and dc cables fitted with warning labels. 6. The installation will then be fitted with all the appropriate warning labels in the correct positions.
7.8 | Installation of inverter
7.8.1 | See PDF titled se_hd)wave_inverter_installation_guide.
7.9 | Installation of battery
7.9.1 | See PDF titled se-energy-bank-installation-guide
7.1 | Install Generation Meter
7.10.1 | See page 10 of PDF titled EMP1 basic versions user manual V1_0
7.11 | Commission Array
7.11.1 | Commission array in accordance with MSC certified guidance.
7.11.2 | The following documents are of particular relevance for the design and installation of the PV system and works to be completed in accordance with the below:: • Engineering Recommendation G83 (current edition) – Recommendations for the connection of small scale embedded generators (up to 16A per phase) in parallel with public low voltage distribution networks. • Engineering Recommendation G59 (current edition) – Recommendations for the connection of generating plant to the distribution systems of licensed distribution network operators. • BS 7671 (current edition) - Requirements for electrical installations (all parts – but in particular Part 7-712 Requirements for special installations or locations – Solar photovoltaic (PV) power supply systems). • BS EN 62446 (current edition) - Grid connected photovoltaic systems - Minimum requirements for system documentation, commissioning tests and inspection.
7.12 | Set up Monitoring
7.12.1 | See PDF titled se-single-phase-hd-wave-inverters-setapp-datasheet
7.13 | Completion
7.13.1 | A. Leave works in clean and tidy condition. B. Inspection by senior personnel and ensure full sign off. C. Handover to client and training to operate array to be provided for two sessions. D. Handover pack compiled. E. Handover pack issued.
TOTAL SOLAR PV WORKS |  |  |  | 0

## MEP
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item |  | Description | Quantity | Units | Rate
PART EIGHT - THE WORKS
MECHANCIAL, ELECTRICAL & PLUMBING
8.1 |  | WATER
8.1.1 |  | Redundant Water Services
8.1.1.1 |  | Allow for commissioning a survey to establish the extent of the water pipework in the form of a validation report. Provide report showing locations at roof level that needs to be retained, and the extent of pipework that is redundant so can be stripped out. Once the strip out works are complete, the Contractor is to ensure that record drawings indicating the location and function of any retained water pipework, are prepared and issued to the CA prior to handover.
8.1.1.2 |  | Allow a provisional sum of £5,000 to fully remove redundant water pipework, not in use and as directed by the Contract Administrator. |  |  | 5000
8.1.1.3 |  | Allow a provisional quantity of 50 l/m of lagging to replace at roof areas. Any adds or omissions are to be calculated on a pro-rata basis.
8.2 |  | LIGHTING
8.2.1 |  | Electrical Installations
8.2.1.1 |  | Carry out validation works, including a fixed wire testing of the electrical systems, to include the lighting systems in communal areas. Provide Electrical Installation Condition Report by a qualified electrician on completion. Testing to be carried out prior to lighting to confirm system is suitable for new lighting systems to be installed.
8.2.2 |  | Communal Areas; Light Fittings
8.2.2.1 |  | Contractors Design Portion - Design, supply and install replacement communal area light fittings to all communal areas. Allow to remove all existing fittings and carry out all associated modifications to layout to ensure even spread of regular light and emergency light fittings. Communal area lighting design to provide within circulation areas to be a minimum 150 lux (200 lux optimum), stair flights to be 150 lux (200 lux optimum) and landings to be 150 lux (200 lux optimum). Wall mounted light fittings to be positioned approx. 2.5m from floor level. The Contractor is to use Thorlux Prismalette 360 – Vandal-resistant Circular Luminaire light fittings for ceilings, soffits and walls. Lighting is to be operated via integrated microwave sensors and to have integrated CCT selectable Kelvin range. The Contractor is to provide full design for Contract Administrator approval ahead of orders being placed. Allow to make good any disturbed surfaces of relocated lighting.
a) |  | In consideration of the above, the Contractor is to provide proposals fully in accordance with the RBKC Communal & Emergency Lighting General Specification, refer to Appendix J.6.
b) |  | Proposals to achieve the above with support by way of lighting calculations and drawings. Refer to Thorlux Lighting for assistance: Tim Davy Tim.Davy@thorlux.co.uk Direct UK Sales Line: +44(0)1527 583 222. Mob: 44 (0)7767 273019
8.2.2.2 |  | Contractors Design Portion - Provide emergency exit running man signage to all floors, as per specifcication to all stair lobby locations.
8.3 |  | DRAINAGE
8.3.1 |  | Modifications
8.3.1.1 |  | To the basement staircase on Bramley Road side, modify existing PVC downpipe detail by cutting back downpipe 1m from horizontal bend section and installing a 112.5 degree bend pipe to match existing with PVC-U pipe. Connect length of pipe and install further collar meeting the horizontal section, close to the parapet wall junction. Allow for all necessary connections, clips, plastic welds etc. necessary to install.
8.3.2 |  | Repairs
8.3.2.1 |  | Rod and flush through all downpipes with high pressure jetting, remove debris and leave external plumbing goods in proper working and free-flowing order.
8.3.2.2 |  | The Contractor is to commission a CCTV survey of the existing SVP’s, including all access and equipment required to safely do so. The survey will need to cover: direction of flow, pipe sizes, use of pipework, pipe materials and structural condition. Also provide a detailed site map, still images of any major defects and survey footage with relevant recommendations provided to rectify any faults found.
8.3.2.3 |  | Provide a cost for relining 1no. full building height Soil Vent Pipe, including all required lateral cuts. Further repairs are to be calculated on a pro-rata basis.
8.3.2.4 |  | All exposed SVP sections above roof line are to be degreased, wire brushed, prepared and redecorated. Apply 1 coat primer and 2 coats of enamel paint in black.
8.3.2.5 |  | Remove all existing cages to tops of SVP's and provide and fit new black soil vent cowls.
8.3.2.6 |  | For the Main Contractor’s guidance only a quotation for these works dated 6th April 2021 has been obtained from 'London Drainage Facilities'. If used; the Contractor should allow for all costs in connection therewith, including profit, attendances, management etc. In no circumstances is the Contractor to classify 'London Drainage Facilities' as a nominated subcontractor. All risk associated will be attained to the Main Contractor.
8.3.2.7 |  | With full reference to the CCTV below ground drainage survey, completed by M&O Construction & Civil Engineering ltd, dated 02 June 2020; Ref: CCPR2000 (refer to Appendix L for report), provide repair costs for the below:
| a) | Page 5 MH02 (D/S) MH03 Clean line first then to install x2 100mm Epoxy patch repairs to faults noted at 0.40Mtrs & 0.84 Mtrs.
| b) | Page 8 MH03 (D/S) MH04 To fully clean line with specialist Picote equipment, To descale line flush line and re-survey and supply report findings accordingly.
| c) | Page 26 MH04 (D/S) MH11 To fully clean line with specialist Picote equipment, To descale line flush line and re-survey and supply report findings accordingly.
| d) | Page 32 MH13 (U/S0 PIPECMH13 Clean line first then to install x1 100mm Epoxy patch repair to fault noted at 7.93Mtrs.
| e) | Page 41 MH21 (U/S) PIPECHM21 Clean line first then to install x 3 100mm Epoxy patch repairs to faults noted at 3.30Mtrs 5.39 Mtrs & 7.0Mtrs.
| f) | Page 65 MH10 (D/S) JNMH10 To fully clean line with specialist Robotic cutting equipment, To cut encrustation from line flush line and re-survey and supply report findings accordingly.
| g) | Page 73 MH15 (U/S) PIPECMH15 (100mm x 2.50Mtrs) Clean line first then Install structural liner utilising pressurised air inversion installation method to correct noted faults in this line.
| h) | Page 84 MH06 (U/S) PIPEDMH06 To fully clean line with specialist Picote equipment, To descale line flush line and re-survey and supply report findings accordingly.
| i) | Page 86 MH05 (U/S) PIPECMH05 Clean line first then to install x1 100mm Epoxy patch repair to fault noted at 0.90Mtrs.
8.3.2.8 |  | Install new 18mm marine grade plywood boxing around vent pipes to roof, leaving top section able to vent out. Allow to paint in RAL colour TBC by Contract Administrator.
8.3.2 |  | Rainwater Goods
8.3.2.1 |  | Remove defective cast iron rainwater pipework and associated branch to rainwater outlet, complete with holderbats and fittings; disposal; replace with new cast iron pipe and branch; complete with holderbats and fittings; connections to existing pipes and branches; make good brickwork and walkways and soffits. Pipes between different walkway levels; approximately 3m long. Provisionally allow for 8 No. and further works are to be priced on a pro-rata basis.
8.3.2.2 |  | Take out defective rainwater outlets, disposal; replace with new; including connections to existing; make good walkways and soffits. Provisionally allow for 8 No. and further works are to be priced on a pro-rata basis.
TOTAL MEP WORKS |  |  |  |  | 0

## Prov Sums & Completion Req.
Schedule of Works
Bramley House, Bramley Road, LONDON, W10 6SX
Item | Description | Quantity | Units | Rate
PART NINE - THE WORKS
PROVISIONAL SUMS & CONTINGENIES
9.1 | Provisional Sums
9.1.1 | No distinction has been made between defined and undefined Provisional Sums, and the Contractor is deemed to have made due allowance in programming, planning and pricing preliminaries unless he has specifically identified such items on the Form of Tender.
9.1.2 | Allow for all preliminaries, management costs, general and special attendances.
9.2 | Contingency Sums
9.2.1 | The expenditure of contingency sums is only upon the express written instruction from the Contract administrator.
9.2.2 | Allow a contingency sum of £10,000 for repairs to existing roof, only to be expended as directed formally by the Contract Administrator. |  |  | 10000
9.2.3 | Allow a contingency sum of £5,000 for repairs/rebuilding Courtyard wall or railings, only to be expended as directed formally by the Contract Administrator. |  |  | 5000
9.2.4 | Allow a contingency sum of £5,000 for above ground SVP repair works, only to be expended as directed formally by the Contract Administrator. |  |  | 5000
9.2.5 | Allow a contingency sum of £1,000 for removing; storing; replacing on completion, Grenfell Tower memorial plaques, banners etc., only to be expended as directed formally by the Contract Administrator. |  |  | 1000
9.2.6 | Allow a contingency sum of £2,000 for replacing insulation on roof pipework with Armourflex or other repairs, only to be expended as directed formally by the Contract Administrator. |  |  | 2000
COMPLETION REQUIRMENETS
9.3 | Test Certificates
9.3.1 | Contractor to provide testing and commissioning certificates for all required elements and to satisfy Building Control sign off. To include, but not limited to: - Electrical Work; - Emergency Lighting; - PV Install; - Roof Guarantees; - etc.
9.4 | Leak Testing
9.4.1 | Contractor to provide an electronic leak test of the roof by a WITA approved contractor, in accordance with the manufacturers guidelines and requirements. The sub-contractor used is to be first approved by the Contract Administrator. The Contract Administrator is also to be invited to attend the testing and is to be provided sufficient notice.
9.5 | General
9.5.1 | Contractor is to leave site clean and tidy, removing all rubbish accumulation.
9.5.2 | Upon completion of the works thoroughly clean the premises throughout, including windows, to ensure that the demises are left in clean condition. Allow to carry out a professional clean of site.
9.5.3 | Provide 3 No. hard copies of the Health & Safety & Operation & Maintenance File on completion of the works. File is to be set-out in a logical sequence with a contents section at the front and section dividers at relevant places. File is to contain full operation and maintenance manuals as appropriate and a DRAFT digital copy is to be provided for review to the Contract Administrator, before the final digital copy and 3 hard copies are provided.
9.5.4 | Allow to include a Client/CA training on the operation of the PV array, including a handover pack and allow to provide training over two separate sessions.
9.6 | Employer Contingency
9.6.1 | Allow an Employers Contingency of 5% of the contract sum. This sum is to be expended in part or in whole as only directed by the Contract Administrator by formal contract instruction. |  |  | 150
SUB TOTAL - PRELIMS |  |  |  | 0
SUB TOTAL - SECTION 1 (External Elevations, Walkways, Balconies, External Areas, Decorations & General MEP Works) |  |  |  | 0
SUB TOTAL - SECTION 2 (Windows & Doors) |  |  |  | 0
SUB TOTAL - SECTION 3 (Roof, Green Roof & Solar PV Works) |  |  |  | 3000
TOTAL |  |  |  | 3000