## DAC 1+DAC 2
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright Turnstile 1 out | Plowright Turnstile 1 in | Plowright Pass Gate out | Plowright Pass Gate in | Plowright Turnstile 2 out | Plowright Turnstile 2 in | Plowright Turnstile 1 out |  | Plowright GW05 IN | Plowright GW05 OUT | Plowright GC07 OUT | Plowright GC07 IN | Plowright GC18 |  |  |  | Plowright GS01 Inner out | Plowright GS04 out | [14 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | [12 empty] | Main Entrance
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | T | T | T | T | T | T | T | [9 empty] | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N/A | N | N/A | N | N/A | N | [9 empty] | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [9 empty] | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [9 empty] | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | ü |  |  |  | ü | ü
PSU No#

## DAC 3+DAC 4
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright GE01B IN | Plowright GE01B OUT | Plowright GE03B IN | Plowright GE03B OUT | Plowright GE04B OUT | Plowright GE04B IN |  |  | Plowright GE05E IN | Plowright GE05E OUT | Plowright GE05A OUT | Plowright GE05A IN |  |  |  |  | Plowright GE02B IN | Plowright GE02B OUT | Plowright GE07A OUT | Plowright GE07A IN | Plowright GE07B OUT | Plowright GE07B IN |  |  | Plowright GE09A | Plowright GE09B | Plowright GE12A | Plowright GE12B |  |  |  |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | [10 empty] | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | [10 empty] | N/A | N | N | N/A | N | N/A
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | [10 empty] | N/A | N/A | N/A | N/A | N/A | N/A
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate
PSU No#

## DAC 5+DAC 6
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright GE10A | Plowright GE10B | Plowright GE11A | Plowright GE11B |  |  |  |  | Plowright GE13A | Plowright GE13B |  |  | Plowright GE14 IN | Plowright GE14 OUT |  |  | Plowright GE08B | Plowright GE08A |  |  | Plowright GE16 | Plowright SBE05 out | Plowright SBE02 IN | Plowright SBE02 OUT | Plowright GE20/GE21 IN | Plowright GE20/GE21 OUT | Plowright GE20A/GE21 IN | Plowright GE20A/GE21 OUT | Plowright GMS03 out | Plowright GS03 out | Plowright GE20A/GS03 out |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M |  |  |  |  | M | M |  |  | M | M |  |  | M | M |  |  | M | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü |  |  |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N |  |  |  |  | N | N |  |  | N | N |  |  | N | N |  |  | N | N | N | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P |  |  |  |  | P | P |  |  | P | P |  |  | P | P |  |  | P | P | P | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü |  |  |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü |  |  |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü |  |  |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A |  |  |  |  | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü |  |  |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü |  |  | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 7+DAC 8
SITE: The Pirbright Institute, Pirbright
LOCATION: |  |  | Plowright GN28 Pass Through Hatch 1 | Plowright GN28 Pass Through Hatch 2 | Plowright GN35-2 IN | Plowright GN35-2 OUT | Plowright GN28 Pass Through Hatch 3 | Plowright GN28 Pass Through Hatch 4 | Plowright GN36 IN | Plowright GN36 OUT |  |  | Plowright GS02 out |  |  |  | Plowright GN37C OUT | Plowright GN37C IN | Plowright GN35-1 IN | Plowright GN35-1 OUT | Plowright GN15 IN | Plowright GN15 OUT | [10 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: |  |  | Plowright Pass Through Hatch 1 Out of Restricted Area | Plowright Pass Through Hatch 2 Out of Restricted Area |  |  | Plowright Pass Through Hatch 2 Into Restricted Area | Plowright Pass Through Hatch 1 Into Restricted Area
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | [9 empty] | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | [9 empty] | M | M | M
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N/A | N/A | N/A | N/A | [9 empty] | ü | ü | ü
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | N/A | N/A | N/A | N/A | [9 empty] | N | N | N
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | [9 empty] | P | P | P
Check void transactions | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [9 empty] | ü | ü | ü
Check standby power units operate |  |  | ü | ü | ü | ü | ü | ü | ü | ü |  |  | ü |  |  |  | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 9+DAC 10
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright GN14 IN | Plowright GN14 OUT | Plowright GN32-1 OUT | Plowright GN32-1 IN | Plowright GN37 OUT | Plowright GN37 IN | Plowright GN32-2 IN | Plowright GN32-2 OUT | Plowright GN27 IN | Plowright GN27 OUT | Plowright Dunk Tank IN |  | Plowright GN29 | Plowright GN28 IN | Plowright Dunk Tank OUT | Plowright GN28 OUT | Plowright FW19-2 | Plowright UPS05 IN | Plowright UPS05 OUT | Plowright GS01 ext IN | Plowright GS01 ext OUT |  |  |  | Plowright HS05 IN | Plowright HS05 OUT | Plowright UPS09 OUT | Plowright FW17 IN | Plowright FW17 OUT | Plowright UPS09 IN |  |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | [10 empty] | Plowright GN Dunk Tank 3 in |  |  |  | Plowright GN28 Dunk Tank 3 out
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M | M | [5 empty] | M | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [5 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N/A | N | N | N | N | N | N | N | N | N | N | [5 empty] | P | P | P | P | P | P | P | P | P | P | P
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | N/A | N/A | P | P | P | P | P | P | P | P | P | [5 empty] | P | P | P | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [5 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [5 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [5 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [5 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [5 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 11+DAC 12
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright FW05 OUT | Plowright FW16 OUT | Plowright FW19-1 | Plowright FW02 | Plowright FW03 | Plowright GS01 Int in |  |  | Plowright UPS01 OUT | Plowright UPS01 IN | Plowright HS01 OUT | Plowright HS01 IN | Plowright FW01 | Plowright FW05 IN |  |  | Plowright FW12A | Plowright FW14 | Plowright FW15B | Plowright FW15A |  |  |  |  | Plowright FW12B | Plowright FW13B | Plowright FW13A | Plowright FW16 in |  |  |  |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | Plowright FW06 | [12 empty] | Plowright FW06
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M | [6 empty] | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [6 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | P | P | P | P | N | P | P | N | N | N | [6 empty] | P | P | P | P | P | P | P | P
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | P | [6 empty] | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [6 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [6 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [6 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | [6 empty] | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 13+DAC 14
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright FE02B | Plowright FE05 | Plowright FE02A | Plowright FE30A | Plowright FE26 OUT | Plowright FE26 IN | Plowright FE08B | Plowright FE30 (reader shut relay in panel PSU) | Plowright UPS08 IN | Plowright UPS08 OUT | Plowright GS04 in | Plowright FE24 OUT | Plowright FE24 IN | Plowright FE43/FC07 APR Door | Plowright GS04 IN | Plowright GS04 OUT | Plowright FE10 | Plowright FE08A | Plowright FE35 | Plowright FE11 | Plowright GS03 | Plowright GE20A/GS03 In |  |  |  |  | Plowright FE41A | Plowright FE41B | Plowright FS03 OUT |  | Plowright FS03 IN |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 15+DAC 16
SITE: The Pirbright Institute, Pirbright
LOCATION: |  |  | Plowright FE39 OUT | Plowright FE39 IN |  | Plowright FE09 |  | Plowright SBE05 | Plowright HS03 IN | Plowright HS03 OUT | Plowright UPS03 IN | Plowright UPS03 OUT | Plowright GMS03 |  |  |  | Plowright FE19A | Plowright FE23 IN | Plowright FE24 OUT | Plowright FE29B OUT | Plowright FE29B IN (reader disable relay in panel PSU) |  |  |  | Plowright FE19B | Plowright FE40 | Plowright FE22-1 | Plowright FE36 | Plowright HS04 OUT | Plowright HS04 IN |  |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | [7 empty] | M | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | [7 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | N | N | [7 empty] | N | N | N | N | N | N |  | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | [7 empty] | P | P | P | P | P | P |  | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | [7 empty] | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | [7 empty] | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | [7 empty] | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [7 empty] | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | [7 empty] | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü
PSU No#

## DAC 17+DAC 18
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright FE18A | Plowright FE18B | Plowright FE36A | Plowright FE38 OUT | Plowright FE38 IN |  |  |  | Plowright FE21A | Plowright FE20 | Plowright FE22-2 | Plowright FE21B | Plowright FE17 |  |  |  | Plowright SS07 IN | Plowright SS07 OUT | Plowright UPS07 IN | Plowright UPS07 OUT | Plowright FN36/FC07 APR Door | [11 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M | M | M |  |  |  |  | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  |  |  |  | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | N | N | N | N | N |  |  |  |  | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | P | P | P |  |  |  |  | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  |  |  |  | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  |  |  |  | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  |  |  |  | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  |  |  | ü | ü | ü | ü | ü
PSU No#

## DAC 19+DAC 20
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright FN30B | Plowright FN03 | Plowright FN29B | Plowright FN04 | Plowright FN26 | Plowright FN30A | Plowright FN08 In |  | Plowright UPS02 IN | Plowright UPS02 OUT | Plowright FN05 | Plowright FN29A | Plowright FN23 | Plowright HS02 IN | Plowright HS02 OUT | Plowright GS02 in | Plowright FN17 | Plowright FN16 | Plowright FN32 OUT | Plowright FN32 IN | Plowright FN22-1 OUT | Plowright FN22-2 IN | Plowright FN22-1 IN | Plowright FN22-2 OUT | [8 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 21+DAC 22
SITE: The Pirbright Institute, Pirbright
LOCATION: | Plowright FN15 | Plowright FN31 | Plowright FN14B | Plowright FN28B |  | Plowright FN25 | Plowright FN08 Out | Plowright FN14A | Plowright FN12 | Plowright FN25 | Plowright FN11 | Plowright FN33 OUT | Plowright FN13B | Plowright FN33 IN | Plowright FN13A | Plowright FN28A | Plowright EC 1st Floor Plant Rm | Plowright EC Boiler Rm Left | Plowright EC Boiler Rm Right | Plowright EC LV Rm Front | Plowright EC LV Rm Rear | Plowright EC Water Tank Rm | Plowright EC Water Treatment Room | [9 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | S | S | S | S | S | S | S
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 23+DAC 24
SITE: The Pirbright Institute, Pirbright
LOCATION: | Pirbright Gate House Main Entrance | Pirbright Main Entrance Turnstile In | Pirbright Main Entrance Turnstile Out | Pirbright Main Entrance Barrier In | Pirbright Main Entrance Barrier Out | Pirbright Main Entrance Pedestrian Gate IN | Pirbright Main Entrance Pedestrian Gate OUT | [11 empty] | Ash/03 | Ash/02 IN | Ash/02 OUT | [11 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | Plowright Gate House Main Entrance | Plowright GH Barrier In | Plowright GH Barrier Out | Plowright GH Pedestrian Gate | Plowright GH Turnstile in | Plowright GH Turnstile out | [12 empty] | IAH Ash Building (First Floor Plantroom)
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | T | T | M | T | T | [12 empty] | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | [12 empty] | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | [12 empty] | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | [12 empty] | ü | ü | ü
Check door open alarm operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | [12 empty] | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | [12 empty] | F | F | F
PSU No#

## DAC 25+DAC 26
SITE: The Pirbright Institute, Pirbright
LOCATION: | Ash/10 IN | Ash/10 OUT | Ash/07 | teessstt | Ash/08 IN | Ash/08 OUT | Ash/09 IN | Ash/09 OUT | Ash/01 IN | Ash/01 OUT | Ash/06 | Ash/05 | PK3/01 | PK4/01 | PK1/01 | PK2/01 | Ash/11 | Ash/12 | [14 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | Directors Suite |  | Ash Building (IT Workshop) - Door to IT Workshop in Ash Building |  | Ash Building (IT Server Room D/L) - Double Door to Ash IT Server Room |  | Ash Building (IT Server Room S/L) - Single Door to Ash IT Server Room |  | Ash Building (Main Entrance) - Main Entrance to Ash Building |  | Ash Building (HR Department) | Ash Building (Reception) |  |  |  |  | IAH ASH Fire Exit near Security Room | IAH ASH Office Fire Exit
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M |  | M | M | M | M | [5 empty] | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | [5 empty] | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N |  | N | N | N | N | [5 empty] | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P |  | P | P | P | P | [5 empty] | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | [5 empty] | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | [5 empty] | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | [5 empty] | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | [5 empty] | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü |  | ü | ü | ü | ü | [5 empty] | ü | ü
PSU No#

## DAC 27+DAC 28
SITE: The Pirbright Institute, Pirbright
LOCATION: | IAH A & B Portakabin Side Entrance | IAH A & B Portakabin Entrance | IAH Gym Entrance | A & B Portakabin Turnstile IN | A & B Portakabin Turnstile OUT | A & B Block Portakabin 8 | [10 empty] | A Block (Front Door) | A Block (Room 1) |  |  | Freezer Portakabin Main Entrance |  | Liquid Nitrogen Room | B Block Main Entrance | PK 6 | PK 7 | [6 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | [16 empty] | A Block Front Door - Left hand door of double door set | Door in Paul Barnett's Office |  |  |  |  | Liquid Nitrogen Room< Outside of A Block
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | T | T | M | [10 empty] | M | M |  |  | M |  | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü |  |  | ü |  | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N/A | N/A | N | [10 empty] | N | N |  |  | N |  | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | N/A | N/A | P | [10 empty] | P | P |  |  | P |  | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü |  |  | ü |  | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü |  |  | ü |  | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | N/A | N/A | ü | [10 empty] | ü | ü |  |  | ü |  | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | N/A | N/A |  |  | N/A |  | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | [10 empty] | ü | ü |  |  | ü |  | ü | ü | ü | ü
PSU No#

## DAC 30
SITE: The Pirbright Institute, Pirbright
LOCATION: | [16 empty] | Bathroom Left IN | BSU RA (Shower IN) | BSU CL3 Main Entrance | BSU RA (Shower OUT) | BSU Double Door Entrance | BSU Door to G18 Area OUT | BSU (Plantroom 1) | BSU (Plantroom 2) | BSU G25 IN | BSU G25 OUT | BSU Lobby IN | [5 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | [20 empty] | Door to G18 Area
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | [16 empty] | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | [16 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | [16 empty] | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | [16 empty] | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | [16 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | [16 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | [16 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | [16 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | [16 empty] | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 31+DAC 32
SITE: The Pirbright Institute, Pirbright
LOCATION: | Insectary/01 | [15 empty] | IS4L (First Floor Plantroom) IN | IS4L (First Floor Plantroom) OUT | IS4L (Technical Room 1033) IN | IS4L (Technical Room 1033) OUT | IS4L (Autoclave Outside) IN | IS4L (Autoclave Outside) OUT | IS4L (Technical Room 1037) IN | IS4L (Technical Room 1037) OUT | IS4L (6 Person Lab Room 1029) IN | IS4L (6 Person Lab Room 1029) OUT | IS4L (12 Person Lab1 Room 1030) IN | IS4L (12 Person Lab1 Room 1030) OUT | IS4L (Virus Lab Room 1023) IN | IS4L (Virus Lab Room 1023) OUT | IS4L (Electrical Room 1041) OUT | IS4L (Electrical Room 1041) OUT | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | Insectary (Front Door)
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | [15 empty] | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | [15 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | [15 empty] | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | [15 empty] | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | [15 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | [15 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | N/A | [15 empty] | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | [15 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü
PSU No#

## DAC 33+DAC 34
SITE: The Pirbright Institute, Pirbright
LOCATION: | IS4L (Virus Lab Room 1024) IN | IS4L (Virus Lab Room 1024) OUT | IS4L (12 Person Lab2 Room 1030) IN | IS4L (12 Person Lab2 Room 1030) OUT | IS4L Corridor Room 1028 To Freezer Room 1018 | IS4L Freezer Room 1018 to Corridor Room 1028 | IS4L (6 Person Lab Room 1031) IN | IS4L (6 Person Lab Room 1031) OUT | IS4L (Equipment Room 1026) IN | IS4L (Equipment Room 1026) OUT | IS4L (6 Person Lab Room 1032) IN | IS4L (6 Person Lab Room 1032) OUT | IS4L (Autoclave Inside Room 1022) IN | IS4L (Autoclave Inside Room 1022) OUT | IS4L New Entrance IN | IS4L New Entrance OUT | IS4L (Entrance) IN | IS4L (Entrance) OUT | IS4L (Entrance to PPE Change Lobby) | IS4L PPE Change To Entrance Lobby | IS4L (Corridor to PPE Change) | IS4L PPE Change to Corridor | IS4L (Equipment Room 1021) IN | IS4L (Equipment Room 1021) OUT | IS4L (Microscopes Dark Room 1019) IN | IS4L (Microscopes Dark Room 1019) OUT | IS4L (Corridor 1008 To Freezers Room 1018) | IS4L Freezers Room 1018 To Corridor 1008 | IS4L (6 Person Lab Room 1003) IN | IS4L (6 Person Lab Room 1003) OUT | IS4L (12 Persons Lab1 Room 1002) IN | IS4L (12 Persons Lab1 Room 1002) OUT | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | [9 empty] | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | [9 empty] | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | [9 empty] | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [9 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | [9 empty] | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 35
SITE: The Pirbright Institute, Pirbright
LOCATION: | CSU (Freezer Park Ext) | CSU (Freezer Park Int) | CSU (Freezer Park) | IS4L (12 Person Lab2 Room 1002) | IS4L (Bioimaging Room 1001) | IS4L (Live Cell Lobby Room 1009) | IS4L (Virus Lab Room 1011) | IS4L (Virus lab Room 1013) | IS4L (Virus Lab Room 1015) | IS4L (Virus Lab Room 1016) | [22 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | N | N | N | N | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | P | P | P | P | P | P | P
Check card reader releases door on valid transaction | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 38
SITE: The Pirbright Institute, Pirbright
LOCATION: | [16 empty] | ISO 10 (Gents WC ) | ISO 10 (First Floor West Plantroom) | ISO Gate Entrance | ISO Gate Exit |  |  |  |  | ISO 10 Mens Changing Room Door | [7 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | [16 empty] | Mens Changing Room Entrance Door - ISO 8
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | [16 empty] | M | L | M | M |  |  |  |  | M
Tighten all fixing and lubricate as required | [16 empty] | ü | ü | ü | ü |  |  |  |  | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | [16 empty] | N | N | N/A | N/A |  |  |  |  | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | [16 empty] | P | P | N/A | N/A |  |  |  |  | P
Check card reader releases door on valid transaction | [16 empty] | ü | ü | ü | ü |  |  |  |  | ü
Check void transactions | [16 empty] | ü | ü | ü | ü |  |  |  |  | ü
Check door open alarm operates correctly | [16 empty] | ü | ü | ü | ü |  |  |  |  | ü
Check to ensure any fire override interface operates correctly | [16 empty] | N/A | N/A | N/A | N/A |  |  |  |  | N/A
Check standby power units operate | [16 empty] | PSU/ 24 | F | F | F |  |  |  |  | F
PSU No#

## DAC 39+DAC 40
SITE: The Pirbright Institute, Pirbright
LOCATION: | ISO 10 (Ladies WC ) | ISO 10 (Ground Floor North Plantroom) | ISO 10 (First Floor North Plantroom) | ISO 10 (Second Floor North Plantroom) | [10 empty] | ISO 10 North |  | ISO 11 (First Floor East Plantroom) | ISO 11 (Second Floor East Plantroom) | ISO 11 (Autoclave Ext) | [8 empty] | ISO 11 (First Floor South West Plantroom) | ISO 11 (First Floor North West Plantroom) | ISO 11 (Bathroom Door) |  |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | L | L | L | [10 empty] | L |  | L | L | L | [8 empty] | L | L | L
Tighten all fixing and lubricate as required | ü | ü | ü | ü | [10 empty] | ü |  | ü | ü | ü | [8 empty] | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N/A | N/A | N/A | [10 empty] | N/A |  | N | N | N | [8 empty] | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | H | H | H | [10 empty] | H |  | H/P | H/P | H/P | [8 empty] | H/P | H/P | H/P
Check card reader releases door on valid transaction | ü | ü | ü | ü | [10 empty] | ü |  | ü | ü | ü | [8 empty] | ü | ü | ü
Check void transactions | ü | ü | ü | ü | [10 empty] | ü |  | ü | ü | ü | [8 empty] | ü | ü | ü
Check door open alarm operates correctly | ü | N/A | N/A | N/A | [10 empty] | N/A |  | ü | ü | ü | [8 empty] | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | N/A | [10 empty] | N/A |  | N/A | N/A | N/A | [8 empty] | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü | ü | [10 empty] | ü |  | ü | ü | ü | [8 empty] | ü | ü | ü
PSU No#

## DAC 41+DAC 42
SITE: The Pirbright Institute, Pirbright
LOCATION: | Incinerator (GTD 03) | Incinerator (GTD 06) | Incinerator (GTD 08) | iSTAR Reader4-ACM-IAH Incinertor | iSTAR Reader5-ACM-IAH Incinertor | iSTAR Reader6-ACM-IAH Incinertor | iSTAR Reader7-ACM-IAH Incinertor | Incinerator (Personal Entrance) | [8 empty] | Incinerator (First Floor West Plantroom) | ISO 8 (First Floor East Plantroom) | ISO 8 (Formalin Room Spare) | ISO 8 (Gents W.C) | ISO 8 (Ladies W.C) | ISO 8 (Second Floor East Plantroom) | ISO 9 (First Floor South Plantroom) | ISO 9 (First Floor West Plantroom) | ISO 9 (First Floor North Plantroom) | ISO 9 (Gents W.C) | ISO 9 (Ladies W.C) | ISO 9 (Second Floor North Plantroom) |  |  |  |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M | U/K | U/K | U/K | U/K | M | [8 empty] | M | M | M |  |  | M | M | M | M |  |  | M
Tighten all fixing and lubricate as required | ü | ü | ü | U/K | U/K | U/K | U/K | ü | [8 empty] | ü | ü | ü | U/C | U/C | ü | ü | ü | ü | U/C | U/C | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N | N | N | U/K | U/K | U/K | U/K | N | [8 empty] | N | N | N | U/C | U/C | N | N | N | N | U/C | U/C | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | P | P | P | U/K | U/K | U/K | U/K | P | [8 empty] | P | P | P | U/C | U/C | P | P | P | P | U/C | U/C | P
Check card reader releases door on valid transaction | N/A | ü | N/A | U/K | U/K | U/K | U/K | N/A | [8 empty] | ü | ü | ü | U/C | U/C | ü | ü | ü | ü | U/C | U/C | ü
Check void transactions | N/A | ü | N/A | U/K | U/K | U/K | U/K | N/A | [8 empty] | ü | ü | ü | U/C | U/C | ü | ü | ü | ü | U/C | U/C | ü
Check door open alarm operates correctly | ü | ü | ü | U/K | U/K | U/K | U/K | ü | [8 empty] | ü | N/A | N/A | U/C | U/C | N/A | N/A | N/A | ü | U/C | U/C | N/A
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A | U/K | U/K | U/K | U/K | N/A | [8 empty] | N/A | N/A | N/A | U/C | U/C | N/A | N/A | N/A | N/A | U/C | U/C | N/A
Check standby power units operate | ü | ü | ü | U/K | U/K | U/K | U/K | ü | [8 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 44
SITE: The Pirbright Institute, Pirbright
LOCATION: | [16 empty] | E&M Workshop | [15 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | [16 empty] | M
Tighten all fixing and lubricate as required | [16 empty] | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | [16 empty] | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | [16 empty] | P
Check card reader releases door on valid transaction | [16 empty] | ü
Check void transactions | [16 empty] | ü
Check door open alarm operates correctly | [16 empty] | ü
Check to ensure any fire override interface operates correctly | [16 empty] | N/A
Check standby power units operate
PSU No#

## DAC 45+DAC 46
SITE: The Pirbright Institute, Pirbright
LOCATION: |  | Modula Building 2 LHS Exit | Modular Building 2 RHS Exit | Modular Building 2 Main Entrance | [12 empty] | John Sisk Turnstile IN | John Sisk Turnstile OUT | [14 empty] | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock |  | M | M | M
Tighten all fixing and lubricate as required |  | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel |  | N | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle |  | P | P | P
Check card reader releases door on valid transaction |  | ü | ü | ü
Check void transactions |  | ü | ü | ü
Check door open alarm operates correctly |  | ü | ü | ü
Check to ensure any fire override interface operates correctly |  | N/A | N/A | N/A
Check standby power units operate |  | ü | ü | ü
PSU No#

## DAC 47+DAC 48
SITE: The Pirbright Institute, Pirbright
LOCATION: | DDT Freezer Park IN |  | DDT Freezer Park OUT |  | DDT Main Door | [11 empty] | CL2 GND External Autoclave IN | CL2 GND External Autoclave OUT | CL2 GND Virus Prep IN | CL2 GND Virus Prep OUT | CL2 GND Autoclave IN | CL2 GND Autoclave OUT | CL2 GND East Lobby IN | CL2 GND East Lobby OUT | CL2 GND Tick Cell Biobank | CL2 GND Serice Corridor IN | CL2 GND Serice Corridor OUT | CL2 GND Cryostore | CL2 GND Water Storage Plant | CL2 Gnd West IN | CL2 Gnd West OUT | CL2 GND Freezer Store | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS: | [24 empty] | Anthropods Genetic Group
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M |  | M |  | M | [11 empty] | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü |  | ü |  | ü | [11 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N/A |  | N |  | N | [11 empty] | N/A | N | N/A | N | N/A | N | N/A | N | N | N/A | N | N | N | N/A | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | N/A |  | N/A |  | P | [11 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | P | N/A | N/A | P | P | N/A | N/A | P
Check card reader releases door on valid transaction | ü |  | ü |  | ü | [11 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü |  | ü |  | ü | [11 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | F |  | F |  | ü | [11 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A |  | N/A |  | N/A | [11 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü |  | ü |  | ü | [11 empty] | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
PSU No#

## DAC 49+DAC 50
SITE: The Pirbright Institute, Pirbright
LOCATION: | CL2 GND Radioactive Room IN | CL2 GND Radioactive Room OUT | CL2 GND Comms Room |  | CL2 GND Entrance Lobby IN | CL2 GND Entrance Lobby OUT | CL2 GND Entrance Lobby Revlving Door IN | CL2 GND Entrance Lobby Revlving Door OUT | [8 empty] | CL2 Plant Room East Stairs IN | CL2 Plant Room East Stairs OUT | CL2 Lift to Plant | CL2 Plant to Lift |  |  |  |  | CL2 1st West Lobby IN | CL2 1st West Lobby OUT | CL2 1st Central Lobby IN | CL2 1st Central Lobby OUT | CL2 1st East Lobby IN | CL2 1st East Lobby OUT | CL2 1st Comms Room |  | LOCATION
DOORS | READERS | [15 empty] | READERS
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
DESCRIPTIONS:
Check operation of locking equipment R=Release L=Lock M=Magna Lock T=Turnstiles/Barrier S=Shotbolt/Shearlock | M | M | M |  | M | M | M | M | [8 empty] | M | M | M | M |  |  |  |  | M | M | M | M | M | M | M
Tighten all fixing and lubricate as required | ü | ü | ü |  | ü | ü | ü | ü | [8 empty] | ü | ü | ü | ü |  |  |  |  | ü | ü | ü | ü | ü | ü | ü
Check emergency break glass unit releases door. Activates Alarm's N=Not Monitored S=Sounder P=Panel | N/A | N | N |  | N/A | N | N/A | N | [8 empty] | N/A | N | N | N |  |  |  |  | N/A | N | N/A | N | N/A | N | N
Check exit push button releases door. P=Push Button T=T-Rex H=Handle | N/A | N/A | P |  | N/A | N/A | N/A | N/A | [8 empty] | N/A | N/A | N/A | N/A |  |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | P
Check card reader releases door on valid transaction | ü | ü | ü |  | ü | ü | ü | ü | [8 empty] | ü | ü | ü | ü |  |  |  |  | ü | ü | ü | ü | ü | ü | ü
Check void transactions | ü | ü | ü |  | ü | ü | ü | ü | [8 empty] | ü | ü | ü | ü |  |  |  |  | ü | ü | ü | ü | ü | ü | ü
Check door open alarm operates correctly | ü | F | ü |  | ü | ü | ü | ü | [8 empty] | ü | ü | ü | ü |  |  |  |  | ü | ü | ü | ü | ü | ü | ü
Check to ensure any fire override interface operates correctly | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | [8 empty] | N/A | N/A | N/A | N/A |  |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Check standby power units operate | ü | ü | ü |  | ü | ü | ü | ü | [8 empty] | ü | ü | ü | ü |  |  |  |  | ü | ü | ü | ü | ü | ü | ü
PSU No#