## Sheet1
CLARIFICATION LOG
Tender: | Solar Energy System and Battery Storage
Tender Reference: | NZ739
Published Date: | 2024-03-22
Version number: | 0.6
Number | Clarification | Response | Reply date
1 | Are we limited to using a hybrid inverter? It would be far more practical and cost efficient to use one or two larger "main" inverters connected to AC battery chargers. | No - not limited. If you believe that you have a better solution - please detail this and explain why and clearly indicate the cost. | 2024-03-26
2 | Are we able to cover skylights? | No | 2024-03-26
3 | Is it the building circled? | Yes | 2024-03-26
4 | Would you be open to higher power panels? 560/580W panels? | The specification states MINIMUM requirement - so yes. | 2024-03-26
5 | Please confirm where the plant room/point of connection is located. | Within 20ft of the incoming power supply. Separate shed will be built for the batteries. | 2024-03-28
6 | I’m assuming the shed is going to be build by a third party for the BESS storage? | Yes | 2024-04-02
7 | Also, can you please highlight where this is due to go as the cabling and trenching can be costly and we are conscious of the fixed budget on this one. | 15m from where the power comes into the building. | 2024-04-02
8 | Do we only need to install the panels on the roof which is lined in red? Because if we install the panels on north-east facing roof, generation will be less. But south-west facing roof is OK. | Yes. 170-180kw output is required. | 2024-04-02
9 | Do you have power outs? | Yes. Please ensure your system accounts for this. | 2024-04-02
10 | Has the DNO application been completed and approved by National Grid to install the 170-180kw of PV with 75kw battery storage? | No | 2024-04-04
11 | Is your location within an AONB or have any planning restrictions? | No | 2024-04-04
12 | Has a structural survey of the building been conducted for the planned installation site? | No | 2024-04-04
13 | This project is subjected to a grant funding approval, do you have the expected timeline of when you will be considered for approval and when you are looking for the installation to be completed? | We hope that the decision will be made by the end of June. Installation must be completed and invoiced by the end of December 2024. | 2024-04-04
14 | Our specialist energy solutions provider has reviewed the scope and does not believe the minimum requirements are achievable. | Please detail what you believe to be achievable levels on the building specified. | 2024-04-04
15 | Can you comment on designs. | No as this is an open and competitive process. | 2024-04-04
16 | We also need to know fuse box capacity and tech. specs. to configure the project with a full backup system. | 600amps fuse box capacity | 2024-04-04
17 | Do we need to write technical explanation on compliancy matrix for the PV system or products | The matrix needs to be completed to ensure compliancy with the specification. If you choose to write a technical explanation to accompany, then that is fine. | 2024-04-04
18 | Had a DNO application been made or is this part of the project? | No | 2024-04-05
19 | Any particular reason for having string and hybrid inverters why not connect the whole system to the hybrid inverters and the battery system? | If you believe that you have a better solution - please detail this, explain why and clearly indicate the cost. As long as the inverter will deal with 120Kw then this will be acceptable. | 2024-04-05
20 | Has an electrical survey been done? | No | 2024-04-05
Clarifications will be published against the Contract Notice on Contracts Finder.
If interested in tendering for this project please ensure you add a "watch this notice" for alerts as from time to time additional information or clarifications may be published related to this tender.
It will be the responsibility of Bidders to ensure they are aware of all published clarifications and ensure that their bid has taken these into account.
In the event of any queries please contact: jackie@jackiegeorge.co.uk