## Front Sheet
Electric Heater Battery Schedule
Client | THE PIRBRIGHT INSTITUTE |  | Document Ref | 30686-BS-SC-0002
Site | PIRBRIGHT |  | Status | DESIGN & REVIEW
Project Name | TPI BACS CONTROL ROOM - MOD 2 |  | Revision | B2
Project Number | 30687 |  | Date | 2023-01-03
This document contains proprietary information belonging to Scitech and shall be used only for the purpose for which it was supplied. It shall not be copied, reproduced or otherwise used, nor shall such information be furnished in whole or in part to others, except in accordance with the terms of any agreement under which it was supplied or with the prior written consent of Scitech and shall be returned upon request.
Issue | Date | Description | By | Checked | Approved
B1 | 2023-01-01 | FIRST ISSUE- FOR REVIEW | RW
B2 | 2023-04-03 | TENDER ISSUE | RW | BB
All revisions are in red
Document Sign Off
Role | Name |  | Signature |  | Date
Author
Checker
Approver

## Heater Battery
30687-BS-SC-0002 Electric Heater Battery Schedule
TAG No |  | Location | Room No. | System and/or service | Application | Air Flow | Max Face Velocity | APD | Temperatures |  | Total Min Capacity | Electrical Details | [5 empty] | NOM Size |  |  |  | Air Flow Direction | Model ref | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO
[9 empty] | EAT | LAT |  | Phase | Voltage | Frequency | Power | IP | Diameter | Height | Length | Area | Casing Depth
[6 empty] | m³/h | m/s | Pa | °C | °C | kW |  | V | Hz | kW |  | mm | mm | mm | m² | mm
FC | 01 | MOD2 | INTAKE ROOM | HRVU | INLET AIR FROST COIL | 150 | 1.6276 |  | -10 | 5 | 0.81 | 1 | 230 | 50 |  | IP55 | n/a | 160 | 160 | 0.0256 | tba | vertically down | VFL-MTEML160X160-0.8kW-1x230V-A-IP55-NI
NOTES
1. All Electric heaters shall be as manufactured by VEAB.
2. Indicate air flow direction - horizontal, vertical down or vertical up. The Contractor shall confirm.
3. Casing manufactured from Aluzinc-coated sheet steel with stainless steel heating elements to EN14301. Flanged connections. Has potential-free alarm contacts that indicate tripping of the overheating protection with auto reset. Has a built-in electronic air flow monitor
4. Degree of protection: Refer to schedule
5. Grey cells to be confirmed by the manufacturer.
6. Complete with duct mounted temperature sensor with temperature setpoint adjuster.