## Front Sheet
30687-BS-SC-0005 Cassette & Heat Pump Schedule
Client | THE PIRBRIGHT INSTITUTE |  | Document Ref | 30687-BS-SC-0005
Site | PIRBRIGHT |  | Document Title | DETAILED DESIGN
Project Name | TPI BACS CONTROL ROOM - MOD 2 |  | Revision | B2
Project Number | 30687 |  | Date | 2023-03-03
This document contains proprietary information belonging to Scitech and shall be used only for the purpose for which it was supplied. It shall not be copied, reproduced or otherwise used, nor shall such information be furnished in whole or in part to others, except in accordance with the terms of any agreement under which it was supplied or with the prior written consent of Scitech and shall be returned upon request.
Issue | Date | Description | By | Checked | Approved
B1 | 2023-03-03 | FIRST ISSUE | RW | BB
B2 | 2023-04-03 | TENDER ISSUE | RW | BB
All revisions are in red
Document Sign Off
Role | Name |  | Signature |  | Date
Author
Checker
Approver

## TAGS
Tagging Requirements - Applies to all equipment schedules
Notes
Type 'A' to be used for valves and other pipe line equipment
Line 1 to be service type e.g. chw (chilled water)
Line 2 to be sequential number
Types 'B, C, D' to be used for equipment
Line 1 to be equipment type e.g. Ahu (air handling unit)
Line 2 to be sequential number
Tagging type is shown on each schedule of equipment

## Cassette
30687-BS-SC-0005 Cassette Inverter Heat Pumps Schedule
TAG No. | Location | No. Of | Room No. | System and/or service | Application | Model | Unit Ref | Refrigerant (Charge kg) | Cooling Duty Each (Kw) |  | Heating Duty Each (Kw) | Power Requirements kW | Electrical Supply (V/P/Hz) | Spigots | Comments | Rev
[9 empty] | Sensible | Total
OU01 | External Heat Pump | 1 | MOD2 | VRF | heating & cooling | City Multi | PUHY-M250YNW-A1 | R32 (6.5kg) |  | 28 | 31.5 | 9 | 380V 3ph 50Hz | n/a | Configured as duty/standby
OU02 | External Heat Pump | 1 | MOD2 | VRF | heating & cooling | City Multi | PUHY-M250YNW-A1 | R32 (6.5kg) |  | 28 | 31.5 | 9 | 380V 3ph 50Hz | n/a | Configured as duty/standby
HBC01 | Intake Room | 1 | MOD2 | VRF | controller | City Multi | CMB-M106V-J1 | R32 |  | n/a | n/a | 0.11 | 220V 1ph 50Hz | n/a
WU01 | Control Room | 1 | MOD2 | VRF | heating & cooling | City Multi | PKFY-P63LVM-E | R32 |  | 7.1 | 8 | 0.05 | 220V 1ph 50Hz | n/a | Wall mounted
WU02A | Intake Room | 1 | MOD2 | VRF | heating & cooling | City Multi | PKFY-PI0LVM-E | R32 |  | 1.2 | 1.4 | 0.02 | 220V 1ph 50Hz | n/a | Wall mounted - Configured as duty/standby
WU02B | Intake Room | 1 | MOD2 | VRF | heating & cooling | City Multi | PKFY-PI0LVM-E | R32 |  | 1.2 | 1.4 | 0.02 | 220V 1ph 50Hz | n/a | Wall mounted - Configured as duty/standby
WU03 | Control Room | 1 | MOD2 | VRF | heating & cooling | City Multi | PKFY-P63LVM-E | R32 |  | 7.1 | 8 | 0.05 | 220V 1ph 50Hz | n/a | Wall mounted
WU04 | Control Room | 1 | MOD2 | VRF | heating & cooling | City Multi | PKFY-P63LVM-E | R32 |  | 7.1 | 8 | 0.05 | 220V 1ph 50Hz | n/a | Wall mounted
CP01 | Control Room | 1 | MOD2 | VRF | controller | City Multi | AT-50B | n/a |  | n/a | n/a |  | From CC01 | n/a
CC01 | Intake Room | 1 | MOD2 | VRF | cenralised controller | City Multi | PAC-SC51KUA | n/a |  | n/a | n/a |  | 220V 1ph 50Hz
Notes
1 Design based on Mitsubishi City Multi
2 To be supplied and installed as a complete package with all VRF pipework, condensate pipework, pipework supports, insulation, controls and interconnecting wiring, installation and commissioning
3 To be supplied by others: Incoming power supply, builders work holes and concrete base