Architectural Specification

Client Name: The Pirbright Institute

Client Project Name: TPI BACS Control Room Design Services

Project Location: PIRBRIGHT

Scitech Project Number: 30687

| This document contains proprietary information belonging to Scitech Engineering Limited and shall be used only for the purpose for which it was supplied. It shall not be copied, reproduced or otherwise used, nor shall such information be furnished in whole or in part to others, except in accordance with the terms of any agreement under which it was supplied or with the prior written consent of Scitech Engineering Limited and shall be returned upon request. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| B1 | 30-03-23 | Detailed Design | MJS | JH | JPJ |
| A1 | 25-03-23 | RIBA Stage 4 | MJS | JH |  |
| ISSUE | DATE | DESCRIPTION | BY | CHECKED | APPROVED |

- Table of Contents

1.0	SCHEDULE OF DOCUMENTS TO BE READ WITH THIS SPECIFICATION	6

1.1	Overview	6

1.2	Existing MOD2 building	6

1.3	Existing Plowright control room	6

1.4	Drawings	6

2.0	GENERAL REQUIREMENTS	7

2.1	Site surveys	7

2.2	Shop drawings and documents	7

2.3	Co-ordination	7

2.4	Specified items	8

3.0	QUALITY CONTROL	8

3.1	Codes & standards	8

3.2	Quality checks	8

3.3	Shop drawings	8

3.4	As-built documentation	8

3.5	Maintenance / operation manual	8

3.6	Construction Design  Management regulations 2015	8

3.7	Health & Safety file / Building maintenance manual information	9

3.8	Method statements	9

4.0	DEMOLITION AND CONDITION SURVEY	9

4.1	Demolition	9

4.2	Dilapidations and conditions survey	9

4.3	Execution	10

4.3.1	Demolition generally	10

4.3.2	Asbestos Removal	10

4.3.3	Unforeseen hazards during survey	10

5.0	MOD 2 SPECIFICATION	10

5.1	Walls	10

5.1.1	External Walls	10

5.1.2	Internal Walls	10

5.1.3	Installing framed partitions generally	11

5.1.4	Installing plasterboard to metal framing	11

5.1.5	Sealing gaps and air paths around partitions	11

5.1.6	Installing gypsum based board	11

5.1.7	Installing additional supports	11

5.1.8	Joints between gypsum based boards	12

5.1.9	Repairs to plasterboard	12

5.2	Floor	12

5.2.1	Control Room Floor	12

5.2.2	Intake Room Floor	13

5.2.3	Execution	13

5.2.4	Installation control samples	13

5.2.5	Condition of building and notification of commencement	14

5.2.6	Conditioning of flooring prior to laying	14

5.2.7	Environmental conditions before, during and after laying	14

5.2.8	Assessing suitability of bases	14

5.2.9	Remove existing floorings	15

5.2.10	Level of Existing Bases	15

5.2.11	Layout – setting out seams	15

5.2.12	Colour consistency	15

5.2.13	Welded or sealed seams	15

5.2.14	Joints at doorways	15

5.2.15	Fixing edgings and cover strips	15

5.3	Ceiling	15

5.3.1	Execution	16

5.3.2	Handling and storage of coating materials	16

5.3.3	Wet paint signs	16

5.3.4	Control samples of coating systems	16

5.3.5	Preparation for coating systems generally	16

5.3.6	Applying coating generally	17

5.4	External door	17

5.4.1	Pre-Construction Survey	18

5.4.2	Installing external doorsets or frames	18

5.4.3	Fixing of loose thresholds	18

5.4.4	Installation of emergency and panic exit device	18

5.4.5	Preparation	18

5.5	Windows	18

5.5.1	Pre-Construction Survey	19

5.5.2	Workmanship generally	19

5.5.3	Preparation	19

5.5.4	Window installation generally	19

5.6	Glazing Mirror Film	19

5.7	External services compound fencing and gate	19

6.0	PLOWRIGHT SPECIFICATION	20

6.1.1	New Stud Walls	20

6.1.2	Execution	21

6.1.3	Installing framed partitions generally	21

6.1.4	Installing framing for partitions	21

6.1.5	Installing plasterboard to metal framing	22

6.1.6	Sealing gaps and air paths around partitions	22

6.1.7	Installing insulation and cavity barriers in framed partitions	22

6.1.8	Installing gypsum based board	22

6.1.9	Installing additional supports	23

6.1.10	Level of dry lining across joints	23

6.1.11	Joints between gypsum based boards	23

6.1.12	Seamless jointing to gypsum boards	23

6.1.13	Repairs to plasterboard	23

6.1.14	Installing steel frames for linings	24

6.1.15	Installing beads	24

6.2	New glazed walls	24

6.3	Existing glazed curtain wall	25

6.4	Decoration / finishing	25

6.4.1	Steelwork Glazing Frame	25

6.4.2	New Walls	25

6.4.3	Existing Walls	25

6.4.4	Execution	26

6.4.5	Handling and storage of coating materials	26

6.4.6	Wet paint signs	26

6.4.7	Control samples of coating systems	26

6.4.8	Preparation for coating systems generally	26

6.4.9	Applying coating generally	27

6.5	Floor	27

6.5.1	Execution	27

6.5.2	Installation control samples	27

6.5.3	Condition of building and notification of commencement	28

6.5.4	Conditioning of flooring prior to laying	28

6.5.5	Environmental conditions before, during and after laying	28

6.5.6	Assessing suitability of bases	28

6.5.7	Remove existing floorings	29

6.5.8	Level of Existing Bases	29

6.5.9	Layout – setting out seams	29

6.5.10	Colour consistency	29

6.5.11	Welded or sealed seams	29

6.5.12	Joints at doorways	29

6.5.13	Fixing edgings and cover strips	29

6.6	Ceiling	29

6.6.1	Execution	30

6.6.2	Demountable suspended ceiling preliminary installation	30

6.6.3	Demountable suspended ceiling control samples	30

6.6.4	Installing demountable suspended ceilings generally	31

6.6.5	Protective coverings	31

6.6.6	Setting out demountable suspended ceilings	31

6.6.7	Infill and access units, integrated services	31

6.6.8	Edge or perimeter infill unit size (minimum)	31

6.6.9	Corner infill unit size (minimum)	31

6.6.10	Infill joints and exposed suspension members	31

6.6.11	Protection of demountable suspended ceilings	31

6.6.12	Installing cavity fire barriers above demountable suspended ceilings	31

6.6.13	Ceiling systems not intended for fire protection	32

6.6.14	Installing air plenum barriers above demountable suspended ceilings	32

6.6.15	Installing upstands and bulkheads to demountable suspended ceilings	32

6.6.16	Installing integrated services in demountable suspended ceilings	32

6.6.17	Services outlets: 	32

6.7	Motorised roller blinds	32

6.8	Glazing Mirror Film	33

# SCHEDULE OF DOCUMENTS TO BE READ WITH THIS SPECIFICATION

This Specification is to be read in conjunction with documents listed below, together with other documents mentioned within the text of this specification and other Tender Documentation:

## Overview

This document sets out the specification for the Architectural Works for the TPI BACS Control room project

## Existing MOD2 building

This is a 147m2 G.I.A. single storey modular building. The building currently serves as an office building with WC’s and a tea kitchen. The building is a Foremans Relocatable Building Systems modular building. Portakabin have advised that this is their building product reclad by Foremans and have advised the following construction:

Walls

Cladex insulated panel

Adhesive

Plastisol coated steel

Foam insulation

Plasterboard

Roof

Steel – foam – steel construction

Profile roof sheet

92mm thick o/all

Floor

Welded steel floor construction, joists and beams in galvanised steel which is 305mm deep

18mm chip board

O/all height 323mm

Portakabin have further advised the use of Bugle Phillips 3.5x35 Drywall Screws for fixing the plywood and plasterboard to the external walls.

## Existing Plowright control room

The existing control room is a small office on the ground floor, West wing of the Plowright building. The office area is 23m2 G.I.A. The Plowright building is a 2/3 storey building containing offices, meeting rooms and laboratories with plant located above.

## Drawings

This document is to be read in conjunction with the following documents:

| Item reference | Description |
| --- | --- |
| 30687-AR-DR-1002-A2 | Site Location Plan – MOD 2 and PLOWRIGHT |
| 30687-AR-DR-1101-A3 | Client Definition - Ground Floor MOD 2 |
| 30687-AR-DR-1102-A3 | Client Definition - Ground Floor PLOWRIGHT |
| 30687-AR-DR-1201-A2 | Fire Strategy - Ground Floor MOD 2 |
| 30687-AR-DR-1202-A2 | Fire Strategy - Ground Floor PLOWRIGHT |
| 30687-AR-DR-1301-A2 | Reflected Ceiling Plan - Ground Floor MOD 2 |
| 30687-AR-DR-1302-A2 | Reflected Ceiling Plan - Ground Floor PLOWRIGHT |
| 30687-AR-DR-1401-A2 | Setting Out - Ground Floor MOD 2 |
| 30687-AR-DR-1402-A2 | Setting Out - Ground Floor PLOWRIGHT |
| 30687-AR-DR-1501-A2 | Disinvestment - Ground Floor MOD 2 |
| 30687-AR-DR-1502-A2 | Disinvestment - Ground Floor PLOWRIGHT |
| 30687-AR-DR-3001-A2 | Room Elevations MOD 2 - Sheet 1 0f 2 |
| 30687-AR-DR-3002-A2 | Room Elevations MOD 2 - Sheet 2 0f 2 |
| 30687-AR-DR-3006-A2 | Room Elevations PLOWRIGHT - Sheet 1 0f 2 |
| 30687-AR-DR-3007-A2 | Room Elevations PLOWRIGHT - Sheet 2 0f 2 |
| 30687-AR-DR-3011-A2 | Proposed Building Elevations - MOD 2 |
| 30687-AR-DR-4001-A1 | Glazed Office Partition - PLOWRIGHT |

# GENERAL REQUIREMENTS

## Site surveys

The contractor shall include for visiting the site before submitting tender return documents, and for the thorough review of all affected areas prior to commencing work and to verify the extent and accuracy of existing information shown on the drawings.

## Shop drawings and documents

The contractor shall allow for all deliverables required as part of this specification including manufacturer’s product information, fabrication drawings, method statement, maintenance and operation manual, as-built documents, guarantees and warranties.

## Co-ordination

The contractor shall allow for full co-ordination with other services and trades throughout the period of the contract. Work will need to be sequenced with other trades on site.

## Specified items

Any variance to products, systems and items specified must be equal and approved/agreed with the Architect/CA prior to ordering/commencing.

# QUALITY CONTROL

The high standards for materials and installation works described within the requirements of this specification are an express requirement of this subcontract. The contractor will actively pursue quality materials, products, workmanship and installation to the standards specified, and this will feature strongly in the requirements of the subcontractor’s quality checks and the contractor’s final test, inspection and snagging procedure.

The subcontractor shall therefore operate a quality control process, which will interface directly with the requirements of this specification.

## Codes & standards

Comply with all current codes and standards as applicable to the work; and as specifically required by the NBS specification clauses.

## Quality checks

The subcontractor shall work to a “Quality Schedule” which will list the main points of the specification and allow them to be checked on site and signed off as having been correctly provided. This is to be reviewed and agreed prior to start on site.

Refer to APPENDIX C.

## Shop drawings

All drawings are to be produced in Revit preferably, but otherwise in AutoCAD (current version). The proposed list of shop drawings to be produced by the subcontractor is to be included with the tender.

## As-built documentation

The subcontractor shall supply all appropriate certificates, instruction manuals and shop drawings indicating ‘As-Built’ conditions within a maximum 30 days of final acceptance of the work or prior to building handover (whichever is the sooner).

## Maintenance / operation manual

Provide copies of manufacturer’s complete parts list, recommended parts inventory and complete maintenance instructions for all laboratory furniture.

Provide manufacturer’s operation including emergency instructions for all equipment supplied under this Contract.

## Construction Design  Management regulations 2015

The Subcontractor shall comply fully with the requirements of the CDM Regulations 2015.

Refer to CONSTRUCTION HEALTH & SAFETY PLAN.

Without in any way detracting from the above paragraph, attention is drawn to the following:

Regulation 13 - Designers Duties

Subcontractors undertaking work that includes elements of Design Responsibility (as defined in part 1 of this specification) shall comply fully with Regulation 13 - Requirements on Designer.

This shall include the completion of Designers Risk Assessments and these shall be submitted to the contractor prior to finalisation of the design elements. Where subcontractors are required to submit shop drawings these shall be accompanied by their completed Risk Assessments.

Refer to CONSTRUCTION PHASE PLAN (CDM 2015).

## Health & Safety file / Building maintenance manual information

The subcontractor shall provide information sufficient to satisfy the requirements of Construction (Design and Management) Regulations 2015 (and as listed elsewhere in this specification) to assist persons carrying out construction, maintenance or demolition work on the structure at any time after completion.

## Method statements

The subcontractor is to prepare method statements for carrying out the works, which shall include all specified testing. These method statements are to be agreed and approved by the contractor prior to commencement of the related work.

Refer to CONSTRUCTION PHASE PLAN (CDM 2015)

# DEMOLITION AND CONDITION SURVEY

## Demolition

- Scope: As required to complete project works and as indicted on project drawings

- Pre-Commencement Survey Requirements:

  - Scope of contractor survey: Internal and external areas affected by works

  - Type of survey: As noted below

- Pre-Existing Surveys:

TPI have provided no existing survey information for the MOD 2 or Plowright Buildings.

The contractor should allow to provide surveys as they require to fulfil their CDM regulatory duties.

## Dilapidations and conditions survey

- Scope:

- Prior to commencement a Pre-Construction Dilapidations and Condition Survey shall be conducted by a Professional Building Surveyor to assess and record the condition of the existing building 4 fabric and structure (and any related adjacent areas and buildings).

- The survey should cover external areas relating to the external works and services installations including the existing Building 4 roof.

- Pre-Commencement Survey Requirements:

- Report to provide written documentation and photographic record on the pre-construction condition of the areas affected by the proposed works

- The Dilapidations and Condition Survey is to identify and record the pre-existing condition of the structure and finishes including but not limited to cracks, distortion, leakages, settlement, and other building defects.

## Execution

### Demolition generally

- Standard: To BS 6187:2011 Code of practice for full and partial demolition

- Risk Assessment and Method Statements: Contractor to provide detailed Risk Assessments and Method Statements (RAMS) for demolition works for review by CA prior to commencing work to ensure works are to be carried out in a safe manner. The RAMS should identify the sequence and assessment of risks of uncontrolled collapse or structural damage during the demolition.

### Asbestos Removal

- Discovered asbestos:

  - Requirement: Give notice immediately. Do not disturb.

- Managing personnel or organization: A fully licensed asbestos removal Contactor compliant with all current asbestos removal legislation and requirements. ARCA registered.

### Unforeseen hazards during survey

- Requirement: Give notice when unrecorded hazards or hazardous materials are found. Do not disturb.

# MOD 2 SPECIFICATION

## Walls

### External Walls

- Drawing Reference:

Setting Out drawings 30687-AR-DR-1401

- 1 no. layer 12mm WBP plywood

- 12mm square edge vinyl coated duplex plasterboard over

- White UPVC Joint cover strips to match existing

- New UPVC skirtings and architraves to match existing

- UPVC coving trim to match existing

- Portakabin have further advised the use of Bugle Phillips 3.5x35 Drywall Screws for fixing the plywood and plasterboard to the external walls

### Internal Walls

- Drawing Reference:

Setting Out drawings 30687-AR-DR-1401

- 1 no. layer 12mm plywood

- 1 no. layer 12mm square edge vinyl coated plasterboard

- Full fill Rockwool sound deadening quilt

- White UPVC Joint cover strips to match existing

- New UPVC skirtings and architraves to match existing

- UPVC coving trim to match existing

### Installing framed partitions generally

- Standard: To BS 8000-0 and BS 8212.

- Deviations and tolerances:

  - Vertical deviation (maximum): ± 5 mm measured above or below the setting out position, in accordance with BS 8212 clause 3.3.2.

  - Horizontal deviation (maximum): ± 3 mm measured at the setting out level (ceiling or floor), in accordance with BS 8212 clause 3.3.2.

  - Finished surfaces: Maximum deviation band of 10 mm in accordance with BS 8212 clause 3.3.3.

### Installing plasterboard to metal framing

- Fixings: British Gypsum Drywall screws as recommend by supplier, screws to be corrosion resistant

- Wall linings: Fix securely.

- Fixing centres (maximum):

  - Single layer boarding: 300 mm centres generally and 200 mm centres at external angles.

  - Multi-layer boarding: Inner layers at 300 mm centres round perimeters; face layer at 300 mm centres.

- Fixing positions: Position screws 10 mm minimum from edges of boards.

- Screw heads: Set in a depression. Do not break paper or gypsum core.

### Sealing gaps and air paths around partitions

- Location of sealant: To perimeter abutments and around openings. At board-to-board and board-to-metal frame junctions in pressurized shafts and ducts.

- Application: To clean, dry and dust free surfaces as a continuous bead with no gaps. After sealing, fill gaps greater than 6 mm between floor and underside of plasterboard with jointing compound.

### Installing gypsum based board

- General: Use fixing, jointing, sealing and finishing installation methods recommended by board manufacturer.

- Cutting plasterboard: Neat and accurate. Do not damage core or tear paper facing.

- Cut edges: Minimize. Position at internal angles wherever possible. Mask with bound edges of adjacent boards at external corners.

- Fixing boards: Securely, to suitably prepared and accurately levelled backgrounds.

- Finishing: Neat. Provide flush, smooth, flat surfaces free from bowing and abrupt changes of level.

### Installing additional supports

- Support to board edges and perimeters: At board edges and lining perimeters, as recommended by board manufacturer to suit type and performance of lining

- Fixtures and fittings: For all fixtures, fittings and service outlets, mark framing positions clearly and accurately on linings. Accurately position all additional framing and fix securely.

### Joints between gypsum based boards

- Surfaces exposed to view: Horizontal joints not permitted. Seek instructions if partition height exceeds maximum available board dimension.

- Multi-layer boarding: Stagger joints between layers by at least 600 mm.

- Board edges: Support with additional framing. In multi-layer boarding, support edges of outer layer.

- Joints: Centre on studs. Stagger joints on opposite sides of studs. In multi-layer boarding, stagger joints between layers.

- Edge profile:

  - Square: Gap to match existing with UPVC joint cover strip provided

### Repairs to plasterboard

- Filling small areas with broken cores:

  - Generally: Cut away paper facing, remove loose core material and fill with jointing compound.

  - Finish: Flush, smooth surface suitable for redecoration.

- Large patch repairs:

  - Generally: Cut out damaged area and form neat hole with rectangular sides. Replace with matching plasterboard.

  - Fixing: Use methods to suit type of dry lining, ensuring full support to all edges of existing and new plasterboard.

  - Finishing: Fill joints, tape and apply jointing compound to give a flush, smooth surface suitable for redecoration.

## Floor

### Control Room Floor

- Drawing Reference: Client definition drawing 30687-AR-DR-1101

- Type: Forbo Struktur 2 Linear 50x50cm carpet tiles fitted in accordance with manufacturers recommendations.

- Colour: To be selected by client from the following range

- Format: To be selected by client

### Intake Room Floor

- Drawing Reference: Client definition drawing 30687-AR-DR-1101

- Type: Forbo Surestep Original R10 fully welded vinyl

- Colour: To be selected by client from the following range

### Execution

### Installation control samples

- Required samples:

  - Types: Forbo Struktur 2 Linear and Forbo Surestep Original

  - Purpose: For use as an installation reference sample.

  - Timing: Lay during preliminary installation. Obtain approval of appearance before proceeding.

### Condition of building and notification of commencement

- Condition of works before laying materials:

  - Building envelope: Weathertight and well dried out.

  - Wet trades: Finished.

  - Paintwork: Finished and dry.

  - Conflicting overhead work: Complete.

  - Floor service outlets, duct covers and associated fixtures: Fixed, where materials are to be cut.

- Notification prior to laying floor coverings (minimum): 48 hours.

### Conditioning of flooring prior to laying

- Standards: To BS 8203 and BS 5325.

- General:

  - Before laying: Condition materials by unpacking and separating in spaces where they are to be laid.

  - Resilient flooring rolls: Maintain in an upright position.

  - Carpet: Unroll and keep flat on a supporting surface.

- Conditioning time and temperature (minimum):

  - Generally: As recommended by manufacturer.

  - Materials stored or transported at a temperature below 10°C immediately before laying: Extend time by a factor of two.

### Environmental conditions before, during and after laying

- Temperature and humidity: Maintain approximately at levels which will prevail after building is occupied.

- Ventilation: Adequate.

- Underfloor heating before laying: Turn off at least 48 hours before start of laying.

### Assessing suitability of bases

- Existing bases:

  - Notification: Before commencing work, confirm that existing bases will, be suitable to receive coverings.

  - Suitability of bases and conditions within any area: Do not lay coverings on unsuitable bases and in unsuitable conditions.

- New wet-laid bases:

  - Base drying aids: Do not use for at least four days before moisture content testing.

  - Base moisture content: Test in accordance with BS 5325, Annexe A or BS 8203, Annexe A.

  - Locations for readings: In all corners, along edges, and at regular centres over general areas being tested.

  - Laying coverings: Do not start until all readings show 75% relative humidity or less or as recommended by manufacturer.

### Remove existing floorings

- Base: Clear of covering and as much adhesive as possible. Skim with smoothing underlayment compound to give a smooth, even surface.

### Level of Existing Bases

- Existing sub bases to be levelled with self-levelling smoothing compound prior to laying new flooring

- Tolerances: Allow for grinding down/grouting high and low spots in existing concrete or other sub bases to ensure flatness tolerance of SR1+/-3mm maximum deviation from a 2m straight edge in contact with the floor (BS8204:part 2) is achieved for the flooring installations

- Levelling Compound:

Manufacturer: ARDEX UK Ltd

Product reference: ARDEX K 15 Rapid Drying Self-Levelling Sub-Floor Smoothing Compound

Primer: P51 primer

Other requirements: For thicknesses, greater than 7mm up to 35mm thick use ARDEX K 15-B (Base coat) and apply a 3mm smoothing layer of ARDEX K 15.

### Layout – setting out seams

- Setting out of seams: Seams to be hidden where possible and to line through parallel to walls.

### Colour consistency

- Appearance in any one area or room: Free from banding or patchiness.

### Welded or sealed seams

- Materials: Hot welding rods.

- Commencement (minimum): 24 hours after laying, or after adhesive has set.

- Joints: Neat, smooth. Strongly bond. Flush with finished surface.

### Joints at doorways

- Joint location: On centre line of door leaf.

### Fixing edgings and cover strips

- Fixing: Secure with edge of covering gripped. Use matching fasteners where exposed to view.

## Ceiling

- Drawing Reference: Client definition drawing 30687-AR-DR-1101

- System manufacturer: AkzoNobel

- Product: Dulux Trade Satinwood

- Preparation: The amount of preparatory work required on a Previously Coated Surface can vary considerably due to a variety of circumstances. This System is for Preparation up to and including partial failure/breakdown. Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and *dust off. All manually prepared surfaces should be prepared to a minimum standard of St3. BS EN ISO 8501-1: 2007 at the time of coating. Note *When rubbing down dry and/or dusting off wear a suitable face mask to avoid the inhalation of dust. (See AkzoNobel Site Work Instruction vExt1. for further information.)

- Finishing coats: 2 coats of Dulux Trade Satinwood each applied to give a minimum wet film thickness of 50 microns per coat, giving a minimum dry film thickness of 25 microns per coat

- Products supplied for the carrying out of this specification are compliant with Statutory Instrument 2005 No. 2773 (Environmental Protection) - The Volatile Organic Compounds in Paints, Varnishes and Vehicle Refinishing Products Regulations 2005

### Execution

### Handling and storage of coating materials

- Coating materials: Deliver in sealed containers, labelled clearly with brand name, type of material and manufacturer’s batch number.

- Materials from more than one batch: Store separately. Allocate to distinct parts or areas of the work.

### Wet paint signs

- Requirement: Provide where necessary.

### Control samples of coating systems

- Sample areas of finished work: Complete wall area as sample panel before progressing, location tbc

- Timing: Apply during preliminary installation.

- Approval of appearance: Obtain before starting general coating work.

### Preparation for coating systems generally

- Standard: Comply at all times with BS 6150: 2006 Code of Practice for Painting of Buildings (or as amended) and BS EN ISO 12944: 1998 Paints and Varnishes - Corrosion Protection of Steel Structures by Protective Paint Systems (or as amended). and manufacturers recommendations

- Substrates: Sufficiently dry in depth to suit coating.

- Suspected existing hazardous materials: Prepare risk assessments and method statements covering operations, disposal of waste, containment and reoccupation, and obtain approval before commencing work.

- Efflorescence salts: Remove.

- Dirt, grease and oil: Remove.

- Contamination of surfaces and substrates: Give notice.

- Surface irregularities: Remove.

- Joints, cracks, holes and other depressions: Fill flush with surface. Provide smooth finish.

- Dust, particles and residues from preparation: Remove and dispose of safely.

- Water-based stoppers and fillers: Apply before priming.

- Oil based stoppers and fillers: Apply after priming.

### Applying coating generally

- Application: In order to achieve the optimum results, it is extremely important to adhere to the systems and AkzoNobel Decorative Paints Site Work Instructions vEXT1 quoted

- Environmental conditions: Maintain suitable temperature, humidity and air quality during application and drying.

- Surfaces: Clean and dry at time of application.

- Thinning and intermixing of coatings: Not permitted unless recommended by manufacturer.

- Overpainting: Do not paint over intumescent strips or silicone mastics.

- Initial coats:

  - Thickness: To suit surface porosity.

  - Application: As soon as possible on same day as preparation is completed.

- Finish: Even, smooth and of uniform colour. Free from brush marks, sags, runs and other defects.

- Cutting in: Cut in neatly.

## External door

Steel faced door intended to be used in portable and modular buildings and other non-residential applications.

- Drawing Reference: Client definition drawing 30687-AR-DR-1101

- Conform to the following classification of characteristics in Annex ZA of standard EN 14351-1:2006:

- Dangerous substances - Self declaration as required

- Acoustic Performance - 32 (-2;-7) dB

- Thermal transmittance - 1.8W/m2K

- Door Furniture: 0210180424 - 4 Point emergency escape ironmongery Approved to LPS 1175 Level 4 (Burglary Resistance Test in stainless steel finish; CE Marked and Certified to EN 1125.Anti-thrust on Bottom Bolt

- Access Control Doors: Reinforcement panel for mag lock to be provided on access controlled doors

- Hinges: minimum of 3 stainless steel ball bearing butt hinges suited to leaf size and weight.

- External Sill: Standard threshold

- Door and Frame Finish: Polyester powder coat finish to a standard RAL / BS colour

- Configuration: Single action single configuration

- Frame and architraves: Hardwood, factory finished in BS/RAL colours

- Other Requirements:

- Door to be installed in accordance with manufacturers instructions

- Provide fabrication drawings of doors and ironmongery for review prior to manufacture

### Pre-Construction Survey

- Procedure: Before starting work on designated items, take the site dimensions, record them on shop drawings and use them to ensure accurate fabrication.

- Primary support structure: Carry out survey sufficient to verify that required accuracy and security of erection can be achieved

- Timing: Before fabrication

### Installing external doorsets or frames

- Standard: In accordance with BS 8213-4.

- Fixings and fasteners: In accordance with manufacturers recommendations

- Protection: Materials dry until fixed. Protect insulating glass units and plastics glazing units from the sun and other heat sources

### Fixing of loose thresholds

- Spacing of fixings (maximum): 100 mm from each end and at 450 mm centres

- Position and level: Ensure threshold is level and square to door frame and leaf

- Sealing: Ensure that voids are minimal and are sealed adequately

### Installation of emergency and panic exit device

- Installation: Emergency exit devices in accordance with BS EN 179.

### Preparation

- Surrounds, rebates, grooves and beads: Clean and prepare safely before installing subframe or window units. Take necessary precautions for minimizing exposure where lead-based paint is present and execute work in accordance with method statements

- Surfaces inaccessible after installation: Prime or seal before fixing components

## Windows

- Drawing Reference: Drawings 30687-AR-DR-1101,3001, 3002 and 3011

- Windows W1-7 and W12 are to be replaced with new fixed shut toughened glass double glazed units.

- One way mirror film to inside of double glazed units.

- The window frames will comply with BS EN 12608 PAS 24 with Kitemark KM522039

- 6.2mm laminated glazing will be resistant to manual attack using the axe test set out in BS EN 356.

- Windows W8-11 are to be removed and a new Plastisol coated external steel skin provided over the openings (colour to match existing). Internally the void is to be infilled with PIR insulation and then to receive ply and plasterboard as detailed above.

### Pre-Construction Survey

- Procedure: Take site dimensions, record on shop drawings and use to ensure accurate fabrication.

- Primary support structure: Carry out survey sufficient to verify that required accuracy and security of erection can be achieved

- Timing: Before fabrication

### Workmanship generally

- Standard: In accordance with BS 8000-7 generally

- Integrity: Window system installations must be wind and watertight under all conditions with full allowance made for deflections and other movements

- Materials Compatibility: No contact between glazing panes and/ or units and alkaline materials such as cement and lime

- Protection: Materials dry until fixed. Protect insulating glass units and plastics glazing units from the sun and other heat sources

### Preparation

- Surrounds, rebates, grooves and beads: Clean and prepare safely before installing subframe or window units. Take necessary precautions for minimizing exposure where lead-based paint is present and execute work in accordance with method statements

- Surfaces inaccessible after installation: Prime or seal before fixing components

### Window installation generally

- Installation: Into existing window openings

- Plastics windows: In accordance with British Plastics Federation publication Code of practice for the installation of PVC-u windows and doorsets in new domestic dwellings

- Distortion:  Windows installed without twist or diagonal racking.

## Glazing Mirror Film

See section 6.8 of Plowright Specification

## External services compound fencing and gate

- Drawing Reference: Client definition drawing 30687-AR-DR-1101 and 3011

- Supplier: JB Corrie and Co Ltd (or equivalent).

- Type: 50mm x 50mm square mesh fencing on square section fence posts (inner perimeter). Colour: green to match existing perimeter fencing on site

- Height: 1.8m above ground level

- Finish: Galvanised and polyester powder coated

- Gates: Single Leaf 1200mm hinged gates, complete with sliding latch and padlock

- Other Requirements:

- Allow for concrete bases to primary fence posts, approx. 600mm below adjacent ground level.

# PLOWRIGHT SPECIFICATION

### New Stud Walls

- Drawing Reference: Client definition drawing 30687-AR-DR-1101

- Manufacturer: British Gypsum

- System reference: GypWall ‘C’ stud

- System: 92 S 50 stud @ 600mm centres

- 1 no. layer 12mm plywood (inner layer control room side) and 1 layer 12.5mm Gyproc Wallboard (outer layer) both sides.

Partition full height to structural or roof soffit scribed around service penetrations

- Head condition:

  - Type: Gypframe 94 DC 60 Deep Flange Floor and Ceiling Channels, fixed to new and existing structure (fixings to be recommended by British Gypsum to ensure robust connection to structure)

  - Deflection Allowance: +-25mm deflection head

- Finishing:

  - Type: Taped seamless finish.

  - Primer/ Sealer: 1 coat of Gyproc Drywall Primer.

- Accessories: As required and recommended by British Gypsum White Book technical guidance

- Framing: ‘C’ stud 92 S 50

- Insulation: Full fill Rockwool sound deadening quilt

- Linings:

  - Inner layers: 12mm plywood

  - Face layer: 12.5mm Gyproc Wallboard full height of partition

- Fasteners: British Gypsum Drywall screws as recommend by supplier, screws to be corrosion resistant

- Manufacturer: British Gypsum

Standard: To BS EN 14566.

Screw type: Manufacturer's standard.

Head type: Countersunk cross head.

Length: Manufacturer's standard.

Ensure a minimum penetration of 10mm into metal framing through the board

- Joint treatment: Gyproc Joint Cement

- Finish: refer to client definition drawing

- System accessories: Dry lining beads, corner beads and others as required for installation

- Other requirements: Select appropriate fixing types to suit substrate to ensure partition stability

### Execution

### Installing framed partitions generally

- Standard: To BS 8000-0 and BS 8212.

- Deviations and tolerances:

  - Vertical deviation (maximum): ± 5 mm measured above or below the setting out position, in accordance with BS 8212 clause 3.3.2.

  - Horizontal deviation (maximum): ± 3 mm measured at the setting out level (ceiling or floor), in accordance with BS 8212 clause 3.3.2.

  - Finished surfaces: Maximum deviation band of 10 mm in accordance with BS 8212 clause 3.3.3.

### Installing framing for partitions

- Partition height: 4500mm

- Head condition: existing roof soffit

- Layout: Single row studs.

- Setting out:

  - General: Accurately align and plumb.

  - Frame and stud positions: Equal centres, to suit linings. Maintain sequence across openings.

  - Additional supports: At board edges and partition perimeters;

For partition heads;

For services and service outlets;

For fire and smoke dampers;

For central heating radiators;

For kitchen wall cupboards;

For kitchen floor cupboards;

and For sanitary appliances.

- Fixing perimeter framing to supporting structures: Fix at maximum 600 mm centres.

- Head deflection allowance (maximum): +-25mm

- Openings:

  - General: Form accurately.

  - Openings for doorsets: Provide sleeved or boxed metal studs a to achieve strength grade requirements for framing assembly and adequately support weight of door.

  - Services penetrations: Allow for associated fire stopping.

### Installing plasterboard to metal framing

- Fixings: British Gypsum Drywall screws as recommend by supplier, screws to be corrosion resistant

- Wall linings: Fix securely.

- Fixing centres (maximum):

  - Single layer boarding: 300 mm centres generally and 200 mm centres at external angles.

  - Multi-layer boarding: Inner layers at 300 mm centres round perimeters; face layer at 300 mm centres.

- Fixing positions: Position screws 10 mm minimum from edges of boards.

- Screw heads: Set in a depression. Do not break paper or gypsum core.

### Sealing gaps and air paths around partitions

- Location of sealant: To perimeter abutments and around openings. At board-to-board and board-to-metal frame junctions in pressurized shafts and ducts.

- Application: To clean, dry and dust free surfaces as a continuous bead with no gaps. After sealing, fill gaps greater than 6 mm between floor and underside of plasterboard with jointing compound.

### Installing insulation and cavity barriers in framed partitions

- Insulation:

  - Fitting: Secure with closely butted joints and no gaps.

  - Rigid insulation: Fit tightly between studs.

  - Non rigid insulation: Fix at head of frame using timber battens or metal clips.

- Cavity barriers:

  - Generally: Form accurately with no gaps at joints and perimeters. Mechanically fix securely across full width of cavity.

  - Fire rated partitions: Include cavity barriers to ceiling or floor void above, below or between partitions. Provide same rating for barrier as partition.

  - Junctions: Seal perimeter abutments, service penetrations, etc. Prevent penetration of smoke and flame.

### Installing gypsum based board

- General: Use fixing, jointing, sealing and finishing installation methods recommended by board manufacturer.

- Cutting plasterboard: Neat and accurate. Do not damage core or tear paper facing.

- Cut edges: Minimize. Position at internal angles wherever possible. Mask with bound edges of adjacent boards at external corners.

- Fixing boards: Securely, to suitably prepared and accurately levelled backgrounds.

- Finishing: Neat. Provide flush, smooth, flat surfaces free from bowing and abrupt changes of level.

### Installing additional supports

- Support to board edges and perimeters: At board edges and lining perimeters, as recommended by board manufacturer to suit type and performance of lining

- Fixtures and fittings: For all fixtures, fittings and service outlets, mark framing positions clearly and accurately on linings. Accurately position all additional framing and fix securely.

### Level of dry lining across joints

- Sudden irregularities: Not permitted.

- Joint deviations:

  - General: Measure from faces of adjacent boards using methods and straightedges (450 mm long with feet/ pads) to BS 8212.

  - Tapered edge joints: 3 mm maximum permissible deviation across joints when measured with feet resting on boards.

  - External angles: 4 mm maximum permissible deviation for both faces.

  - Internal angles: 5 mm maximum permissible deviation for both faces.

### Joints between gypsum based boards

- Surfaces exposed to view: Horizontal joints not permitted. Seek instructions if partition height exceeds maximum available board dimension.

- Multi-layer boarding: Stagger joints between layers by at least 600 mm.

- Board edges: Support with additional framing. In multi-layer boarding, support edges of outer layer.

- Joints: Centre on studs. Stagger joints on opposite sides of studs. In multi-layer boarding, stagger joints between layers.

- Edge profile:

  - Tapered: Butt.

  - Square: 3 mm gap.

  - Cut or unbound edges: 3 mm gap.

- Finish: Tape and fill.

### Seamless jointing to gypsum boards

- Cut edges of boards: Lightly sand to remove paper burrs.

- Filling and taping: Fill joints, gaps and internal angles with jointing compound and cover with continuous lengths of paper tape, fully bedded.

- Protection of edges and corners: Reinforce external angles, stop ends, etc. with specified edge/ angle bead.

- Finishing: Apply jointing compound. Feather out each application beyond previous application to give a flush, smooth, seamless surface.

- Nail and screw depressions: Fill with jointing compound to give a flush surface.

- Minor imperfections: Remove by light sanding.

### Repairs to plasterboard

- Filling small areas with broken cores:

  - Generally: Cut away paper facing, remove loose core material and fill with jointing compound.

  - Finish: Flush, smooth surface suitable for redecoration.

- Large patch repairs:

  - Generally: Cut out damaged area and form neat hole with rectangular sides. Replace with matching plasterboard.

  - Fixing: Use methods to suit type of dry lining, ensuring full support to all edges of existing and new plasterboard.

  - Finishing: Fill joints, tape and apply jointing compound to give a flush, smooth surface suitable for redecoration.

### Installing steel frames for linings

- Setting out:

  - General: Accurately align framing, setting studs vertically.

  - At openings: Maintain sequence.

  - Additional frames: At corners and board edges.

- Openings:

  - General: Form accurately.

  - Doorsets: Provide sleeved or boxed metal studs and/ or suitable timber framing to achieve strength grade requirements for framing assembly and adequately support weight of door.

  - Services penetrations: Allow for associated fire stopping.

- Studs:

  - Perimeter framing: Fix securely to supporting structures at maximum 600 mm centres.

  - Intermediate bracing: Permitted at mid height.

### Installing beads

- Cutting: Neatly using mitres at return angles.

- Fixing: Securely using longest possible lengths, plumb, square and true to line and level, ensuring full contact of wings with substrate.

- Finishing: After joint compounds/ plasters have been applied, remove surplus material while still wet from surfaces of beads exposed to view

## New glazed walls

- Drawing Reference: Elevation drawings 30687-AR-DR-3006 and 3007

- Product reference: Polar 30 Single Glazed partition system

- Manufacturer: Komfort Partitioning Ltd

- Web: www.komfort.com

- Contact: Daniel Davies

- Email: daniel.davies@komfort.co.uk

- Tel: 07711 417876

- Location: Plowright Control Room

- Performance of completed system: Severe Duty

- Fire resistance to BS 476-22: Non-rated – refer to drawings for locations

- Acoustic insulation to BS EN ISO 10140-1:2010 + BS EN ISO 10140-2:2010: 34db (Rw)

- Structural Performance in accordance with BS 52342:1992 and BS 6180:2011 0.74kN

- Partition height: 2100mm (600mm above FFL to ceiling height 2700mm)

- Deflection allowance: Not required

- Glazed panels: Head Channel: into 30mm head channel (K30HT), base channel K30FT with K54BG Glazing Bead

- Glass: 12mm toughened glass

- Glazing joints:

- In-line: Bubble (SJ34/K35BJ)

- 90°Corner junction: NA

- Manifestation: To conform to Document ‘N2’ of the Building Regulations 1992)

- Obscure glazing film: 900mm high

- Framework finish: Kolourframe polyester powder coated

- Colour: From standard Komfort colour range – to be selected by client

- Installation: Frame installation and glazing to be carried out by Komfort Partitioning Solutions

## Existing glazed curtain wall

- Type: New polyester powder coated steel/aluminium panels to match existing

- Fixings: To match existing

- Colour: To match existing

- Cleaning: Glazing and rebate area to be thoroughly cleaned prior to installation of the panels

## Decoration / finishing

### Steelwork Glazing Frame

- New steelwork to have 2 no. coats Hammerite Red Oxide Primer

### New Walls

- Walls to have mist and 2 no. coats emulsion from the Dulux Trade Diamond matt range

- New mdf skirtings, architraves and window boards to match existing

- Skirtings/architrave/window board/window head to be primed and 2 no. coat Dulux Trade Diamond matt range to match existing

### Existing Walls

- 2 no. coats emulsion from the Dulux Trade Diamond matt range

- Existing skirtings/architraves to have 1 no. coat Dulux Trade Quick Dry Satinwood to match existing

- Drawing Reference: Client definition drawing 30687-AR-DR-1102

- System manufacturer: AkzoNobel

- Product: Dulux Trade

- Preparation: The amount of preparatory work required on a Previously Coated Surface can vary considerably due to a variety of circumstances. This System is for Preparation up to and including partial failure/breakdown. Thoroughly clean down to remove all surface contamination. Carefully scrape back to a firm edge all areas of defective paint coatings and rub down to 'feather' the broken edges. Scrape and wire brush corroded steel to produce a clean metal surface. Rub down with a suitable abrasive and *dust off. All manually prepared surfaces should be prepared to a minimum standard of St3. BS EN ISO 8501-1: 2007 at the time of coating. Note *When rubbing down dry and/or dusting off wear a suitable face mask to avoid the inhalation of dust. (See AkzoNobel Site Work Instruction vExt1. for further information.)

- Finishing coats: 2 coats of Dulux Trade each applied to give a minimum wet film thickness of 50 microns per coat, giving a minimum dry film thickness of 25 microns per coat

- Products supplied for the carrying out of this specification are compliant with Statutory Instrument 2005 No. 2773 (Environmental Protection) - The Volatile Organic Compounds in Paints, Varnishes and Vehicle Refinishing Products Regulations 2005

### Execution

### Handling and storage of coating materials

- Coating materials: Deliver in sealed containers, labelled clearly with brand name, type of material and manufacturer’s batch number.

- Materials from more than one batch: Store separately. Allocate to distinct parts or areas of the work.

### Wet paint signs

- Requirement: Provide where necessary.

### Control samples of coating systems

- Sample areas of finished work: Complete wall area as sample panel before progressing, location tbc

- Timing: Apply during preliminary installation.

- Approval of appearance: Obtain before starting general coating work.

### Preparation for coating systems generally

- Standard: Comply at all times with BS 6150: 2006 Code of Practice for Painting of Buildings (or as amended) and BS EN ISO 12944: 1998 Paints and Varnishes - Corrosion Protection of Steel Structures by Protective Paint Systems (or as amended). and manufacturers recommendations

- Substrates: Sufficiently dry in depth to suit coating.

- Suspected existing hazardous materials: Prepare risk assessments and method statements covering operations, disposal of waste, containment and reoccupation, and obtain approval before commencing work.

- Efflorescence salts: Remove.

- Dirt, grease and oil: Remove.

- Contamination of surfaces and substrates: Give notice.

- Surface irregularities: Remove.

- Joints, cracks, holes and other depressions: Fill flush with surface. Provide smooth finish.

- Dust, particles and residues from preparation: Remove and dispose of safely.

- Water-based stoppers and fillers: Apply before priming.

- Oil based stoppers and fillers: Apply after priming.

### Applying coating generally

- Application: In order to achieve the optimum results, it is extremely important to adhere to the systems and AkzoNobel Decorative Paints Site Work Instructions vEXT1 quoted

- Environmental conditions: Maintain suitable temperature, humidity and air quality during application and drying.

- Surfaces: Clean and dry at time of application.

- Thinning and intermixing of coatings: Not permitted unless recommended by manufacturer.

- Overpainting: Do not paint over intumescent strips or silicone mastics.

- Initial coats:

  - Thickness: To suit surface porosity.

  - Application: As soon as possible on same day as preparation is completed.

- Finish: Even, smooth and of uniform colour. Free from brush marks, sags, runs and other defects.

- Cutting in: Cut in neatly.

## Floor

- Drawing Reference: Client definition drawing 30687-AR-DR-1102

- Type: Forbo Struktur 2 Linear 50x50cm carpet tiles fitted in accordance with manufacturers recommendations.

- Colour: To be selected by client from the following range

- Format: To be selected by client

### Execution

### Installation control samples

- Required samples:

  - Types: Forbo Struktur 2 Linear

  - Purpose: For use as an installation reference sample.

  - Timing: Lay during preliminary installation. Obtain approval of appearance before proceeding.

### Condition of building and notification of commencement

- Condition of works before laying materials:

  - Building envelope: Weathertight and well dried out.

  - Wet trades: Finished.

  - Paintwork: Finished and dry.

  - Conflicting overhead work: Complete.

  - Floor service outlets, duct covers and associated fixtures: Fixed, where materials are to be cut.

- Notification prior to laying floor coverings (minimum): 48 hours.

### Conditioning of flooring prior to laying

- Standards: To BS 8203 and BS 5325.

- General:

  - Before laying: Condition materials by unpacking and separating in spaces where they are to be laid.

  - Resilient flooring rolls: Maintain in an upright position.

  - Carpet: Unroll and keep flat on a supporting surface.

- Conditioning time and temperature (minimum):

  - Generally: As recommended by manufacturer.

  - Materials stored or transported at a temperature below 10°C immediately before laying: Extend time by a factor of two.

### Environmental conditions before, during and after laying

- Temperature and humidity: Maintain approximately at levels which will prevail after building is occupied.

- Ventilation: Adequate.

- Underfloor heating before laying: Turn off at least 48 hours before start of laying.

### Assessing suitability of bases

- Existing bases:

  - Notification: Before commencing work, confirm that existing bases will, be suitable to receive coverings.

  - Suitability of bases and conditions within any area: Do not lay coverings on unsuitable bases and in unsuitable conditions.

- New wet-laid bases:

  - Base drying aids: Do not use for at least four days before moisture content testing.

  - Base moisture content: Test in accordance with BS 5325, Annexe A or BS 8203, Annexe A.

  - Locations for readings: In all corners, along edges, and at regular centres over general areas being tested.

  - Laying coverings: Do not start until all readings show 75% relative humidity or less or as recommended by manufacturer.

### Remove existing floorings

- Base: Clear of covering and as much adhesive as possible. Skim with smoothing underlayment compound to give a smooth, even surface.

### Level of Existing Bases

- Existing sub bases to be levelled with self-levelling smoothing compound prior to laying new flooring

- Tolerances: Allow for grinding down/grouting high and low spots in existing concrete or other sub bases to ensure flatness tolerance of SR1+/-3mm maximum deviation from a 2m straight edge in contact with the floor (BS8204:part 2) is achieved for the flooring installations

- Levelling Compound:

Manufacturer: ARDEX UK Ltd

Product reference: ARDEX K 15 Rapid Drying Self-Levelling Sub-Floor Smoothing Compound

Primer: P51 primer

Other requirements: For thicknesses, greater than 7mm up to 35mm thick use ARDEX K 15-B (Base coat) and apply a 3mm smoothing layer of ARDEX K 15.

### Layout – setting out seams

- Setting out of seams: Seams to be hidden where possible and to line through parallel to walls.

### Colour consistency

- Appearance in any one area or room: Free from banding or patchiness.

### Welded or sealed seams

- Materials: Hot welding rods.

- Commencement (minimum): 24 hours after laying, or after adhesive has set.

- Joints: Neat, smooth. Strongly bond. Flush with finished surface.

### Joints at doorways

- Joint location: On centre line of door leaf.

### Fixing edgings and cover strips

- Fixing: Secure with edge of covering gripped. Use matching fasteners where exposed to view.

## Ceiling

- Drawing reference: 30687-AR-DR-1302, 1303

- Type: Ecophon Focus DG white 600x600x20 ceiling tiles

- Other works: Ceiling outside proposed control room to be amended with suspended plasterboard to match existing

- Ceiling Support: Interlocking Connect T24 HD grid

- Support Fasteners: Adjustable hangers/wires, direct fixing barckets

- Ceiling Units: High-density glass wool tiles

- System Accessories: Connect Bridging profile and clip, Edge tool DG, Laser Angle, Lighting Clip 0231 Edge 500, Focus Frieze Dg/Ds Panel 2400 x 600, Focus DG wing

- Size: 600 x 600/to match existing

- Colour/Finish: To match existing

- Grid Colour: White 01

- Trim: Connect Angle trim, Modular Wall, Shadowline 0668

- Lighting/Ventilation: See relevant Scitech drawings

- Weight: 3-4 kg/m2

- Demounting Depth (minimum): 30mm

- Indoor Climate: Recommended by the Swedish Asthma and Allergy Association. Certified as A+ by French VOC. Emission classification of building materials: M1

- Moisture resistance: Class C, relative humidity 95% and 30°C, according to EN 13964:2014

- Fire Safety: To BS EN 13501-1, Class A2-s1, d0

- Sound Absorption: 200 mm-deep system: in accordance with EN ISO 11654, Class A

- Cleaning: The ceiling system can withstand daily dusting and vacuum cleaning, and weekly wet-wiping

### Execution

### Demountable suspended ceiling preliminary installation

- Installation requirements: Complete an area of suspended ceiling in an agreed location.

- Position: Sample rooms for ceiling types

- Extent of area: Entire room

- Timing: Construct and obtain approval of appearance before proceeding with general installation. Retain undisturbed until completion of demountable suspended ceiling installation.

### Demountable suspended ceiling control samples

- Purpose: Submit representative samples for approvals and establishment of quality.

- Samples to be submitted: Ceiling support and Infill units.

- Timing: Representative samples to be submitted during detailed design prior to starting construction work and to be kept on site until project completion.

### Installing demountable suspended ceilings generally

- Standard: To BS EN 13964

- Stability: Where required, install additional bracing and stiffening to give a stable ceiling system resistant to design loads and pressures.

- Out of sequence working: Supply and fix initial tiles for early fixing of ceiling mounted services; Supply and fix initial tiles for early fixing of heat/ smoke detectors and Supply and fix initial tiles for early fixing of sprinkler heads.

### Protective coverings

- Remove at completion.

### Setting out demountable suspended ceilings

- Appearance of completed ceiling: Over the whole of the surface exposed to the room below, a continuous and even surface, jointed (where applicable) at regular intervals.

- Building elements and features to which the ceiling systems relate: Give notice if not square, straight or level.

- Grid: Position to suit infill unit sizes. Allow for permitted deviations from nominal sizes of infill unit.

### Infill and access units, integrated services

- Fit correctly and align.

### Edge or perimeter infill unit size (minimum)

- Half standard width or length.

### Corner infill unit size (minimum)

- Half standard width and length.

### Infill joints and exposed suspension members

- Straight, aligned and parallel to walls.

### Protection of demountable suspended ceilings

- Loading: Do not apply loads for which the suspension system is not designed.

- Ceiling materials: When necessary, remove and replace correctly using special tools and clean gloves, etc. as appropriate.

### Installing cavity fire barriers above demountable suspended ceilings

- Maximum ceiling void dimension in any direction: 20 m.

- Position of barriers: On line of partition and maximum 20 m apart in any direction.

- Fixing: Secure barrier at head and base using proprietary angle support system. Fix angle support system to steel framework. Fix barriers securely to channels or angles at abutments to building structure.

- Fixing at perimeters and joints: Secure, stable and continuous with no gaps to provide a complete barrier to smoke and flame.

- Joints: Form to preserve integrity in fire.

- Service penetrations: Cut barriers neatly to accommodate services. Fit fire resistant sleeves around flexible materials. Fill gaps around services to fire barrier manufacturer's recommendations to maintain barrier integrity. Independently support services passing through the barrier on both sides of the barrier so that no load is placed on the barrier in the event of a fire.

### Ceiling systems not intended for fire protection

- Do not mechanically interlink barriers with ceiling system.

### Installing air plenum barriers above demountable suspended ceilings

- Requirements: Permanently stable, continuous and airtight.

- Fixing: Fix tightly at perimeters and joints using methods recommended by the barrier manufacturer.

- Edges and joints: Seal effectively to prevent air leakage.

- Special requirements: Where barriers are also fire and smoke barriers, double boarding with staggered joints will be required to achieve the designated fire and smoke rating. Restrain quilted barriers on all edges and stitch and lap as manufacturers' instructions to achieve the required fire and smoke rating.

### Installing upstands and bulkheads to demountable suspended ceilings

- Vertical ceiling systems: Support and brace to provide alignment and stability.

- High upstands: Provide support at base of upstand.

### Installing integrated services in demountable suspended ceilings

- Criteria: Position services accurately, support adequately. Align and level in relation to the ceiling and suspension system. Do not diminish performance of ceiling system.

- Small fittings: Support with rigid backing boards or other suitable means. Do not damage or distort the ceiling.

- Surface spread of flame rating of additional supporting material: Not less than ceiling material.

### Services outlets:

Supported by ceiling system

Provide additional hangers.

Independently supported

Provide flanges to support ceiling system.

Services in ceiling void

Space beneath installed services to be sufficient for installation and removal of ceiling system components and periodic removal and replacement of infill units.

## Motorised roller blinds

- 3 no. Silent Gliss SG4970 electric operated roller blind system

- Colour/fabric to be selected by client

## Glazing Mirror Film

- Drawing Reference: Client definition drawing 30687-AR-DR-1102

- Manufacturer: Purlfrost Ltd. Vision 3, Kendal Avenue, London, W3 0AF.

- Type: SRF 20 Dark Reflective Window Film

- Location: As noted on drawings; to be fitted internally

- Performance:

UV Radiation				99%

Visible light transmition		18%

External visible light reflection	60%

Internal visible light reflection		60%

Total solar energy rejected		79%

Solar energy reflection		55%

Solar energy absorption		55%

Solar energy transmission		55%

Glare reduction			83%

Solar heat gain (G value)		0.20

U-value (W/sq.mK)			5.10

Shading coefficient			0.22

- Warranty: 7 Years

- Storage: Store for up to 3 years in a dry place, between -5 and +40 C

- Construction:

"Hard" scratch resistant layer, for durability and ease of maintenance during window cleaning

High optical quality polyester, with anti IR metal particles deposit

Bonding adhesive

High optical quality polyester

PS adhesive, glass polymerization within 15 days

Protection release liner, disposable after installation

- Maintenance Instructions:

For best cleaning results, do not clean the film for 30 days after installation. Do not use brushes, pure ammonia, industrial strength cleaners, or solutions that contain abrasive materials. Always use a soft clean cloth to wash and dry your windows. Avoid coarse paper towels. A rubber squeegee may also be used

- Application:

Step by step instructions on how to apply window film & frost glass

Regardless of the type of window film or stickers you purchase, whether frosted, tinted, mirror or decorative, the principle on how to fit window film will be the same.

Glass Preparation (the crucial task)

Make a slip solution using a few drops of washing up liquid mixed with water in a spray bottle and thoroughly clean the glass. Use a glass scraper to remove specks of paint, or any other glass covering like stickers.

Film Cutting

Unless your window film is already cut to size, and if the film has a paper liner with a metric grid, measure your glass at the top and bottom, and left and right and mark and cut your window film. You can also cut the film bigger than required and trim it once applied to the glass.

Film Application

A. Thoroughly wet the glass with the slip solution.

B. Place the window film face down an a flat surface and expose a small amount of the adhesive or cling side.

C.  Spray the adhesive or cling side liberally with the slip solution as you peel off the protective liner.

D. Slip the adhesive or cling side of the film on the glass butting one edge and the top against the window frame or rubber gasket (double glazed unit).

Squeegee Technique

A. Liberally wet the face of the film with the solution to act as a lubricant fro your squeegee or felt edged tool.

B-C. Squeeze out the solution from under the film using a firm and even pressure, starting from the top and working your way down and across the film.

Film Trimming

Run a credit card and a retractable knife blade down the edge of the glass to trim any excess film. The thickness of the card will allow for a small gap to help any remaining solution to be squeezed out. Once trimming is complete go over the film once more to squeeze out all the solution.

Final Checks

1. Make sure that all the solution has been squeezed out.

2. Wipe the film and any remaining solution with paper towel.

3. Inspect the film on both sides of the glass to check for any trapped solution or air bubbles.