## Opt1
Company Name:-
| Project:- CSSD Plant Room Fire Escape |  | Quoted Project Costs
and Kitchen Corridor refurbishment and Cath Lab Staircase
|  | Design Area | Costs
1 | Back Ground
2 | The CSSD plant room has been extended and a new fire escape install. However the fire escape opens up and there is a drop of 4 meters, the plan is to install a platform and create an fire exit through into the kitchen corridor. As well as refurbishing the corridor.
3 | Contract
4 | The Contractor is deemed to have visited site prior to tender or submission of quotation to check all details and dimensions themselves. Any plan issued in connection with this contract is for guidance only. All works to meet with current Approved Documents for England and Wales. JCT minor works contract conditions will apply A retention of 2.5% will be required for 12 months following practical completion. List of Drawings for guidance only: 1. CA/FS/CSSD 070416
5 | Provide all necessary plant, labour, materials, protective hoardings, notices, signage and welfare accommodation to allow safe completion of the works. Ensure all works comply with the Health & Safety at Work Act 1974 & Construction Design & Management Regulations 2007. The Contractor shall provide Method Statements and Construction Phase Plan as necessary.
6 | All construction work to comply with the Princess Alexandra Trust current Health & Safety Policy, a copy of which is available for review at this office. In particular your attention is drawn to Standards for Contractors Health & Safety requirements "Site rules" Appendix 1
7 | Where works may interfere with smoke / fire detection contact the PAH Estates Department & obtain a permit to work. Allow for any temporary disconnection / or protection of the system for the duration of the works. Upon completion ensure the system is reinstated & left in good working order.
8 | Allow to clear away from site all waste and debris arising from the works where appropriate using skips. No waste is to be left for this NHS trust disposal. At the end of each working day the site is to be left clean and tidy using the contractors own cleaning equipment. Plant, equipment, materials and tools are the sole liability of the contractor and should not be left on site outside of normal working hours.
9 | All electrical work to be undertaken to comply with good practise, British Standards BS 7671: 2001 (2004) equivalent European Standard and in accordance with the current edition of the IEE Wiring Regulations. Work to be undertaken by an approved NIC EIC installer. Provide a test certificate on completion.
10 | All contractors must visit, survey the site and check the current capacity of the Static Systems Nurse Call, Electrical Distribution Board(s) to ensure adequate loading provision for additional LED light fittings and power sockets to ensure there will be adequate provision within the cost for the systems expansion prior to the tender submission.
11 | Scope of Works
12 | Prelims
13 | Site set up
14 | skips
15 | Preparation
16 | Site preparation:
17 | CSSD Court yard
18 | Allowing for hoarding, taping of doors to conceal dust and debris entering into corridor.
19 | Liaising with Estates, completing permit to works, isolate fire alarm, heating services , Domestic services and Electrical power.
20 | Allow to liaise with Plateform manufacture to install Plateform in court yard
21 | Remove and relocate Condesing unit,Electrics, and pipe work, liaising with Estates. Locate the condensing below the window line on the left hand wall as looking at the condesing unit.
22 | Remove Fire doors in Kitchen corridor
23 | Cut New fire door opening into main Kitchen corridor.
24 | Allow for 1nr new 30 minutes fire resistant single door (DR23) + frames + door closers + kick plates + vision panels+ intumescent strips and all ironmongery. Complete with door frame and thresh hold.
25 | Main Kitchen Corridor
26 | Relocate removed fire doors to position shown on drawing
27 | Fire protection
28 | Replace the existing ceiling from old position of fire doors up to the new position with 1hr fire board.
29 | Remove old ceiling tiles by auto-matic doors Allow for new Armstrong Bioguard 95% RH 600x 600mm Tegular Suspended ceiling system. Include tegular perimeter edge trim, laid in accordance with manufacturer recommendations. From: Armstrong World Industries Ltd., Building Products Division, Armstrong House, 38 Market Square, Uxbridge UB8 1NG. Phone: 0800 371849
30 | Allow to remove old wall protection
31 | Decoration
32 | Corridors, Waiting Areas.
33 | Dulux Trade Diamond High Performance (D598) 2 Coats: Colour White Cotton
34 | Trim and Interior joinery (door frames, skirting)
35 | Dulux Quick Dry (D1043) 3 coats: Colour Grey OONN 53/000
36 | Wall Protection
37 | Install wall protection: Allow to install :-Aluminium Chequer Plate 2500 x 1250 X3mm Five Bar Pattern 3mm Base Thickness both sides of corridor designing in protection for doors, Allow for secure fixing.
38
39
40
41 | Estimated Cost of Building Works Only sub Total
42 | Contingency
43 | Total |  | 0
44 | Add VAT @ 20% |  | 0
45 | Include any other works
46 | Total Estimated Project Cost