Stand alone pumping stations

Annual costs

Site No 12		
Site Name: Elizabeth Road, Wokingham RG40 1UB

Descriptions in this listing are abbreviated forms of the full description in paragraph 10 of Schedule 1 of the Conditions of Contract – The Services; the numbering also relates to that section.

| No | Description | Unit | Quant’y | Rate | £ | P |
| --- | --- | --- | --- | --- | --- | --- |
| 1) | Safety: Follow safety requirements specified and all other good working practices at all times. |  |  |  |  |  |
| 4 (III) (a) 4 (I) (c) 6) 4) (III) (b) | Monthly: Isolate electricity supply and remove covers: (i) Check appearance of internals and ensure that all retaining fittings are present and secure. (ii) Clear any debris from the inlet and outlet pipes and other areas of the mechanism where they may cause malfunction. (iii) Replace covers and make secure. (iv) Reinstate electricity supply. (v) Check noise of operation. Mechanical maintenance to be carried out as described in this section and in the datasheets and in accordance with the plant manufacturers’ recommendations where provided. Control Kiosk (a) All equipment must be isolated before any maintenance work is carried out. (b) Inspect all cables and fittings. Check heater and thermostat setting where present. Check operation of indicators, lamps, lights and security of earthing straps. (c) Check and reset overloads. (e) Alert the Contract Administrator to recurrent issues, particularly, but not limited to, repeated needs to reset equipment and recurrent overloads. Pumps Pump pits to be opened and checked and pumps should be checked visually and audibly, pumps should be run manually to check operation and then be returned to auto mode, check hoses and pipework for wear and tear or damage. | Per visit Per visit Per visit Per visit | 12 12 12 12 |  |  |  |
| 4) (I) (b) 5) 4) (III) | Quarterly: Oil all locks. Meter reading (a) Read and record the electricity meter. (b) Advise the Contract administrator of the latest meter reading, the previous quarter meter reading and the units consumed, drawing attention to excessively high or low consumption. Pumps (c) Lift floats as appropriate, clean and return. (d) Check greasers and replace as necessary. | Per visit Per reading Per Pump | 4 4 4 |  |  |  |
| 2) (a) 6 (d) | Six monthly: The Contractor shall test earth continuity every six months in accordance with the plant manufacturers’ requirements and current IEE Regulations. Any electrical faults found that require urgent attention must be reported to the Contract Administrator the same day. Clean the control kiosk, remove cobwebs and dirt and wash down exterior | Per test Per clean | 2 2 |  |  |  |
| 4 (III) | Annually: Pump (e) Check up to 100m upstream manholes for signs of backing up. (f) Empty (1807 litres), remove rags etc, jet wash to remove fat build up and leave clean. (g) (i) Replace covers and make secure. (ii) Reinstate electricity supply. (iii) Check noise of operation (h) Undertake bench test of pumps. | Per set of inspect-ions Per empty Per clean Per clean Per test | 1 1807 1 1 2 |  |  |  |
| 2) (b) | Three yearly: The Contractor shall arrange for periodic inspection and testing of all electrical installations (BS 7671:1992 as amended) and for issuing a copy of the Test Certificate to the Contract Administrator. This shall be undertaken in the third year of the contract. Certificates relating to the electrical installations at the commencement of the contract shall be available from the Contract Administrator. (Enter annual equivalent – 1/3 total cost) | 3 yearly inspection | 1/3 |  |  |  |