Frimley Park Hospital Main Generator G59
We would like to invite quotations to update our existing two main generators control system, to allow for short and long term parallel operation with the mains.
Initially this is to allow for a no-break operation whilst conducting generator tests, followed by long term operation as required during CHP maintenance.

Generators
· Dorman 1000kVa
· FG Wilson 1000kVa
 Controls
· Both generators use ComAp Intelisys controls
System Operation
The system currently operates by synchronising both generators then switching over to supply the site. No provision for paralleling with the mains is currently available on these two generators.
Requirements 
 
Replace existing generator controls 
· Install G59/3 mains protection relay

· Test and commission the new system outside normal working hours

· Supply and connection of 2 x 1000 kVA temporary generators to be used whilst the existing generators and control systems are being modified to provide emergency backup in the case of mains failure
· Load banks to carry out load testing

· Fuel management Including standby diesel for 8 hours continuous running

· Carry out G59 injection testing proving system and witness testing with SSE protection engineer

· Co-ordination of all works including all Health and Safety

· Certificates

· Full O&M manual

Page | 1

