Rutherford Appleton Laboratory

BREEAM 2018 UK New Construction

BREEAM Excellent Specification

Certification Requirements

- The Contractor must adhere to the BREEAM Pre-Assessment and subsequent reports at all times. Some specific clauses have been inserted into the Contract Prelims, M&E and Architectural specifications. These are not exhaustive and ongoing liaison with the BREEAM Assessor must continue throughout the programme.

- Where a credit cannot be achieved, the Principal Contractor is required to request a change in writing to the assessor and propose an alternative credit to equal value in order to ensure the required Excellent rating is achieved.

- The appointed main contractor must demonstrate submission of the BREEAM Design Stage assessment, sufficient to achieve an Excellent rating, within 3 months of meaningful start on site. Evidence must consist of an email from the BRE confirming submission, and a date for initial feedback. Should the initial feedback be returned with comments requiring further action, a follow up submission must be demonstrated, by the same means, within 2 weeks. A Design Stage certificate demonstrating a BREEAM Excellent rating has been achieved must be issued to the client or client representative no later than 6 months from start on site.

- In order to issue Practical Completion by the client’s representative, the appointed main contractor must provide a BREEAM Post Construction Stage certificate demonstrating a rating of BREEAM Excellent. Should the certificate be unavailable due to BRE QA timescales or the information not being available to issue to the assessor at this stage, Practical Completion will only be issued subject to acceptable (to the client representative) correspondence from the BREEAM Assessors, or the BRE, indicating the current stage of progress and the score being targeted. This must include a detailed summary of all outstanding information and a methodology and timescale for completion of the assessment including a date for submission and, following this, a copy of the BRE’s email confirming the date for initial feedback. A Post Construction Stage certificate demonstrating a BREEAM Excellent rating has been achieved, must be issued to the client or client representative no later than 6 months from Practical Completion.

Credit 1 Man 01 Project brief and design - Project Delivery Planning

The client and their Design Team Consultants will ensure:

- Prior to completion of the Concept Design, the client and design team meet  to identify and define for each key phase of project delivery:

- Roles

- Responsibilities

- Contributions.

- The design team consultant will consider each one of the following items when defining roles, responsibilities and contributions for each key phase of the project:

- End user requirements

- Aims of the design and design strategy

- Particular installation and construction requirements/limitations

- Design and construction risk assessments e.g. CDM, legionella risk assessment

- Legislative requirements e.g. building control notification, heritage requirements

- Procurement and supply chain

- Identifying and measuring project success in line with project brief objectives

- Occupiers' budget and technical expertise in maintaining any proposed systems

- Maintainability and adaptability of the proposals

- Requirements for the production of project and end user documentation

- Requirements for commissioning, training, and aftercare support.

- Where the building occupants are not known, the list of considerations above still applies. The appropriate items will be considered, based on likely scenarios of building occupancy. The project team will demonstrate how the contributions and the consultation process outcomes influence the following:

- Initial Project Brief

- Project Execution Plan

- Communication

- Concept Design.

Credit 2 Man 01 Project brief and design - Stakeholder Consultation (Interested Parties)

- Prior to completion of the Concept Design, the client and Design Team consult with all interested parties outside of the design team and public stakeholders, outside of the design team, on matters that cover the minimum consultation content.

- The Design Team Consultants will demonstrate how the stakeholder contributions and consultation exercise outcomes influence the Initial Project Brief and Concept Design.

- Prior to completion of the detailed design (RIBA Stage 4, Technical Design or equivalent), all interested parties have been opportunity to give and receive consultation feedback.

Minimum Consultation Content:

Consultation content is dependent on the building type but the design team will ensure the following items are considered:

- Functionality, build quality and impact (including aesthetics).

- Provision of appropriate internal and external facilities (for future building occupants and visitors or users).

- Management and operational implications.

- Maintenance resources implications.

- Impacts on the local community, e.g. local traffic or transportation impact.

- Opportunities for shared use of facilities and infrastructure with the community or appropriate

- stakeholders.

- Compliance with statutory (national or local) consultation requirements.

- Energy use and sustainability measures.

- Implementing principles and processes that deliver an inclusive and accessible design.

- The end users' broad requirements for such facilities, including appropriate sizing, optimisation and

- integration of equipment and systems.

Credit 3 Man 01 Project brief and design – BREEAM AP (Concept Design)

The Client has ensured a BREEAM AP has been appointed and involved in the project during Concept Design stage at the appropriate time/level to:

- Work with the project time, including the client, to consider the links between BREEAM issues and assist them in maximizing the project’s overall performance up to Concept Design

- Monitor progress against the performance targets

- Proactively identify risks and opportunities related to achievement of targets

- Provide feedback to the project team to support them making corrective actions and achieving agreed performance targets

- Monitor and coordinate the generation of appropriate evidence by the project team.

Credit 4 Man 01 Project brief and design – BREEAM AP (Developed Design)

The Contractor must ensure a BREEAM AP has been appointed and involved during the developed design phases at the appropriate time to:

- Work with the project time, including the client, to consider the links between BREEAM issues and assist them in maximizing the project’s overall performance up to Concept Design

- Monitor progress against the performance targets

- Proactively identify risks and opportunities related to achievement of targets

- Provide feedback to the project team to support them making corrective actions and achieving agreed performance targets

- Monitor and coordinate the generation of appropriate evidence by the project team.

Credit 1 Man 02 Life cycle cost and service planning – Elemental LCC

The Design Team Consultants will ensure an elemental life cycle costing exercise is undertaken at RIBA Stage 2 in accordance with the following requirements:

- A competent person carries out an outline, entire asset LCC plan at Process Stage 2 (equivalent to Concept Design - RIBA Stage 2) together with any design options appraisals in line with 'Standardised method of life cycle costing for construction procurement' PD 156865: 2008

- The elemental LCC plan is  to provide an indication of future replacement costs over a period of analysis as required by the client (e.g. 20, 30, 50 or 60 years); includes service life, maintenance, and operational cost estimates.

- Design Team Consultants will demonstrate how the elemental LCC plan has been used to influence building and systems design and specification to minimise life cycle costs and maximise critical value.

Credit 3 Man 02 Life cycle cost and service planning – Capital Cost Reporting

- The Contractor will report the capital cost for the building in pounds per square metre of gross internal floor area (£k/m2) as part of the submission to BRE.

- The contractor will provide specific capital costs in (£k/m2) for the following items:

- Construction, including preparatory works, materials, equipment and labour

- Site management

- Construction financing

- Insurance and taxes during construction

- Inspection and testing

Prerequisite Man 03 Responsible construction practices – Legally Harvested and Traded Timber

- The Demolition and Principal Contractor will ensure all timber and timber-based products used during the construction process of the project are legal and sustainable timber, in accordance with the below definition.

Legally harvested and sustainable timber

BREEAM follows the UK government's definition of legally sourced timber, as outlined in the Central Point of Expertise on Timber (CPET) 5th Edition report on the UK Government Timber Procurement Policy.  At the time of writing, the policy requires all timber and wood-based products to be covered by at least one of the following:

- Third party, independent forest certification schemes–Category A (e.g. FSC or PEFC)

- Evidence on a case-by-case basis in line with the Framework for Evaluating Category B evidence–Category B.

- For the avoidance of doubt, the contractor must ensure 100% of the timber and timber-based products are compliant.

Further information on the UK Government's TPP and compliant responsible sourcing certification schemes is available from the CPET website.

Reusable timber formwork itself does not automatically comply. The Contractor will ensure all timber used in the manufacturing of the formwork must be covered by a responsible sourcing certification scheme (RSCS) recognised by BREEAM. See Guidance Note 18 for the BREEAM recognised RSCS.

Credit 1 Man 03 Responsible construction practices – Environmental Management

The Demolition Contractor and Principle Contractor will operate an environmental management system (EMS) covering their main operations. The EMS must be in place prior to any works commencing on site and be either:

- Third party certified, to ISO 14001:2015, EMAS (EU Eco-Management and Audit Scheme) or equivalent standard; or

- Have a structure that is in compliance with BS 8555:2003 and has reached phase four of the implementation stage, ‘implementation and operation of the environmental management system’, and has completed defined phase audits 1 to 4, as defined in BS 8555:2003.

The Demolition Contractor and Principal Contractor implement best practice pollution prevention policies and procedures on site in accordance with Pollution Prevention Guidelines, Working at construction and demolition-sites: PPG6, and complete the PPG6 form.

Credit 2 Man 03 Responsible construction practices – BREEAM AP (site)

- The Contractor will appoint a BREEAM Advisory Professional who is site based or attends site regularly, in addition to the BREEAM AP appointments made for Man 01 credits, prior to construction works commencing. The BREEAM AP will:

- Work with the project team to consider the links between BREEAM issues and assist them in achieving and if possible going beyond the design intent, to maximise the project’s performance against the agreed performance targets throughout the Construction, Handover and Close Out stages.

- Monitor construction progress against performance targets throughout all stages where decisions critically impact BREEAM performance.

- Proactively identify risks/opportunities related to the procurement and construction process and the achievement of targets.

- Provide feedback to the constructors and the project team to support them in taking corrective actions and achieving their agreed performance targets.

- Monitor and coordinate the generation of appropriate evidence by the project team and the provision to the assessor.

Credit 3 Man 03 Responsible construction practices – Responsible Construction Management

- The Demolition Contractor and Principal Contractor must achieve all items listed in table 4.1 Responsible construction management items, of the BREEAM New Construction 2018 Guidance.

- The Demolition Contractor and Principal Contractor will provide relevant evidence and documentation to demonstrate compliance with items listed in Table 4.1 of the BREEAM New Construction 2018 Guidance.

- The Demolition Contractor and Principal Contractor will complete Table 1 of BRE’s Guidance Note 33 ’Responsible Construction Management’.

- The Demolition Contractor and Principal Contractor will register the site with the Considerate Constructors Scheme (CCS).

- The Demolition Contractor and Principal Contractor must achieve a minimum site score of 35 on the CCS, and a minimum of 7 in each of the five categories. Doing so will automatically result the Contractor compliance with a-f, h-o, r-s.

Table 4.1 Responsible Construction Management, BREEAM New Construction 2018 Guidance

| Item | Criteria |
| --- | --- |
| Risk Evaluation and Implementation |  |
| Vehicle Movement |  |
| A | Manage the construction site entrance to minimise the impacts (e.g. safety, disruption) arising from vehicles approaching and leaving the development footprint. |
| B | Ensure the development footprint is accessible for delivery vehicles fitted with safety features (e.g. side under run protection) to remove or limit the need for on-street loading or unloading. Where on-street loading is unavoidable, this should be appropriately managed. |
| C | Identify access routes to the development footprint, including for heavy vehicles to minimise traffic disruption and safety risks to others. |
| Pollution Management |  |
| D | Minimise the risks of air, land and water pollution. |
| E | Minimise the risks of nuisance from vibration, light and noise pollution. |
| Tidiness |  |
| F | Practices ensure the development footprint is safe, clean and organised at all times. This includes, but is not limited to, facilities, materials and waste storage. |
| G | Ensure clear and safe access in and around the buildings at the point of handover. |
| Health and Wellbeing |  |
| H | Provide processes and equipment required to respond to medical emergencies. |
| I | The principal contractor identifies and implements initiatives to promote and maintain the health and wellbeing of all site operatives within the development footprint. This can be via site facilities, site management arrangements, staff policies etc. |
| J | Establish management practices and facilities encouraging equality, fair treatment and respect of all site operatives. |
| K | Provide secure, clean and organised facilities (e.g. changing and storage facilities) for site operatives within the development footprint. |
| Security Processes |  |
| L | Minimise risks of the site becoming a focus for antisocial behaviour in the local community (e.g. robust perimeter fencing, CCTV, avoid creating dark corners etc.). |
| Training, Awareness, and Feedback |  |
| M | Aspects of the construction process that might impact the community are communicated regularly, ensuring that nuisance and intrusion are minimised. |
| N | Ensure ongoing training is provided, and up to date, for personnel and visitors (covering items a to l, as appropriate.) |
| O | The principal contractor ensures that site operatives are trained for the tasks they are undertaking (including any site-specific considerations). |
| P | The fleet operators (see Definitions on page 56), undertakes driver training and awareness to promote safety within the development footprint and off site. |
| Monitoring and Reporting |  |
| Q | The fleet operators, captures and investigates any road accidents, incidents and near misses and reports them back to the principal contractor. The principal contractor analyses these items. |
| R | All visitor, workforce and community accidents, incidents and near misses are recorded and action is taken to reduce the likelihood of them reoccurring. |
| S | Processes are in place to facilitate collecting and recording feedback from the community and to address any concerns related to the development footprint. |

Credit 4 Man 03 Responsible construction practices – Monitoring of Construction Site Impacts

- The Demolition Contractor and Principal Contractor will assign responsibility to an individual for monitoring, recording and reporting energy use, water consumption and transportation data resulting from all on-site construction processes (and dedicated off-site manufacturing) throughout the build programme.

First monitoring credit – Utility consumption

Energy consumption

- The Demolition Contractor and Contractor will monitor and record data of the site energy consumption in kWh (and where relevant, litres of fuel used) as a result of the use of construction plant, equipment (mobile and fixed) and site accommodation.

- The Demolition Contractor and Contractor will report the total carbon dioxide emissions (total kgCO2/project value) from the construction process to the BREEAM Assessor.

Water consumption

- The Demolition Contractor and Contractor will monitor and record data on principal constructor's and subcontractors' potable water consumption (m³) arising from the use of construction plant, equipment (mobile and fixed) and site accommodation as relevant to the project type.

- Using the collated data, the Demolition Contractor and Contractor will report the total net water consumption (m³), i.e. consumption minus any recycled water use from the construction process to the BREEAM Assessor.

Second monitoring credit – Transportation of construction materials and waste

Demolition Contractor and will monitor and record data separately on transport movements and impacts resulting from delivery of the majority of construction materials to site and construction waste from site. As a minimum this must cover:

- Transport of materials from the point of supply to the building site, including any transport, intermediate storage and point of supply. Scope of this monitoring must cover the following as a minimum:

- Materials used in major building elements

- Ground works and landscaping materials

- Transport of construction waste from the construction gate to waste disposal processing or recovery centre gate. Scope of this monitoring must cover the construction waste groups outlined in the project's resource management plan.

- Using the collated data, report separately for materials and waste, the total transport-related carbon dioxide emissions (kgCO2eq), plus total distance travelled (km) to the BREEAM Assessor.

Credit 1 Man 04 Commissioning and handover – Testing Schedule and Responsibilities

- The Contractor will develop a schedule of commissioning and testing. The schedule identifies and includes a suitable timescale for commissioning and re-commissioning of all complex and non-complex building services and control systems and for testing and inspecting building fabric.

- The schedule identifies the appropriate standards for all commissioning activities to be conducted, in accordance with, where applicable:

- Current Building Regulations

- BSRIA guidelines

- CIBSE guidelines

- Other appropriate standards.

- Exclude from the assessment any process or manufacture-related equipment specified as part of the project. However, include such equipment in cases where they form an integral part of the building HVAC services, such as heat recovery systems.

- The Contractor will ensure an appropriate project team member(s) is appointed to monitor and programme pre-commissioning, commissioning, testing and, where necessary, re-commissioning activities on behalf of the Client. The Contractor will confirm this individual within the commissioning schedule.

- The Contractor accounts for the commissioning and testing programme, responsibilities and criteria within their budget and main programme of works, allowing for the required time to complete all commissioning and testing activities prior to handover.

Building Management Systems:

Where a building management system (BMS) is specified, the Contractor must ensure the following commissioning procedures are carried out:

- Commissioning of air and water systems is carried out when all control devices are installed, wired and functional.

- Include physical measurements of room temperatures, off-coil temperatures and other key parameters as appropriate.

- The BMS/controls installation should be running in auto with satisfactory internal conditions prior to handover.

- All BMS schematics and graphics (if BMS is present) are fully installed and functional to user interface before handover.

- The occupier or facilities team is fully trained by the Contractor in the operation of the system.

Credit 2 Man 04 Commissioning and handover – Design and Preparation

The Contractor must appoint an appropriate project team member during design stage, who will be responsible for:

- Undertaking design reviews and giving advice on suitability for ease of commissioning

- Providing commissioning management input to construction programming and during installation stages

- Management of commissioning, performance testing and handover or post-handover stages

For buildings with complex building services and systems, this role needs to be carried out by a specialist commissioning manager.

The Contractor will confirm who this individual is to the BREEAM Assessor and ensure the individual provides a statement/document on how they will address and act on points 1-3.

Specialist Commissioning Manager

The specialist commissioning manager is a specialist contractor rather than a general sub- contractor, able to independently verify the work carried out by the project team members installing the systems. The specialist commissioning manager can be appointed by the client or the contractor to perform the tasks described under the relevant criteria for buildings with complex building services and systems and defined in their contract. The specialist commissioning manager shall be a professional who, in the opinion of the assessor, has experience or qualifications that enable them to undertake the responsibilities described in this issue. As an example, membership to the Commissioning Specialists Association (CSA) is a relevant qualification.

Credit 3 Man 04 Commissioning and handover – Testing and Inspecting Building Fabric

- The Contractor must complete post-construction testing and inspection to quality-assure the integrity of the building fabric, including continuity of insulation, avoidance of thermal bridging and air leakage paths (this is through airtightness testing and a thermographic survey). The Contractor appoints a suitably qualified professional to undertake the survey and testing in accordance with the appropriate standard.

- The Contractor must ensure they rectify any defects identified during post-construction testing and inspection prior to building handover and close out. Any remedial work must meet the required performance characteristics for the building or element as defined at the design stage.

- The Contractor must ensure the thermographic survey covers 100% of the treated spaces, unless it is a large complex building. Ensure that all elements of the building fabric that enclose an internal heated or conditioned (treated) zone of the building are tested. This includes internal walls separating treated and untreated zones.

Suitably Qualified Professional

Thermography surveys and airtightness testing are to be undertaken by suitably qualified professionals in accordance with the appropriate standards, as follows:

- Airtightness testing: by professionals with membership of Air Tightness Testing and Measurement Association (ATTMA) or Independent Air Tightness Testing Scheme (IATS) attained at organisational level.

- Thermographic survey: by professionals holding a valid Category 2, e.g. PCN (Personnel Certification in Non-Destructive Testing) or QCF (Ofqual's Qualification and Credit Framework) or RQF (Regulated Qualifications Framework) Level 4, e.g. ABBE (Awarding Body for the Built Environment), certificate in thermography (as defined by the UKTA (UK Thermography Authority) website). Where a Category 2 or Level 4 thermographer is not available, the survey may be undertaken by a Category 1 thermographer and then the images interpreted by a Category 2 or Level 4 thermographer.

Credit 4 Man 04 Commissioning and handover – Handover

- Prior to handover, the Contractor will develop two building user guides:

- A non-technical user guide for distribution to the building occupiers

- A technical user guide for the premises’ facilities managers.

- A draft copy must be developed and discussed with users first to ensure the guide is most appropriate and useful to potential users.

- The Contractor must prepare two training schedules timed appropriately around handover and proposed occupation plans for:

- A non-technical training schedule for building occupiers

- A technical training schedule for the premises’ facilities managers.

- The Contractor must document all training given, date training was delivered, and personnel in attendance.

Building user guides

The Contractor will develop a building user guide that is a dedicated building/site specific guidance for the non-technical building user. The purpose of the guide will be to help building users access, understand and operate the building efficiently and in a manner in keeping with the original design intent. The Building User Guide will provide easily accessible and understandable information relevant to the following stakeholders:

- The building’s staff (or where relevant residents).

- The non-technical facilities management team/building manager.

- Other building users, e.g. visitors/community users.

The content of the guide will be specific to the building type and end users, but broadly the Contractor will include information on the following:

- Overview of the building and its environmental strategy, e.g. energy/water/waste efficiency policy/strategy and how users should engage with/deliver the policy/strategy.

- Provision of, and access to, shared facilities.

- Safety and emergency information or instructions.

- Building-related operational procedures specific to building type or operation, e.g. laboratories.

- Building-related incident reporting and feedback arrangements.

- Provision of and access to transportation facilities, e.g. public transport, cyclist facilities, pedestrian routes etc.

- Provision of and access to local amenities.

- Links, references and relevant contact details.

Additionally, for the non-technical building user guide for building occupiers:

- Building services overview and access to building occupant controls, e.g. where to find them, what they control, how to operate effectively and efficiently etc.

- Pre-arrival information for visitors, e.g. access and security procedures or provisions.

Additionally, for the technical building user guide for facilities managers:

- Building services overview and access to facilities management controls, e.g. where to find them, what they control, how to operate effectively and efficiently etc.

- Refit, refurbishment and maintenance arrangements or considerations

- Building related training information or links.

Training Schedule:

The training schedules shall include the following as a minimum:

- The building’s design intent.

Additionally, for the building occupiers’ training schedule:

- Introduction to the non-technical building user guide for building occupiers and other relevant building documentation.

- Additionally, for the facilities managers’ training schedule:

- The available aftercare provision and aftercare team main contacts, including any scheduled commissioning and post occupancy evaluation.

- Introduction to, and demonstration of, installed systems and key features, particularly building management systems, controls and their interfaces.

- Introduction to the technical building user guide for facilities managers’ and other relevant building documentation, e.g. design data, technical guides, maintenance strategy, operations and maintenance (O&M) manual, commissioning records, log book etc.

- Maintenance requirements, including any maintenance contracts and regimes in place.

Credit 1 Man 05 Aftercare – Aftercare support

The Contractor will provide aftercare support to the building occupiers through having in place operational infrastructure and resources, to include as a minimum:

- A meeting between the aftercare support team/individual, and the building occupier/management team (prior to initial occupation)

- Introduce the aftercare support available, including the content of the building user guide and training schedule.

- Present key information about features of the building including the design intent and how to use the building to ensure it operates efficiently and effectively as possible.

- On-site facilities management training including a walkabout of the building and introduction/familiarization with the building systems, controls and how to operate them in accordance with the design intent and operational demands.

- Provide initial aftercare support for at least the first month of building occupation, e.g. weekly attendance on-site to support building users and management.

- Provide longer term aftercare support for occupiers for at least the first 12 months from occupation, e.g. a helpline, nominated individual or other appropriate system to support building users/management.

- The Client/Tenant will establish operational infrastructure and resources to coordinate the collection and monitoring of energy and water consumption data for a minimum of 12 months, once the building is substantially occupier. This facilitates analysis of discrepancies between actual and predicted performance, with a view to adjusting systems and user behaviours accordingly. Where the Client appoints the Contractor to complete this data collection, the Contractor must do so in accordance with this requirement.

Credit 2 Man 05 Aftercare – Commissioning Implementation

The Contractor must complete the following commissioning activities over a minimum 12-month period, once the building becomes substantially occupied:

- Complex systems: the specialist commissioning manager will:

- Identify changes made by the owner/operator that might have cause impaired or improved performance.

- Test all building services under full load conditions, i.e. heating equipment in mid-winter, colling and ventilation equipment in mid-summer and under part load conditions (spring and autumn).

- Carry out testing during periods of extreme (high or low) occupancy, where applicable.

- Interview building occupants to identify problems or concerns regarding effectiveness of systems.

- Produce monthly reports comparing sub-metered energy performance to the predicted one.

- Identify inefficiencies and areas in need of improvement.

- Re-commission systems (following any work needed to serve revised loads) and incorporate any revisions in operating procedures into the operations and maintenance (O&M) manuals.

- Simple systems (naturally ventilated): the Contractor, aftercare team or facilities manager will:

- Review the thermal comfort, ventilation, and lighting, at three, six- and nine-month intervals after initial occupation, either by measurement or occupant feedback.

- Identify deficiencies and areas in need of improvement.

- Re-commission systems and incorporate any relevant revisions in operating procedures into O&M manuals.

Credit 3 Man 05 Aftercare –Post-Occupancy Evaluation (POE)

The Client/building occupier commits to carry out a POE exercise one year after the building is substantially occupied. This gains a comprehensive in-use performance feedback and identifies gaps between design intent and in-use performance. The aim is to highlight improvements/interventions that need to be made and to inform operational processes.

An independent party carries out the POE covering:

- Review of the design intent and construction process (review of design, procurement, construction, and handover processes).

- Feedback from a wide range of building users including facilities management on the design and environmental conditions of the building covering:

- Internal environmental conditions (light, noise, temp, and air quality)

- Control, operation, and maintenance

- Facilities and amenities

- Access and layout

- Energy and water consumption

- Other relevant issues, where appropriate

The independent party provides a report with lessons learned to the client/building occupiers.

The client/building occupier commits funds to pay for the POE in advance. This requires an independent party to be appointed to carry out the POE, evidence of the appointment and schedule of responsibilities which fulfils the BREEAM criteria are acceptable to demonstrate compliance.

Credit 1 Hea 01 Visual comfort – Control of Glare from Sunlight

- The Clients Design Team Consultants will identify areas at risk of glare using a glare control assessment. The glare control assessment also justifies any areas deemed not at risk of glare.

- Where the risk has been identified within a relevant building area, the Clients Design Team Consultant will confirm the glare control strategy to design out the potential for glare.

- The Contractor must install or construct the chosen glare control strategy.

- The Clients Design Team Consultant ensure the glare control strategy does not increase energy consumption used for lighting. This is achieved by:

- Maximizing daylight levels in all weather, cloudy or sunny AND

- Ensuring the use or location of shading does not conflict with the operation of lighting control systems.

- The Clients Design Team Consultants will ensure the glare control strategy provides shading from both high-level summer and low-level winter sun.

- Where blinds are the chosen glare control strategy, the Contractor must ensure they are installed to all areas at risk of glare from sunlight and the openness factor of the blinds is 1% or less, and the fabric light transmittance value is < 0.1 (10%).

Credit 3 Hea 01 Visual comfort – View Out

- The Clients Design Team Consultants will confirm whether 95% of the floor areas, in 95% of spaces for each relevant building area, provides an adequate view out for building occupants.

- The Clients Design Team Consultants will confirm whether an ‘adequate’ view-out is achievable by confirming floor depths/relevant building areas are within 8m of an external wall which has glazed area of ≥20% of the surrounding wall area.

- Alternatively, where room depth is greater than 8m the Clients Design Team Consultants confirm the percentage of glazing is ≥ values in Table 1.0 BS8206: Part 2.

- Where the Clients Design Team Consultants confirm either of the above are achievable based on the design, the Contractor must construct the development as designed to ensure as-built compliance.

Credit 4 Hea 01 Visual comfort – Internal and External Lighting Levels, Zoning and Control

Internal Lighting

The Clients Design Team Consultants will ensure:

- Internal lighting in all relevant areas of the building is designed to provide illuminance (lux) levels and colouring rendering in accordance with SLL Code for Lighting 2012 and any other relevant industry standard. Internal lighting should be appropriate to the tasks undertaken, accounting for building user concentration and comfort levels.

- Areas where computer screens are regularly used, the lighting design complies with CIBSE Lighting Guide 7 sections 2.4, 2.13 to 2.15, 2.20, and 6.10 to 6.20.

- The Contractor will ensure the internal lighting layouts are implemented as designed and the final internal lighting arrangements comply with points 1 and 2.

External Lighting

The Contractor will ensure:

- All external lighting located within the construction zone is specified in accordance with BS 5489-1:2013 Code for the practice for the design of road lighting. Lighting of roads and public amenity areas and BS EN 12464-2:2014 Lighting of workplaces - Part 2: Outdoor workplaces. External lighting should provide luminance levels that enable users to perform outdoor visual tasks efficiently and accurately, especially during the night.

Zoning and Occupant Control

The Clients Design Team Consultants will ensure the internal lighting is designed to ensure it is zoned to allow for occupant control in accordance with the criteria below for relevant areas present within the building:

- In office areas, zones of no more than four workplaces.

- Workstations adjacent to windows/atria and other building areas separately zoned and controlled.

- Seminar and lecture rooms: zoned for presentation and audience areas.

- Library spaces: separate zoning of stacks, reading and counter areas.

- Teaching space or demonstration area.

- Whiteboard or display screen.

- Auditoria: zoning of seating areas, circulation space and lectern area.

- Dining, restaurant, café areas: separate zoning of servery and seating/dining areas.

- Retail: separate zoning of display and counter areas.

- Bar areas: separate zoning of bar and seating areas.

- Wards or bedded areas: zoned lighting control for individual bed spaces and control for staff over groups of bed spaces.

- Treatment areas, dayrooms, waiting areas: zoning of seating and activity areas and circulation space with controls accessible to staff.

Any areas used for teaching, seminar or lecture purposes will have lighting controls provided in accordance with CIBSE Lighting Guide 5.

The Contractor will ensure they construct and install internal lighting controls in accordance with the Clients Design Team Consultants design and the above requirements, A-L for applicable rooms.

Prerequisite Hea 02 Indoor air quality – Indoor Air Quality (IAQ) Plan

- The Clients Design Team Consultants will ensure an Indoor Air Quality Plan is produced and implemented, with the objective of facilitating a process that leads to design, specification and installation decisions and actions that minimise indoor air pollution during the design, construction and occupation of the building. The Indoor Air Quality Plan will consider the following:

- Removal of contaminant sources

- Dilution and control of contaminant sources

- Procedures for pre-occupancy flush out

- Air quality requirements of specialist areas such as laboratories

- Third party testing and analysis

- Maintaining good indoor air quality in-use.

- The Contractor must ensure they implement all recommendations outlined in the indoor air quality and construct the development in accordance with this plan.

Credit 1 Hea 02 Indoor air quality – Ventilation

- The Clients Design Team Consultants will ensure the building has been designed to minimise the indoor concentration and recirculation of pollutants in the building as follows:

- Provide fresh air into the building in accordance with the criteria of the relevant standard for ventilation (see below).

- Ventilation pathways are designed to minimise the ingress and build-up of air pollutants inside the building.

- HVAC systems incorporate suitable filtration to minimise external air pollution, as defined in BS EN 16798-3:2017. The specified filters should achieve supply air classification of at least SUP 2.

- The Clients Design Team Consultants will confirm whether areas of the building are expected to be subject to large and unpredictable or variable occupancy patterns. Where this is applicable they will ensure carbon dioxide or air quality sensors are designed in to the scheme and:

- In mechanically ventilated buildings or spaces: sensors are linked to the mechanical ventilation system and provide demand-controlled ventilation to the space

- In naturally ventilated buildings or spaces: sensors either have the ability to alert the building owner/manager with CO2 levels exceed the recommended set point, or are linked to controls with the ability to adjust the quantity of fresh air, i.e. automatic opening windows or roof vents

- For naturally ventilated or mixed mode buildings, the design demonstrates that the ventilation strategy provides adequate cross flow of air to maintain the required thermal comfort conditions and ventilation rates in accordance with CIBSE AM10.

- The Contractor will ensure they implement the design teams ventilation strategy as designed and in compliance with points 1a-e.

- The Contractor ensures they install CO2 sensors where deemed applicable.

- The Contractor will ensure the final installed ventilation strategy meets one of the below ventilation strategy standards and has been implemented in accordance with one of the methodologies.

Relevant Standards for Ventilation

- Education buildings: Building Bulletin 101 or BS EN 13779 (excluding naturally ventilated buildings), whichever requires the higher performance.

- Clinical areas with controlled environmental conditions: HTM 03-01 Specialised ventilation for healthcare premises (England, Wales and Northern Ireland) SHTM 03-01 Ventilation for healthcare premises Part A: Design and Validation (Scotland) or BS ISO 17772-1:2017 (excluding naturally ventilated buildings), whichever requires the higher performance.

- All other buildings: BS ISO 17772-1:2017 or, for naturally ventilated buildings, CIBSE AM10.

Methodologies for Ventilation Strategies

The installation of air-conditioned and mixed mode buildings should minimise the build-up of air pollutants. Locations of ventilation intakes and airflow pathways should be designed in accordance with any or a combination of the following methods:

- Locating the building's air intakes and exhausts, in relation to each other and sources of external pollution, in accordance with the following best practice as appropriate:

- PD CEN/TR 16798-4:2017

- BRE FB 30 Ventilation for healthy buildings: Reducing the impact of urban air pollution (2011)

- BRE IP 9/14 Locating ventilation inlets to reduce ingress of external pollutants into buildings, as appropriate.

- CIBSE TM21(66).

- Pollutant dispersion modelling can be used to inform the location of the building's air intakes and exhausts in relation to each other and sources of external pollution. This can be achieved using either wind tunnel modelling or numerical modelling. Pollutant dispersion modelling in urban areas is complex, so it is important that the person carrying out the modelling is a competent individual.

- Positioning the building's air intakes and exhausts at least 10m of horizontal distance apart. Positioning intakes at least 10m horizontal distance from sources of external pollution (including the location of air exhausts from other buildings). The building's air intakes and exhausts should be located to reduce the risk of the intake air being contaminated by the exhausts. Exhausts or other pollutant sources should not be discharged into enclosed spaces, such as courtyards, in which intakes are also located.

Where significant levels of gaseous pollutants such as nitrogen dioxide are identified in the outdoor air, as in an Air Quality Management Area (AQMA), the use of appropriate gas phase filtration in the building ventilation system should be considered.

Design teams must ensure that filter performance is appropriate for the pollutant conditions experienced at the site.

The design of naturally ventilated buildings should minimise the build-up of air pollutants. Ventilation intakes and airflow pathways should be designed using the following methods: Following guidance given in:

- BRE FB 30 Ventilation for healthy buildings: Reducing the impact of urban air pollution (2011),

- BRE IP 9/14 Locating ventilation inlets to reduce ingress of external pollutants into buildings (2014), and,

- CIBSE TM21 Minimising pollutants at air intakes (1999), as appropriate.

These give guidance on ventilation strategies, and the optimum location of ventilation inlets, openable windows, and trickle and background ventilators to reduce ingress of external pollutants into buildings.

- Positioning openable windows/ and background ventilators over at least 10m of horizontal distance from sources of external pollution (including the location of any building-related air exhausts).

Credit 2 Hea 02 Indoor air quality – Emissions from Construction Products

- The Contractor must ensure all internal finishes and construction products applicable to material types listed below, meet emission limits, testing requirements and any additional requirements, as per Table 5.11: Emission criteria by product type, In BEEAM New Construction 2018 v3.0.

- Interior paints and coatings

- Wood-based products (incl. wood flooring)

- Flooring materials (incl. floor levelling compounds and resin flooring)

- Ceiling, wall, and acoustic and thermal insulation materials

- Interior adhesives and sealant (incl. floor adhesives)

Credit 3 Hea 02 Indoor air quality – Post-Construction Indoor Air Quality Measurement

The Contractor must complete post-construction indoor air quality measurement in accordance with the following requirements:

- Formaldehyde concentration in indoor air is measured post-construction (but pre-occupancy) and does not exceed 100ug/m3 averaged over 30 minutes (WHO guidelines for indoor air quality: Selected pollutants, 2010).

- Formaldehyde sampling and analysis is performed in accordance with ISO 16000-2 and ISO 16000-3.

- Total volatile organic compound (TVOC) concentration in indoor air is measured post-construction and does not exceed 500ug/m3 over 8 hours.

- TVOC sampling and analysis is performed in accordance with ISO 16000-5 and ISO 16000-6 or ISO 16017-1.

- Where levels are found to exceed these limits, the project team confirms the measures that have, or will be, undertaken in accordance with the Indoor Air Quality plan, to reduce the TVOC and formaldehyde levels to within the above limits.

- The measured concentration levels of formaldehyde (ug/m3) and TVOC (ug/m3) are reported to the BREEAM Assessor.

Credit 1 Hea 04 Thermal comfort – Thermal Modelling

- The Clients Design Team Consultants ensure thermal modelling is carried out using software in accordance with CIBSE AM11 Building Energy and Performance Modelling.

- The software used to carry out the simulation at the detailed design stage provides full dynamic thermal analysis. For smaller and more basic building designs with less complex heating or cooling systems, an alternative less complex means of analysis may be appropriate (such methodologies must still be in accordance with CIBSE AM11. The modelling will demonstrate the following:

- For air-conditioned buildings, summer and winter operative temperature ranges in occupied spaces are in accordance with the criteria set out in CIBSE Guide A Environmental design, Table 1.5; or other appropriate industry standard (where this sets a higher or more appropriate requirement or level for the building type); or the thermal environment in occupied spaces meet the Category B requirements for PPD, PMV and local discomfort set out in Table A.1 of Annex A of ISO 7730:2005

- For naturally ventilated/free running buildings:

- Winter operative temperature ranges in occupied spaces are in accordance with the criteria set out in CIBSE Guide A Environmental design, Table 1.5; or other appropriate industry standard (where this sets a higher or more appropriate requirement/level for the building type).

- The building is designed to limit the risk of overheating, in accordance with the adaptive comfort methodology outlined in CIBSE TM52: The limits of thermal comfort: Avoiding overheating in European buildings, 2013.

- For air-conditioned buildings, the PMV (predicted mean vote) and PPD (predicted percentage ofdissatisfied) indices based on the above modelling are reported to the BREEAM assessor who can then include it in their final Scoring and Reporting tool.

- To ensure the as-built development achieves the modelled thermal comfort levels, The Contractor must implement and construct the building as designed by the Clients Design Team Consultants. Where the design significantly changes and the final construction is significantly different to the building design the thermal modelling was based on, The Contractor must complete their own thermal modelling analysis in accordance with the above requirements, to re-confirm compliance.

Credit 2 Hea 04 Thermal comfort – Design for Future Thermal Comfort

- The Clients Design Team Consultants will ensure the thermal modelling demonstrates that the relevant requirements set out under Hea 04 above are achieved for a projected climate change environment.

- Where thermal comfort criteria are not met for the projected climate change environment, the project team demonstrates how the building has beenadapted, or designed to be easily adapted in the future using passive design solutions in order to subsequently meet the requirements under the paragraph above.

- For air-conditioned buildings, the PMV and PPD indices based on the above modelling are confirmed in the thermal comfort report.

- To ensure the as-built development achieves the modelled thermal comfort levels for a future climatic scenario, The Contractor must implement and construct the building as designed by the Clients Design Team Consultants. Where the design significantly changes and the final construction is significantly different to the building design the thermal modelling was based on, The Contractor must complete their own thermal modelling analysis in accordance with the above requirements, to re-confirm compliance.

Credit 3 Hea 04 Thermal comfort – Thermal Zoning and Controls

- The Clients Design Team Consultants will outline how the thermal modelling analysis has informed the temperature control strategy for the building and its users.

- The Clients Design Consultants Team and Contractor will ensure the designed and as-built strategy for proposed heating/cooling system(s) demonstrates that it has addressed the following:

- Zones within the building and how the building services could efficiently and appropriately heat or cool these areas. For example, consider the different requirements for the central core of a building compared with the external perimeter adjacent to the windows.

- Where specified, any new local cooling or heating services (or changes to existing services) are designed to ensure they do not conflict with core services (e.g. conflicts between two separate cooling systems, conflicts between core heating and locally provided cooling systems).

- The degree of occupant control required for these zones, based on discussions with the end user (or alternatively building type or use specific design guidance, case studies, feedback) considers:

- User knowledge of building services

- Occupancy type, patterns, and room functions (and therefore appropriate level of control required)

- How the user is likely to operate or interact with the system(s), e.g. are they likely to open windows, access thermostatic radiator valves (TRV) on radiators, change air-conditioning settings etc.

- The user expectations (this may differ in the summer and winter) and degree of individual control (i.e. obtaining the balance between occupant preferences, for example some occupants like fresh air and others dislike drafts).

- How the proposed systems will interact with each other (where there is more than one system) and how this may affect the thermal comfort of the building occupants.

- The need or otherwise for an accessible building user actuated manual override for any automatic systems.

- Both the Clients Design Team Consultants and Contractor will provide statements addressing points a-e.

Credit 1 Hea 05 Acoustics –

- The Clients Design Team Consultants  will ensure acoustic assessment is undertaken by a suitably qualified acoustician to confirm and ensure the building meets the appropriate acoustic performance standards and testing requirements for this building type, for the acoustic principals of:

- Sound insulation

- Indoor ambient noise level

- Room acoustics.

- The buildings performance for the three acoustic principles must comply with the relevant sections of BS 8233:2014.

- The Contractor must ensure the development is constructed in accordance with recommendations in this report.

- The Contractor is required to instruct a post-construction acoustic assessment to assess and confirm as built compliance with the above acoustic performance standards.

Credit 1 Hea 06 Security – Security of Site and Building

- The Clients Design Team Consultants  will ensure a Suitably Qualified Security Specialist (SQSS) conducts an evidence-based Security Needs Assessment (SNA) during or prior to Concept Design (RIBA Stage 2 or equivalent).

- The SQSS develops a set of security controls and recommendations for incorporation into the proposals. Those controls and recommendations aim to ensure that the design of buildings, public and private car parks and public or amenity space are planned, designed, and specified to address the issues identified in the preceding SNA.

- The Contractor must ensure the controls and recommendations proposed by the SQSS are implemented. Any deviation from those recommendations or solutions will need to be justified, documented, and agreed in advance with a SQSS.

Credit 2 Hea 07 Safe and healthy surroundings – Outside Space

- The Contractor will ensure there is an outside space providing building users with an external amenity area.

- The Contractor will ensure the space is of an appropriate size to provide enough amenity for the predicted number of building users during coffee or lunch breaks to gather, socialise, relax and connect with the natural environment. The space is predominantly intended for building staff, but can be used by other building users where relevant and beneficial to the building users. The Contractor will ensure the outside space must:

- Be an outdoor landscaped area, for example a garden, balcony or terrace; the majority of the space should be open to the sky

- Have appropriate seating areas and be non-smoking,

- Be located to ensure it is accessible to all building users and avoids areas that will have disturbances from sources of noise (e.g. building services, car parks, busy roads, delivery areas etc.).

Credit 1 Ene 01 Reduction of energy use and carbon emissions – Energy Performance

- The Contractor must ensure an accredited energy assessor models the as built energy performance of the building with modelling data sourced from National Calculation Method compliant energy modelling software.

- The Contractor will provide the resulting as-built BRUKL document to the BREEAM Assessor.

- The Contractor must ensure, as a minimum, the energy performance of the building results in a 0.4 energy performance ratio, equivalent to 4 breeam credits, when entering data from the as-built BRUKL into the BRE’s Assessment Scoring and Reporting Tool. The Contractor is required to meet this energy performance ratio as a minimum requirement for BREEAM Excellent.

- Additionally, the Contractor must ensure the building achieves the same energy performance as designed by the Clients Design Team Consultants, and evidenced in the as-designed brukl, RAL-ONE-R120-X-RP-M-2000 (P01) R120 Workshop - BRUKL Report (1), dated 20/10/2020. This will ensure the development’s energy performance achieves 6 Ene 01 credits.

Credit 2 Ene 01 Reduction of energy use and carbon emissions – Prediction of Operational Energy Consumption

- The Clients Design Team Consultants will ensure TM54 prediction of operational energy modelling is conducted and:

- Involve relevant members of the design team in an energy design workshop focusing on operational energy performance.

- Undertake additional energy modelling during the design and post-construction stage to generate predicted operational energy consumption figures.

- Report predicted energy consumption targets by end use, design assumption and input data (with justifications).

- Carry out a risk assessment to highlight any significant design, technical, and process risks that should be monitored and managed throughout the construction and commissioning process.

- The Contractor will ensure any recommendations resulting from the TM54 modelling and report and incorporated into the as built development.

Energy Workshop

The Clients Design Team Consultants will ensure the workshop establishes the levels of risk pertaining to the operational energy performance of the building. Discussion at the workshop will consider how the energy performance of the building will be affected by future weather patterns, changes of use and variations in the expected usage of the building and consider the resilience of building systems.

The outcomes of the workshop will be used to inform improvements to the design of the building and to the operational, maintenance and handover strategies. The energy performance risk assessment should inform the scenarios that are to be modelled.

Prediction of Operational Energy

The Design Teams’ suitably qualified energy modeller must model several scenarios creating a range of predicted consumptions, informed by a risk assessment of the building energy uses.

These scenarios will consider:

–  Weather

–  Operating hours for systems

–  Occupancy hours

–  Management factors.

The output of this modelling should be used to estimate the unregulated energy demand.

Credit 1 Ene 02 Energy monitoring – Sub-metering of End-Use Categories

- The Contractor must ensure the energy metering strategy is designed so energy metering systems monitor at least 90% of the estimated annual energy consumption of each applicable fuel is assigned to the end-use categories.

- The Contractor must ensure the energy consumption in the building is metered according to the total useful floor area.

- If the area is greater than 1,000m², the Contractor must ensure energy consumption is metered by end-use category with an appropriate energy monitoring and management system.

- If the area is less than 1,000m², the Contractor must use either:

- An energy monitoring and management system or

- Separate accessible energy sub-meters with pulsed or other open protocol communication outputs, for future connection to an energy monitoring and management system

- The Contractor must ensure building users can identify the energy consuming end uses, e.g. through labelling or data outputs.

- The Contractor must estimate the annual energy consumption of each end-use category. Where it is estimated an end use category accounts for less than 10% of the annual energy consumption for a given fuel type, it is not necessary for this end use to be sub-metered. The Contractor must demonstrate it is less than 10%.

- The Contractor will confirm any end-use categories that are not applicable to this development. End use categories to meter or confirm as non-applicable include: space heating, domestic hot water heating, humidification, cooling, ventilation, pumps, lighting, small power, renewable or low carbon systems, controls, other major energy consuming plant.

Credit 2 Ene 02 Energy monitoring – Sub-metering of High Energy Load and Tenancy Areas

The Contractor must ensure a significant majority of the energy supply is monitored with:

- An accessible energy monitoring and management system for

- Tenanted areas, or,

- Relevant function areas or departments in single occupancy buildings

Or,

- Separate accessible energy sub-meters with pulsed or other open protocol communication outputs to enable future connection to an energy monitoring and management system for

- Tenanted areas, or,

- Relevant function areas or departments in single occupancy buildings

Credit 1 Ene 03 External lighting

- The Contractor must ensure the external light fittings within the construction zone:

- Average initial luminous efficacy of not less than 70 luminaire lumens per circuit watt.

- All external light fittings are automatically controlled for prevention of operation during daylight hours and presence detection in areas of intermittent pedestrian traffic.

Credit 1 Ene 04 Low carbon design – Passive Design

- The Clients Design Team Consultants analyse the proposed building design and development during Concept Design to identify opportunities for the implementation of passive design measures, in a passive design analysis report.

- The Contractor must Implement the passive design measures recommended to reduce the total heating, cooling, mechanical ventilation, lighting loads and energy consumption in line with the passive design analysis findings.

- The Clients Design Team Consultants will quantify the reduced total energy demand and carbon dioxide (CO₂-eq) emissions resulting from the passive design measures and state these figures in the passive design analysis report.

- The Contractor must implement all recommendations in this report to ensure the as-built development meets energy demand reduction and CO2 saving stated.

Credit 2 Ene 04 Low carbon design – Low and Zero Carbon

- The Clients Design Team Consultants have completed a Low and Zero carbon Feasibility Study, RAL-ONE-R120-X-RP-M-0002 (P01) LZC STRATEGY REPORT.

- The contractor must implement all recommendations made in this report and install the Photovoltaic Panels and Air Source Heat Pumps as recommended.

Credit 1 Ene 06 Energy efficient transportation systems – Energy Consumption

- Where the lift included in the scheme has a rated speed greater than 0.15m/s the Clients Design Team Consultants must:

- Analyse the transportation demand and usage patterns for the building to determine the optimum number and size of lifts, escalators or moving walks

- The Contractor must,

- Calculate the energy consumption in accordance with BS EN 1SO 25745 Part 2 or Part 3 for one of the following:

- At least two options for each transportation type, (e.g. for lifts, hydraulic, traction or machine room-less (MRL)) OR,

- At least two options considering different system arrangements and control strategies

- Consider use of regenerative drives, where it produces an energy saving greater than the additional standby energy used to support the drives

- The Contractor must specify the transportation system with the lowest energy consumption following the energy calculation exercise.

Credit 2 Ene 06 Energy efficient transportation systems – Energy Efficient Features

- The Contractor must ensure the specified lift features the following energy efficient features:

- A standby condition for off-peak periods

- Lift car lighting and display lighting provides and average luminous efficacy across all fittings in the car of >70 luminaire lumens per circuit Watt

- Use of a drive controller capable of variable speed, variable voltage, and variable frequency (VVVF) control of the drive motor

- The Contractor must specify regenerative drives where their use is demonstrated to save energy.

Credit 1 Tra 01 Transport assessment and travel plan

- A Travel Assessment and Travel Plan have been completed by the Clients Design Team Consultants.

- The Contractor must ensure they implement all sustainable transport measures relating to the construction and final build of the development, in compliance with the BRE requirements in Tra 02. These currently include:

- The provision of a covered and lit cycle shelter containing 4 Sheffield stand cycle hoops.

- 11 electric vehicle charging points

- 2 showers

- Install of lockers

Additionally, to gain a further bream credit, the Contractor must consult with the Clients Design Team Consultants, and confirm 5% of car parking spaces can be allocated as car share spaces.

Credit 1 Tra 02 Sustainable transport measures – Transport Options Implementation

- A Travel Assessment and Travel Plan have been completed by the Clients Design Team Consultants. This has identified several sustainable transport measures that are currently part of the scheme.

- The Contractor must ensure they implement all sustainable transport measures relating to the construction and final build of the development, in compliance with the BRE requirements. These currently include:

- The provision of a covered and lit cycle shelter containing 4 Sheffield stand cycle hoops. The Contractor must implement the cycle storage in accordance with the following requirements:

- Cycles can be secured within spaces in racks with overhead covering. The cycle racks are set in or fixed to a permanent structure (building or hard standing) or alternatively, may be located in a locked structure fixed to, or part of, a permanent structure with appropriate surveillance

- The distance between each cycle rack, and the cycle racks and other obstructions, e.g. a wall, allows appropriate access to the cycle storage space for easy storage and access to bikes

- The storage facility or entrance to the facility is in a prominent site location visible to potential users from either an occupied building or a main access to a building

- The cycle storage facility has adequate lighting; demonstrated by meeting the lighting criteria in BREEAM issue Hea 01, credit 4.

- The lighting must be controlled to avoid out-of-hours use and operation during daylight hours, where there is sufficient daylight in or around the facility.

- 2 showers. The contractor must ensure the showers meet the following requirements:

- Provision of one shower for every 10 cycle storage spaces, subject to a minimum provision of one shower.

- Both male and female users must be catered for, either separate showers within shared gender-specific facilities (required provision split 50-50) or single shower cubicles and changing space for mixed use

- The showers do not need to be dedicated to cyclists and can be those shared with other users or uses.

- Eleven electric vehicle charging points. The Contractor must ensure:

- The charging points amount to at least minimum 3kW for at least 10% of the total car parking capacity for the development.

- Install of lockers. The Contractor must ensure:

- The number of lockers is at least equal to the number of cycle spaces required

- Lockers are in or adjacent to compliant changing rooms, where provided

- The lockers are sized appropriately for the storage of a cyclists’ equipment.

- The Contractor must work with the Clients Design Team Consultants to Identify further sustainable transport measures to ensure a minimum of 6 Tra 02 credits are achieved. Measures that development can incorporate, include:

- The existing accessibility index is greater than 8.

- Implement an increase in the accessibility through negotiation with a local bus, tram or train company.

- Provide a new enhanced bus stop or liaise with a company to provide a new route to the site.

- Provide a dedicated bus service.

- Provide a live public transport information system.

- Provide electric vehicle charging stations of a minimum 3kW for at least 10% of the total car parking capacity for the development.

- Set up a car sharing group or facility and provide priority spaces for at least 5% of the total car paring capacity for the development.

- Consult with the local authority on the state of local cycling network/public accessible pedestrian routes and agree to implement one proposition.

- Install compliant cycle store spaces to meet the minimum required levels.

- Provide at least 2 cyclist facilities: showers, drying room, lockers, changing facilities. At least 3 existing amenities are present.

- Ensure one new amenity is incorporated into the scheme.

Credit 1 Wat 01 Water consumption

- The Contractor must ensure the flow rates of water consuming components are set to achieve a 40% percentage improvement over a notional baseline building’s water consumption.

- All flow rates will be provided by the Contractor to the BREEAM Assessor at 3 bar pressure. The efficiency of the following ‘domestic scale’ water-consuming component must be included in the assessment (where specified):

- WCs

- Urinals

- Taps (wash hand basins and where specified kitchen taps and waste disposal unit)

- Showers

- Baths

- Dishwashers (domestic and commercial sized)

- Washing machines (domestic and commercial or industrial sized).

- The Contractor will provide a full schedule of water consuming sanitaryware, including specification, quantity of each specification installed, and the flush capacity or flow rate of each.

Credit 1 Wat 02 Water monitoring

- The Contractor will ensure the specification of a water meter on the mains water supply to the building.

- The Contractor will ensure water-consuming plant or building areas, consuming 10% or more of the building’s total water demand, are either fitted with easily accessible sub-meters or have watermonitoring equipment integral to the plant or area.

- The Contractor will ensure each meter (main and sub) has a pulsed or other open protocol communication output to enable connection to an appropriate utility monitoring and management system, e.g. a building management system (BMS), for the monitoring of water consumption.

- In buildings with swimming pools, or large water tanks and aquariums, the Contractor fits separate sub-meters on the water supply of the above and any associated changing facilities (toilets, showers etc.) irrespective of their water consumption levels.

- In buildings containing laboratories, the Contractor fits a separate water meter on the water supply to any process or cooling loop for ‘plumbed-in’ laboratory process equipment, irrespective of their water consumption levels.

Credit 1 Wat 03 Water leak detection – Leak Detection System

- The Contractor will Install a leak detection system capable of detecting a major water leak: On the utilities water supply within the buildings, to detect any major leaks within the buildings, AND,

- Between the buildings and the utilities water supply, to detect any major leaks between the utilities supply and the buildings under assessment.These could be:

- A permanent automated water leak detection system that alerts the building occupants to the leak OR an inbuilt automated diagnostic procedure for detecting leaks

- Activated when the flow of water passing through the water meter or data logger is at a flow rate above a pre-set maximum for a pre-set period of time. This usually involves installing a system which detects higher than normal flow rates at meters or sub-meters. It does not necessarily require a system that directly detects water leakage along part or the whole length of the water supply system

- Able to identify different flow and therefore leakage rates, e.g. continuous, high or low level, over set time periods. Although high and low level leakage rates are not specified, the leak detection equipment installed must have the flexibility to distinguish between different flow rates to enable it to be programmed to suit the building type and owner's or occupier's usage patterns.

- Programmable to suit the owner's or occupier's water consumption criteria

- Where applicable, designed to avoid false alarms caused by normal operation of large water-consuming plant such as chillers.

Credit 2 Wat 03 Water leak detection – Flow Control Devices

- The Contractor must install flow control devices that regulate the water supply to each WC area or sanitary facility according to demand, in order to minimise undetected wastage and leaks from sanitary fittings and supply pipework.

Credit 1, Credit 2 and Exemplary Credit Mat 01 Environmental impacts from construction products – Building LCA – Superstructure, Substructure, Core Services – Concept Design Stage

- The Clients Design Team Consultants have completed Concept design stage Life cycle analysis (LCA) and design options appraisal on the proposed  Superstructure design.

- The Clients Design Team Consultants have completed Concept design stage Life cycle analysis (LCA) and design options appraisal on the proposed Substructure and Hard Landscaping design.

- The Clients Design Team Consultants have completed Concept design stage Life cycle analysis (LCA) and design options appraisal on the proposed  core building services design.

- The Concept Design stage LCA and appraisal on the superstructure, substructure and hard landscaping, and core services has been submitted to the BRE prior to the planning application.

Credit 3: Mat 01 Environmental impacts from construction products – Building LCA – Superstructure – Technical Design Stage.

- At Technical Design Stage the Clients Design Team Consultants will lead a building life cycle analysis and design option appraisal exercise on the Stage 4 design of the proposed development. Where in contract at/during stage 4, the Contractor will additional input into this process.

- The Contractor will be required to engage early from the point of contract to ensure this exercise is commenced, and the Contractor’s input is provided, at the appropriate time.

- The Contractor must collaborate the Clients Design Team Consultants / individual conducting the life cycle analysis to validate and improve the design stage data on materials.

- The Contractor must provide the exact specification and manufacturer for all materials that are to be used in the construction of the superstructure of the building.

- The Contractor must provide accurate quantities for all materials that are to be used in the superstructure of the building.

- The Contractor will use the building elements from the RICS New Rules of Measurement, as stated in table 9.1 of the BREEAM New Construction 2018 v3.0 guidance, to confirm the building element location of each material.

- The Contractor will engage with the Clients Design Team Consultants to develop different technical design option appraisals, which will consider different material specifications. Additionally, the Contractor will therefore input into the options appraisal summary document developed by the design team.

Credit 1 Mat 02 Environmental impacts from construction products - EPD

- Environmental Product Declarations (EPDs) are product/material specific life cycle analyses assessing the embodied and whole-life cycle environmental impacts of a product. When procuring materials the Contractor must request form the manufacturers, EPDs on their products.

- The Clients Design Team Consultants will specify and recommend products and materials with environmental product declarations wherever possible.

- The Contractor must specify construction products with environmental product declarations wherever possible. Where a material the Contractor wants to procure and use on the scheme does not have an EPD, the Contractor must first check impacts this has on achieving the Mat 02 credit with the BREEAM Assessor.

- To enable ongoing monitoring of compliance with this credit, the Contractor must provide a full schedule of materials and specifications to the BREEAM Assessor confirming if materials have EPDs. This will allow the BREEAM Assessor to ascertain credit award and advise where there are cases of non-compliance.

- The BREEAM Assessor will enter the details of each EPD into the Mat 01/02 Results Submission Tool, including the material category classification. The tool will verify the EPD points score and credit award.

- The Contractor must provide all EPD certificates to the BREEAM Assessor.

Prerequisite Mat 03 Responsible sourcing of construction products

- The Contractor will ensure all timber and timber-based products used in the construction of building elements are 'Legally harvested and traded timber'.

Legally harvested and traded timber

BREEAM follows the UK government's definition of legally sourced timber, as outlined in the Central Point of Expertise on Timber (CPET) 5th Edition report on the UK Government Timber Procurement Policy.  At the time of writing, the policy requires all timber and wood-based products to be covered by at least one of the following:

- Third party, independent forest certification schemes–Category A (e.g. FSC or PEFC)

- Evidence on a case-by-case basis in line with the Framework for Evaluating Category B evidence–Category B.

- For the avoidance of doubt, the contractor must ensure 100% of the timber and timber-based products are compliant.

Further information on the UK Government's TPP and compliant responsible sourcing certification schemes is available from the CPET website.

Reusable timber formwork itself does not automatically comply. The Contractor will ensure all timber used in the manufacturing of the formwork must be covered by a responsible sourcing certification scheme (RSCS) recognised by BREEAM. See Guidance Note 18 for the BREEAM recognised RSCS.

Credit 1 Mat 03 Responsible sourcing of construction products – Enabling Sustainable Procurement

- The Contractor must adhere to and source materials for the project in accordance with a documented Sustainable Procurement Plan, produced by the Clients Design Team Consultants

- The Sustainable Procurement Plan will set out a clear framework for the responsible sourcing of materials to guide procurement throughout the project and guide all involved in the specification and procurement of construction materials. The plan may be prepared and adopted at an organisational level or be site/project specific, and for the purposes of BREEAM compliance, will cover the following as a minimum:

- Be in place before Concept Design.

- Include sustainability aims, objectives and strategic targets to guide procurement activities. Note: targets do not need to be achieved for the credit to be awarded but justification must be provided for targets that are not achieved.

- Include a requirement for assessing the potential to procure construction products locally. There must be a policy to procure construction products locally where possible.

- Include details of procedures in place to check and verify the effective implementation of the sustainable procurement plan.

- In addition, if the plan is applied to several sites or adopted at an organisational level it must:

Identify the risks and opportunities of procurement against a broad range of social, environmental and economic issues following the process set out in BS ISO 20400:2017

- The Contractor must provide evidence to demonstrate how they have adhere to the plan and points a-e.

Credit 2 Mat 03 Responsible sourcing of construction products – Measuring Responsible Sourcing

- For all non-timber based materials the Contractor must procure materials from Manufacturers with BES6001 certification.

- The Contractor must ensure all materials used in the superstructure and substructure and hard landscaping for the development are procured from manufacturers with BES6001 certification. Additionally, the Contractor must ensure all internal finishes are procured from manufacturers with BES6001 certification.

- Where the Contractor is considering procuring materials from a manufacturer without BES6001 certification, the Contractor must review the BRE’s Guidance Note 18 BREEAM Recognised Responsible Sourcing v3.3 and ensure the manufacturer has an alternative type of responsible sourcing certification.

- The Contractor must provide the following data to the BREEAM Assessor in a materials schedule:

- Material name and specification

- Building element location

- Manufacturer

- Quantity in kg or m3

- Type of responsible sourcing certification (BES6001)

- Certificate reference number

- The Contractor must ensure at least 10% of responsible sourcing points are achieved. This will be confirmed by the BRE’s Mat 03 Calculator Tool once the above data has been entered by the BREEAM Assessor.

Credit 1 Mat 05 Designing for Durability and Robustness

Part 1 Protecting vulnerable parts of the building from damage

- The Contractor will identify, on floor plan drawings, the anticipated internal pedestrian and trolley movements throughout the building.

- The Contractor will ensure protection measures are incorporated into the building's design and construction to reduce damage to the building’s fabric or materials in case of accidental or malicious damage occurring. These measures must provide protection against:

- Negative impacts of high user numbers in relevant areas of the building (e.g. corridors, lifts, stairs, doors etc.).

- Damage from any vehicle or trolley movements within 1m of the internal building fabric in storage, delivery, corridor and kitchen areas.

- External building fabric damage by a vehicle. Protection where parking or manoeuvring areas are within 1 metre of the building façade and where delivery areas or routes are within 2 metres of the façade, i.e. specifying bollards or protection rails.

- Potential malicious damage to building materials and finishes, in public and common areas where appropriate.

- In areas of higher risk, suitable durability and protection measures to vulnerable parts of the building can include:

- Bollards, barriers or raised kerbs to delivery and vehicle drop-off areas

- Robust external wall construction, up to 2m high

- Corridor walls specified to Severe Duty (SD) as per BS 5234-2

- Protection rails to walls of corridors

- Kick plates or impact protection (e.g. trolleys) on doors

- Hard-wearing and easily washable floor finishes in heavily used circulation areas (i.e. main entrance,

- corridors, public areas etc.)

- Door stoppers to prevent door handles damaging walls

- Designing out the risk without the need for additional materials specification to protect vulnerable areas.

Part 2 Protecting exposed parts of the building from material degradation

- The Contractor will ensure key exposed building elements have been designed and specified to limit long and short term degradation due to environmental factors. This can be demonstrated through one of the following:

- The element or product achieving an appropriate quality or durability standard or design guide, refer to Table 9.14 of BREEAM New Construction 2018. If none are available, the Contractor must use BS 7543:2015 as the default appropriate standard

OR

- The Contractor completes a detailed assessment of each building element's resilience when exposed to the applicable material degradation and environmental factors.

- The Contractor must Include convenient access to the roof and façade for cost-effective cleaning, replacement and repair in the building's design.

- The Contractor must ensure the design of the roof and façade to prevent water damage, ingress and detrimental ponding.

Credit 1 Mat 06 Material efficiency

- At the Preparation and Brief and Concept Design stages, the Clients Design Team Consultant set targets and report on opportunities and methods to optimise the use of materials. These must be done for each of the following stages.

- Preparation and Brief

- Concept Design

- Developed Design

- Technical Design

- Where in Contract at Technical Design stage, the Contractor must set targets and report on opportunities and methods to optimise the use of materials, for point d.

- The Clients Design Team Consultants and Contractor where relevant, will ensure all relevant parties involved in design, specification and construction will be consulted in order to gain input into the report and identify all opportunities and measures. Parties will include where relevant:

- The Clients Design Team, and Contractor where relevant, will develop and record the implementation of material efficiency measures during:

- Developed Design

- Technical Design

- The Clients Design Team Consultants and Contractor must report the actual material efficiencies achieved at each of these design stage

- The Contractor will set targets and report on opportunities to optimise the use of materials and record the implementation of material efficiencies during the construction stage of the development.

- The Contractor must report the targets and actual material efficiencies achieved during the construction stage.

Credit 1Wst 01 Construction waste management - Pre-demolition audit

- The Clients Design Team Consultants will ensure a pre-demolition audit of the existing buildings, structures and hard surfaces present on site will be undertaken. This must be used to determine whether refurbishment or reuse is feasible and, in the case of demolition, to maximise the recovery of material for subsequent high grade or value applications. The audit must cover the minimum content listed below, AND:

- Is carried out at Concept Design stage by a competent person prior to demolition works

- Guide the design, consider materials for reuse and set targets for waste management

- Engages all contractors in the process of maximising high grade reuse and recycling opportunities

- The Contractor must make reference to the audit in their site waste management plan and compare actual waste arisings and waste management routes used with those forecast and investigate significant deviations from planned targets.

Pre-demolition audit scope

- The pre-demolition audit must cover:

- Identification and quantification of the key materials where present on the project

- Potential applications and any related issues for the reuse and recycling of the key materials in accordance with the waste hierarchy

- Opportunities for reuse and recycling within the same development

- Identification of local reprocessors or recyclers for recycling of materials

- Identification of overall recycling targets where appropriate

- Identification of reuse targets where appropriate

- Identification of overall landfill diversion rate for all key materials.

Credit 2 Wst 01 Construction waste management – Construction Resource Efficiency

- The Contractor must prepare a BREEAM compliant site waste management plan (SWMP) in accordance with the following:

- The SWMP aims to promote resource efficiency and to prevent illegal waste activities. The SWMP will outline methods of resource efficiency which includes minimising waste at source and ensuring that clients, designers, and principal contractors assess the use, reuse and recycling of materials and products on site and off site. The Contractor’s SWMP must define:

- A target benchmark for resource efficiency, i.e. m³ of waste per 100m² or tonnes of waste per 100m²

- Procedures and commitments to minimise non-hazardous waste in line with the target benchmark

- Procedures to minimise hazardous waste

- A waste-minimisation target and details of waste minimisation actions to be undertaken

- Procedures to estimate, monitor, measures and report on hazardous and non-hazardous site waste and demolition waste, where relevant, arising from work carried out by the principal contractor and all subcontractors. Waste data obtained from licensed external waste contractors needs to be reliable and verifiable, e.g. using data from EA/SEPA/EA Wales/NIEA waste return forms or from a PAS402 compliant company

- Monthly reporting of all construction waste data throughout the project checked against what would be expected based on the stage of the project, invoices, etc., to validate completeness of waste reporting data

- Procedures to sort, reuse and recycle construction waste into defined waste groups, either on site or through a licensed external contractor

- Procedures to review and update the plan

- The name or job title of the individual responsible for implementing the above.

- The Contractor’s SWMP must cover:

- Non-hazardous waste materials (from on-site construction and dedicated off-site manufacture or fabrication), including demolition and excavation waste

- Accurate data records on waste arisings and waste management routes.

- The Contractor will ensure, as a minimum, meets or improves on the following benchmark for non-hazardous construction waste, excluding demolition and excavation waste: ≤11.1 tonnes per 100m2 of GIFA.

Credit 3 Wst 01 Construction waste management – Diversion of Resources from Landfill

- The Contractor must meet the diversion from landfill benchmarks set out below, where applicable, for non-hazardous construction waste and demolition and excavation waste generated.

- The Contractor must sort waste materials into separate key waste groups, either on-site or through a licensed contractor for recovery.

Diversion from landfill benchmarks

- Non-demolition waste – 80% of waste (in tonnage).

- Demolition – 90% of waste (in tonnage)

- Excavation waste – 95% of waste where applicable ( in tonnage)

Credit 1 Wst 03 Operational waste

The Contractor must ensure a dedicated space(s) is provided for the segregation and storage of operational recyclable waste volumes generated by the assessed building/unit, its occupant(s) and activities. This space must be:

- Clearly labelled, to assist with segregation, storage, and collection of the recyclable waste streams;

- Accessible to building occupants or facilities operators for the deposit of materials and collections by waste management contractors;

- Of a capacity appropriate to the building type, size, number of units (if relevant) and predicted volumes of waste that will arise from daily/weekly operational activities and occupancy rates.

Where the Client has confirmed the following waste management items and facilities are required the Contractor must ensure these are present at the point of handover.

- Static waste compactor(s) or baler(s); situated in a service area or dedicated waste management space.

- Vessel(s) for composting suitable organic waste resulting from the building’s daily operation and use; OR adequate space(s) for storing segregated food waste and compostable organic material prior to collection and delivery to an alternative composting facility.

- Where organic waste is to be stored/composted on-site, a water outlet is provided adjacent to or within the facility for cleaning and hygiene purposes.

Credit 1 Wst 05 Adaptation to climate change – Resilience of Structure, Fabric, Building Services and Renewables Installation

- The Clients Design Team Consultant will conduct a climate change adaptation strategy appraisal using:

- A systematic risk assessment to identify the impact of expected extreme weather conditions arising from climate change on the building over its project’s life cycle. The assessment covers the installation of building services and renewable systems, as well as structural and fabric resilience aspects and includes:

- Hazard identification

- Hazard assessment

- Risk estimation

- Risk evaluation

- Risk management

- The Clients Design Team Consultants will develop recommendations or solutions based on the climate change adaptation strategy appraisal, before or during Concept Design, that aim to mitigate the identified impact.

- The Clients Design Team Consultants will provide and update during Technical Design demonstrating how the recommendation or solutions proposed at Concept Design have been implemented where practical and cost effective. Omissions have been justified in writing by the BREEAM Assessor.

- The Contractor must implement all recommendations made in the design team’s systematic risk assessment and provide input where necessary to the technical design stage update.

Credit 1 Wst 06 Design for disassembly and adaptability - Functional Adaptability Recommendations

- The Clients Design Team Consultants will conduct a study to explore the ease of disassembly and the functional adaptation potential of different design scenarios.

- The Clients Design Team Consultants will develop recommendations or solutions based on the study, during or prior to Concept Design, that aim to enable and facilitate disassembly and functional adaptation.

- The Contractor must implement all recommendations made in the study in the finals as built development.

Credit 2 Wst 06 Design for disassembly and adaptability – Implementation

- The Clients Design Team Consultants, and the Contractor where appropriate, will provide an update during Technical Design on:

- How the recommendations or solutions proposed by Concept Design have been implemented where practical and cost effective. Omissions have been justified in writing to the BREEAM Assessor.

- Changes to the recommendations and solutions during the development of the Technical Design.

- The Contractor will implement any further recommendations made in this update to the study.

- The Contractor will produce a building adaptability and disassembly guide to communicate characteristics allowing functional adaptability and disassembly to prospective tenants. The guide can be in the form of an analogue document or an Asset Information Model from the Building Information Model (BIM) created in accordance with PAS 1192 Part 2-2013 and PAS 1192 Part 3-2014. See the new ISO 20887 for information on what the guide could include.

Credit 1 LE 02 Ecological risks and opportunities – Survey and Evaluation

- The Contractor must confirm, and demonstrate with evidence, they have complied with all relevant UK and EU or international legislation relating to the ecology of the site.

- The Clients Design Team Consultants have ensured a Suitably Qualified Ecologist has carried out a survey and evaluation for the site early enough to influence site preparation works, layout and, where necessary, strategic planning decisions. The Ecologists survey and evaluation is detailed within report ‘13331_R01a_Ecological Assessment_SC_HM_161020’.

- The Contractor must confirm they have reviewed this report prior to construction works commencing and must implement all recommendations made on site preparation and mitigation measures for negative impacts resulting from construction.

- The Contractor must liaise with the Ecologist and Clients Design Team Consultants to confirm the agreed ecological outcomes and landscaping for the site.

- The Contractor must confirm these agreed ecological outcomes have followed the ecological  mitigation hierarchy of: avoidance, protection, limitation of negative impacts, on-site compensation and, enhancement.

- The Contractor must ensure a BREEAM Ecology survey and report is undertaken by a suitably qualified ecologist once the planting/ landscaping is complete, to confirm the ecology credits at the post-construction stage of assessment.

Credit 1 LE 03 Managing impacts on ecology – Planning and Measures On-Site

- The Clients Design Team Consultant will demonstrate they have conducted appropriate planning to avoid and manage negative ecological impacts on-site, early enough to influence the Concept Design and Design Brief, as well as site preparation planning (typically Concept Design stage).

- The Contractor must demonstrate they have conducted appropriate planning to avoid and manage negative ecological impacts on-site, and to influence site preparation.

- The Ecologist has set out on-site measures for managing negative ecological impacts during site preparation and construction in report ‘13331_R01a_Ecological Assessment_SC_HM_161020’.

- The Contractor must ensure all recommendations/measures for managing negative impacts during site preparation and during construction are implemented in-practice (e.g. mitigation measures to protect existing ecological features). The Contractor must collate and provide evidence of this to the BREEAM Assessor.

- Planning will be commensurate to the site, current ecological value, and the proposed development, but could include:

- Further planning needs to be carried out for activities during site clearance and construction. This builds on the measures agreed for delivering optimal ecological outcomes in LE 02 Ecological risks and opportunities, and is likely to include plans for the following :

- Determine responsibilities, relationships and management required for implementing measures, including clear ownership of each task

- Allocate roles and responsibilities and identify when these apply

- Allocate resources to deliver these measures (including financial, time, technical and skills)

- Implement procedures for monitoring progress against these plans and collect feedback for continual improvement

- Align with related activities and processes

- Implement effective handover and collaboration where responsibility is transferred and shared, including transition to long term management and maintenance arrangements.

- The following should be considered to determine timescales for implementing on-site measures (where relevant):

- Which roles and responsibilities apply

- Ecological seasonality

- Alignment with existing and planned activities and processes

- Project phasing, including existing planned activities and processes on or near the site, or in the wider local area

- Contract requirements should focus on:

- Reducing and managing potential knock-on impacts of works (e.g. pollution and disturbance)

- Contractual and other handover project milestones, long term management, maintenance and monitoring requirements as well as outline costs

Credit 2 LE 03 Managing impacts on ecology – Managing Negative Impacts

- The Contractor must ensure, and provide evidence to demonstrate, impacts from site preparation and construction works have been managed according to the mitigation hierarchy and the Ecologists’ recommendations. And, ensured as a minimum;

- The loss of ecological value has been minimized,

And where possible,

- No overall loss of ecological value has occurred,

- The Contractor must ensure a BREEAM Ecology survey and report is undertaken by a suitably qualified ecologist once the planting/ landscaping is complete, to confirm the ecology credits at the post-construction stage of assessment.

Prerequisite  LE 04 Ecological change and enhancement – Managing Negative Impact on Ecology

- The Contractor must ensure the agreed ecological outcomes for the site (agreed between the design team and ecologist), are implemented.

- The Contractor must ensure the recommendations on enhancement outlined by the Ecologist in report ‘13331_R01a_Ecological Assessment_SC_HM_161020’ have been implemented. These contain both on-site and off-site measures in the wider campus.

Credit 1 LE 04 Ecological change and enhancement – Change and Enhancement of Ecology

- The Contractor must ensure they implement all recommendations on enhancement made by the Ecologist to ensure the change in ecological value calculated by the Ecologist at design stage is achieved.

- The Contractor must ensure a suitably qualified ecologist calculates the change in ecological value occurring as a result of the project, once landscaping has been implemented. This must be calculated in accordance with the process set out in GN36 – BREEAM Ecology Calculation Methodology – Route 2

- The Contractor must ensure a BREEAM Ecology survey and report is undertaken by a suitably qualified ecologist once the planting/ landscaping is complete, to confirm the ecology credits at the post-construction stage of assessment. The Contractor must ensure data collated by the Ecologist is analysed and where potentially valuable, is provided to the local environmental records centres nearest to, or relevant for, the site.

Credit 1 LE 05 Long term ecological management and maintenance

- The Contractor must ensure, and provide evidence to demonstrate, measures have been implemented to manage and maintain ecology throughout the project and construction. These measures are based on input from the project team as part of the ‘determining ecological outcomes’ for the site, required under LE 02.

- The Contractor must ensure, these measures  monitor and review the effectiveness of the mitigation and enhancement measures in place for LE 03 & LE 04 to ensure they are implemented.

- The Contractor must ensure a section on Ecology and Biodiversity has been included as part of the tenant or building owner information supplied, to inform the owner or occupant of local ecological features, value and biodiversity on or near the site. This should include detailed management and maintenance plans as required by landscape and asset managers as well as relevant parts of the handover information for occupiers written in a format that encourages understanding and supportive behaviours.

- The Contractor must develop a Landscape and Ecology Management Plan, or equivalent, in accordance with BS 42020:2013 Section 11.1 covering at least the first five years after project completion as a minimum and including:

- Actions and responsibilities of relevant individuals prior to handover

- The ecological value and condition of the site at handover and how this is expected to develop and change over time

- Identification of opportunities for ongoing alignment with activities beyond the development project, which support the aims of BREEAM's Strategic Ecology Framework

- Identification and guidance to trigger appropriate remedial actions to address previously unforeseen impacts

- Clearly defined and allocated roles and responsibilities for delivering the plan

- The landscape and management plan or similar will be updated to support maintenance of the ecological value of the site

Credit 1 Pol 01 Impact of refrigerants

- The Contractor must ensure all systems using refrigerants (with electric compressors) comply with the requirements of BS EN378:2008 (parts 2 and 3) and where refrigeration systems containing ammonia are installed, the Institute of Refrigeration Ammonia Refrigeration Systems Code of Practice.

- The Contractor must ensure all systems using refrigerants have Direct Effect Life Cycle CO2 equivalent emissions (DELC CO2e)of ≤ 1000 kgCO2e/kW cooling/heating capacity.

- The Contractor must ensure systems using refrigerants have a permanent automated refrigerant leak detection system installed;

OR

- An inbuilt automated diagnostic procedure for detecting leakage is installed. In all instances a robust and tested refrigerant leak detection system must be installed and must be capable of continuously monitoring for leaks. The system must be capable of automatically isolating and containing the remaining refrigerant(s)charge in response to a leak detection incident.

Credit 1 Pol 02 Local air quality

- The Contractor must ensure emissions from the boilers and all installed combustion plant that provide space heating and domestic hot water do not exceed the following NOx emission level: 24mg/kWh.

Credit 2 and 3 Pol 03 Flood and surface water management – Surface Water Run-Off and Volume

- The Contractor must implement all recommendations made by the flood risk consultant in their report RAL-ONE-R120-X-RP-C-0001 (P01) FRA. The Contractor must ensure the as-built development has been completed in accordance with this report and recommendations on attenuation and limiting surface water run-off are implemented and achieved.

- The Contractor must ensure the as built development complies with the following criteria:

- For brownfield sites, drainage measures are specified so that the peak rate of run-off from the site to the watercourses (natural or municipal) shows a 30% improvement for the developed site compared with the pre-developed site. This should comply at the 1-year and 100-year return period events.

- For Greenfield sites, drainage measures are specified so that the peak rate of run-off from the site to the watercourses (natural or municipal) is no greater for the developed site than it was for the pre-development site. This should comply at the 1-year and 100-year return period events.

- Relevant maintenance agreements for the ownership, long term operation and maintenance of all specified Sustainable Drainage Systems (SuDS) are in place.

- Calculations on peak rate of run-off include an allowance for climate change. This should be made in accordance with current best practice planning guidance .

- Flooding of property will not occur in the event of local drainage system failure (caused either by extreme rainfall or a lack of maintenance); AND

EITHER

- Drainage design measures are specified so that the post-development run-off volume, over the development lifetime, is no greater than it would have been prior to the assessed site’s development. This must be for the 100-year 6-hour event, including an allowance for climate change.

- Any additional predicted volume of run-off for this event is prevented from leaving the site by using infiltration or other SuDS techniques.

OR

- Justification from the appropriate consultant indicating why the above criteria cannot be achieved, i.e. where infiltration or other SuDS techniques are not technically viable options.

- Drainage design measures are specified so that the post-development peak rate of run-off is reduced to the limiting discharge. The limiting discharge is defined as the highest flow rate from the following options:

- The pre-development one-year peak flow rate

- The mean annual flow rate (Qbar)

- 2L/s/ha.

- For the one-year peak flow rate, the one-year return period event criterion applies.

- Relevant maintenance agreements for the ownership, long term operation and maintenance of all specified SuDS are in place.

- For either option, above calculations must include an allowance for climate change; this should be made in accordance with current best practice planning guidance.

Credit 1 Pol 04 Reduction of nighttime light pollution

- The Contractor must ensure the external lighting strategy has been designed in compliance with Table 2 (and its accompanying notes) of the ILP Guidance notes for the reduction of obtrusive light, 2011. This can be demonstrated via completion of the checklists in Annexes B and C of the guidance note by a relevant member of the design team.

- The Contractor must confirm all external lighting (except for safety and security lighting) can be automatically switched off between 23:00 and 07:00.

- The Contractor must state if security lighting is being installed at this development. The Contractor must ensure safety or security lighting is provided and will be used between 23:00 and 07:00, this part of the lighting system complies with the lower levels of lighting recommended during these hours in Table 2 of the ILP’s Guidance notes.

- The Contractor must confirm is if illuminated advertisements will feature at this development. The Contractor must ensure Illuminated advertisements, where specified, will be designed in compliance with ILE Technical Report 5 – The Brightness of Illuminated Advertisements.

Credit 1 Pol 05 Reduction of noise pollution

- A noise impact assessment in compliance with BS 4142:2014 has been commissioned and undertaken by a suitably qualified acoustician (SQA) at request of the Client. The SQA has measured existing background noise levels and determined noise levels for:

- Existing background noise levels:

- at the nearest or most exposed noise-sensitive development to the proposed assessed site

- including existing plant on a building, where the assessed development is an extension to the building

- Noise rating level from the assessed building.

- The noise level from the assessed building, as measured in the locality of the nearest or most exposed noise-sensitive development, must be at least 5dB lower than the background noise throughout the day and night.

- The Contractor must implement recommendations made by the SQA in report ‘RAL Environmental Noise Survey’ and ensure external noise from plant meet the limits set out by the SQA in their conclusion.

- The Contractor must ensure a suitably qualified acoustician is instructed to complete a post-construction acoustic assessment once plant is installed and the development is concluding

- If the noise sources from the assessed building are greater than the levels described above/ greater than levels stipulated by the Acoustician in their report, the Contractor must ensure measures have been installed to attenuate the noise at its source to a level where it will comply.