| FIRE RISK ASSESSMENT WORKS SCHEDULE OF WORKS. Installation of Emergency lights To communal areas Of General needs blocks Sited in Kettering |  |  |  |
| --- | --- | --- | --- |
| Property type – 3 storey communal blocks, housing up to 6no flats per block owned by Kettering Borough Council Scope of works – Build and create new electric meter cupboards in the communal areas and to fire stop service ducting within the flats |  |  |  |
| Item 1.0 1.2 1.3 1.4 1.5 1.6 2.0 2.1 2.2 2.3 2.4 2.6 | Block 1 – 3B Gloucester Close, Kettering Block 5 – 7B Gloucester Close, Kettering Block 9 – 11B Gloucester Close, Kettering Block 13 – 15B Gloucester Close, Kettering Block 1 – 3B Arthurs Way, Kettering Block 2 – 4B Arthurs Way, Kettering Block 5 – 7B Arthurs Way, Kettering Block 9 – 11B Arthurs Way, Kettering Block 13 – 15B Arthurs Way Kettering Block 27 – 29B Thorngate St Kettering Block 57 – 59B Alexandra St Kettering Block 61 – 63B Alexandra St Kettering Block 65 – 67B Alexandra St Kettering Block 70 – 72B Alexandra St Kettering Block 72 – 74B Alexandra St Kettering Block 71 – 73B Albert St Kettering Electric Meter Cupboard Removing existing electric cupboard - Carefully allow to remove the existing timber framed cupboard from around the electric meters and dispose of from site. Aprox size 1.2 m height x 1.4m width x 300mm deep Removing glass partition and door - Remove existing the timber and glass doors & side frames from the ground floors areas complete & dispose of rubbish from site. Aprox size 2.3m x 2.3m Electric cupboard - Construct new block wall sited under the concrete stairs, using 100mm width high density blocks from floor to fit tight to under stairs, bedded on to the existing concrete floor, 15mm min cement mortar courses between blocks and pointing to be clean finished ready for decoration, ensuring all mortar joints are sealed all round to stop smoke penetration, clean and brush off excess mortar to leave ready for decoration. Aprox 8.5m sq per block Wall to be set back 25mm min from the front edge of the concrete stairs, allow to leave 900mm opening to fit new cupboard fire door. Cupboard door - Supply and fit new GRP fire rated solid door and frame to the entrance of the electric’s cupboard, aprox size 2300 x 900. Frame to include a solid fire-retardant top panel, allow for intumescent vent to be fitted to the door or panel. Door to open outwards against the existing main wall, mostly right hand. Note – sizes provided are an aprox measurement they will vary from block to block and will require a site measure from the contractor before manufacturing, allow to fire stop door frame with intumescing sealant inside and outside of frame Door locks - All door locks to be Euro style and suited, allow to supply 110 keys in total. Interior light - Allow to supply and fit 1no Luceco micro sensor light fitting to the inside wall of the under stairs electric cupboard, run all cables in metal conduit, electrical supply to be obtained from the communal supply in the meter cupboard Fire Stopping Description - Each flat contains an open service duct, this rises from the ground floor through to the roof and contains soil, vent and water pipes. The ducting is sited in a cupboard off the kitchen. Size varies between blocks, aprox measurements are 900mm wide x 500mm deep x 2300 height. Aprox 2.3m² Removing existing ply boarding - Allow to remove existing ply boarding covering the service duct 900 x 2300 and the existing timber frame, remove from site and dispose of. Alterations to water stop tap - Allow to turn off water supply and make alterations to the existing water stop tap, supply new 15mm copper pipe to new position aprox 500mm. Reposition and move forwards to sit outside the service duct, to be fixed at low level to the rear wall of the kitchen cupboard area Block off flooring to service duct - Allow to install timber bearers 50 x 50mm across the floor void in the service duct at 150mm centres, 75mm below the floor line to rest insulation on, fill floor void (on 1st & 2nd floors only) with fire retardant Rockwooll insulation material, tightly packed in, making sure this covers all the area including behind the service pipework’s aprox 0.5m² Board over ducting void - Supply and fit new timber frame 50mm x 50mm treated timbers to service duct opening, consisting of x3 uprights and x4 horizontal rails min, opening size 2.3m x 1m, framework to be screwed fixed to walls @ 600mm centres min Allow to supply and fit x 2 layers of 12mm plasterboard to the frame around the cupboard opening, fix to timber frame using Gyproc plasterboard screws, allow to tape over joints and apply 3mm skim coat plaster to finish level with the front line of the service duct. Make sure all edges have been sealed to stop smoke penetration in to the property. Skirting - Also allow to remove section of timber skirting on the ducting wall and replace with new 100mm rounded top timber skirting to whole length of rear wall over new plastered panel aprox 2m length | 16no 16no 16no 16no item 16no 60no 60no 60no 60no 96no | £ p |
|  |  |  | £ |