EAST NORTHANTS COUNCIL

NBS PRELIMINARIES AND

SPECIFIC CONDITIONS OF CONTRACT

TECD050

COUNCIL OFFICES

THRAPSTON

REPLACEMENT LPHW BOILERS AND ASSOCIATED PLANT

BMH June 2017

A10 PROJECT

PARTICULARS

A10 PROJECT PARTICULARS

110	THE PROJECT

•	 Name: EAST NORTHANTS COUNCIL OFFICES, THRAPSTON.

Nature: REPLACEMENT LPHW BOILERS AND ASSOCIATED PLANT.

Location: CEDAR DRIVE, THRAPSTON, NORTHANTS. NN14 4LZ

•   Length of contract: 4 WEEKS

120	EMPLOYER (CLIENT)

•	 Name: COUNCIL OF EAST NRTHAMPTONSHIRE.

•	 Address:  CEDAR DRIVE, THRAPSTON NORTHANTS

•	 Telephone: 01832 742000

130	PRINCIPAL CONTRACTOR

•	 Name: The Contractor whose tender has been accepted on behalf of the employer.

•	 Address: TBC.

•	 Telephone: TBC.

140	ENC CLIENTS REPRESENTATIVE/PROJECT MANAGER

•	 Name: MATHEW LINEHAM, facilities manager.

•	 Address: COUNCIL OFFICES CEDAR DRIVE, THRAPSTON. NN14 4LZ.

150	CONTRACT ADMINISTRATOR (HEREIN REFERRED TO AS 'CA')

•	 Name:  BARRY HICKMOTT

•	 Address 21 FRITHWOOD CRESCENT, KENTS HILL. MILTON KEYNES. MK7 6HQ.

160	CDM CO-ORDINATOR

•	 Name:  NA

•	 Address NA

A11 TENDER AND

CONTRACT DOCUMENTS

A11 TENDER AND CONTRACT DOCUMENTS

110	TENDER DRAWINGS

•	 The tender drawings are:

BOILER PLANT…………No  TECD050/M01					     			SCHEMATTIC…………...No  TECD050/M02

120	CONTRACT DRAWINGS

•	 The Contract Drawings: The same as the tender drawings.

160	PRE-TENDER HEALTH AND SAFETY PLAN

•	 Format: A separate Pre-tender Health and Safety Plan is included with the tender

documents.

A12 THE SITE/ EXISTING

BUILDINGS

A12 THE SITE/ EXISTING BUILDINGS

110	THE SITE

•	 Description: ENC THRAPSTON OFFICES

•	 Drawings: (Information shown is indicative only):

•	 Other information: NA.

200	ACCESS TO THE SITE

•	 Description: Vehicle access is available off CEDAR DRIVE.

•	 Limitations: None.

210	PARKING

•	 Restrictions on parking of the Contractor's and employees' vehicles: 2 x allocated parking 			bays

220	USE OF THE SITE

•	 General: Do not use the site for any purpose other than carrying out the Works.

•	 Limitations: Work confined to boiler house

240	HEALTH AND SAFETY HAZARDS

•	 General: The nature and condition of the site/ building cannot be fully and certainly

ascertained before it is opened up. However the following hazards are or may be

present:

- None.

•	 Information: The accuracy and sufficiency of this information is not guaranteed by

the Employer or the Employer's representative. Ascertain if any additional

information is required to ensure the safety of all persons and the Works.

•	 Site staff: Draw to the attention of all personnel working on the site the nature of

any possible contamination and the need to take appropriate precautionary

measures.

250	SITE VISIT

•	 Before tendering: Ascertain the nature of the site, access thereto and all local

conditions and restrictions likely to affect the execution of the Works.

•	 Arrangements for visit contact Mathew Lineham, Facilities Manager, 01832 742000

A13 DESCRIPTION OF THE

WORK

A13 DESCRIPTION OF THE WORK

120	THE WORKS

•	 Description: The contract comprises:-

The replacement of: The LPHW heating BOILERS including all associated mechanical, electrical and builders work

The appointed services contractor shall be the Principle Contractor and therefore

responsible for All works including Electrical, Intruder, Fire Alarm, Mechanical

and Construction where applicable. There are no other contractors and the appointed Principle

contractor shall be deemed to have included for all works that go to make a

complete, fit for purpose working system.

A20 JCT MINOR WORKS

BUILDING CONTRACT WITH

CONTRACTOR'S DESIGN

A20 JCT MINOR WORKS BUILDING CONTRACT WITH CONTRACTOR'S

DESIGN

JCT MINOR WORKS BUILDING CONTRACT WITH CONTRACTOR'S DESIGN

•	 The Contract: JCT Minor Works Building Contract with Contractor's Design, 2016

Edition.

•	 Requirement: Allow for the obligations, liabilities and services described therein

against the headings following:

THE RECITALS

First - THE WORKS AND THE CONTRACT ADMINISTRATOR

•	 The work comprises: Installation of new replacement Heating Plant.

•	 CA/ Contract Administrator: See clause A10/140.

Second - CONTRACTOR'S DESIGNED PORTION

•	 The Works include the design and construction of:

- Fixings, Builders work in connection and coordination of services installation with

existing structure. .

THE ARTICLES

3 - CA/ CONTRACT ADMINISTRATOR

•	 CA/ Contract Administrator: See clause A10/140.

4 and 5 – CDM CO-ORDINATOR/ PRINCIPAL CONTRACTOR

•	 CDM Co-ordinator: A10/150.

•	 Principal Contractor: See clause A10/130.

6 - ADJUDICATION

•	 Amendments: -.

CONTRACT PARTICULARS

Fifth Recital - CDM REGULATIONS

•	 All the CDM regulations apply.

Article 7 - ARBITRATION

•	 Article 7 and Schedule 1 Will apply.

A20 JCT MINOR WORKS

BUILDING CONTRACT WITH

CONTRACTOR'S DESIGN

Clause 2.3 - COMMENCEMENT AND COMPLETION

•	 Date for Commencement of the Works: TBA.

•	 Date for Completion: TBA

Clause 2.9 - LIQUIDATED DAMAGES

•	 At the rate of: £350.00 per Week.

Clause 2.11 - RECTIFICATION PERIOD

•	 Period: 3 Months.

155	CLAUSE 2.11 SITE CLEARANCE ON COMPLETION

•	 On termination or completion of the contract, the contractor shall within 7 days,

clear away and remove from the premises and sites owned by the employer all

surplus material and rubbish of every kind and leave the whole premises and sites

clean and in a condition satisfactory to the contract administrator and the

contractor shall carry out the works of repair or maintenance as may reasonably

be requested by the contract administrator.

•	 If the contractor shall fail to do any such work as required under the contract,

the employer shall be entitled to carry out such work by its own workmen or by

other contractor's and shall be entitled to recover from the contract to the cost

thereof or may deduct the same from monies due to the contractor

157	CLAUSE 3.1 ASSIGNMENT

Delete Clause 3.1 and insert new clause 3.2 as follows:

Assignment

The contractor shall not without written consent of the contract administrator under

the contract (which consent shall not be unreasonably withheld to the prejudice of

the contractor) sub let any portion of their works.

Such consents as may be given by virtue of this clause shall not relieve the

contractor from any liability or obligation under the contract and the contractor shall

be responsible for the Acts, defaults and neglects of any sub contractor and such

such subcontractors agents, servants or workmen as fully as if they were acts,

defaults or neglects of the contractor or the contractors agent's, servants or

workmen.

Clause 4.3 - PERCENTAGE OF THE TOTAL VALUE OF THE WORK ETC.

•	 Percentage: 95 per cent.

A20 JCT MINOR WORKS

BUILDING CONTRACT WITH

CONTRACTOR'S DESIGN

Clause 4.5 - PERCENTAGE OF THE TOTAL AMOUNT TO BE PAID TO THE

CONTRACTOR

•	 Percentage: 95 per cent.

Clause 4.8.1 - SUPPLY OF DOCUMENTATION

•	 Period: 3 months.

Clause 4.11 and Schedule 2 - CONTRIBUTION, LEVY AND TAX CHANGES

•	 Clause 4.11 will be deleted.

195	CLAUSE 4.9 RECOVERY OF OVERPAYMENT

Recovery of overpayment

•	 Not withstanding anything herein contained or implied to the contrary, where under

the contract or any other contract, whether entered into before or after this contract

any sum of money is due or payable by the contractor to the employer, such sum

or any part thereto may be deducted by the employer from any sum due or which

thereafter may become due to the employer to the contractor under this contract or

any other contract or contracts.

CLAUSE 5.3.2 - CONTRACTOR'S INSURANCE - INJURY TO PERSONS OR

PROPERTY

•	 Insurance cover (for any one occurrence or series of occurrences arising out of

one event): Not less than £1,000,000.

Clause 5.4 INSURANCE OF WORKS

•	 Delete Clauses 5.4 A and 5.4 B and Insert Clause 5.4 B as follows:

Insurance of works-Existing Structures_

The works (and the existing structures together with the contents thereof owned by

him and for which he is responsible) and all unfixed materials and goods intended

for delivered to, placed on or adjacent to the works and intended therefore (except

temporary buildings, plant, tools and equipment owned or hired by the contractor

or any sub contractors) shall be at the sole risk of the employer as regards loss or

damage by fire, lightning, explosion, storm, tempest, flood, bursting or overflowing

of water tanks, apparatus or pipes, earthquake, aircraft and other aerial devices or

articles dropped there from riot and civil commotion and the Employer shall

maintain adequate insurance against that risk.

If any loss or damage as referred to in this clause occurs then the CA-

supervising officer shall issue instructions for the reinstatement and making good

such loss or damage in accordance with clause 3.4 hereof.

A20 JCT MINOR WORKS

BUILDING CONTRACT WITH

CONTRACTOR'S DESIGN

CLAUSES 5.4A.1 AND 5.4B.1 - PERCENTAGE TO COVER PROFESSIONAL

FEES

•	 Addition: 15 per cent.

CLAUSE 6.6 CORRUPTION

•	 Delete Clause 6.6 and insert new clause 6.6 as follows:

The Council shall be entitled to cancel any Contract or determine the employment

of the Contractor and to recover from the Contract the amount of any loss resulting

from such cancellation or determination, if the Contractor shall have offered or

given or agreed to give to any person any gift or consideration of any kind as an

inducement or reward for doing or forbearing to do or forborne to have done any

contract with the Council, or for showing or forbearing to show favour or disfavour

to any person in relation to the Contract or any other contract with the Council, or if

the like acts shall have been done by any person employed by the Contractor or

acting on behalf of the Contractor (whether with or without the knowledge of the

contractor) or in relation to any contract with the Council the Contractor or any

persons employed by him or acting on his behalf shall have committed any offence

under the Prevention of Corruption Acts 1889 to 1916 or shall have given any fee

or reward to receipt of which is an offence under sub section (2) of section 117 of

the Local Government Act 1972.

Clause 7.2 - ADJUDICATION

•	 The Adjudicator is: Royal Institution of Chartered Surveyors.

•	 Nominator of Adjudicator: President or a Vice president or Chairman or Vice

Chairman of the: Royal Institution of Chartered Surveyors.

Schedule 1 and Schedule 2 - BASE DATE

•	 Base date: 1September 2006.

Schedule 1 paragraph 2.1 - ARBITRATION

•	 Appointer of Arbitrator (and of any replacement): President or a Vice president of

the: The Royal Institution of Chartered Surveyors.

THE CONDITIONS

SECTION 1: DEFINITIONS AND INTERPRETATION

SECTION 1: DEFINITIONS AND INTERPRETATION SEE EAST NORTHANTS

COUNCIL CONDITIONS OF CONTRACT

SECTION 2: CARRYING OUT THE WORKS

SECTION 3: CONTROL OF THE WORKS

SECTION 4: PAYMENT

SECTION 5: INJURY, DAMAGE AND INSURANCE

A20 JCT MINOR WORKS

BUILDING CONTRACT WITH

CONTRACTOR'S DESIGN

SECTION 6: TERMINATION

SECTION 7: SETTLEMENT OF DISPUTES

EXECUTION

•	 The Contract: Will be executed as a deed.

CONTRACT GUARANTEE BOND…Not Required.

•	 Contract Guarantee Bond: East Northants Council Form of Bond.

A30 TENDERING/

SUBLETTING/ SUPPLY

A30 TENDERING/ SUBLETTING/ SUPPLY

MAIN CONTRACT TENDERING

110	SCOPE

•	 General: These conditions are supplementary to those stated in the Invitation to

Tender and on the form of tender.

145	TENDERING PROCEDURE

•	 General: In accordance with JCT Practice Note 6 (Series 2) 'Main Contract

Tendering'.

•	 Errors: Alternative 1 is to apply.

160	EXCLUSIONS

•	 Inability to tender: Immediately inform if any parts of the work as defined in the

tender documents cannot be tendered.

•	 Relevant parts of the work: Define those parts, stating reasons for the inability to

tender.

170	ACCEPTANCE OF TENDER

•	 The Employer and Employer's representatives:

-	Offer no guarantee that any tender will be recommended for acceptance or be

accepted.

Will not be responsible for any cost incurred in the preparation of any tender.

190	PERIOD OF VALIDITY

•	 Period: After submission or lodgement, keep tender open for consideration (unless

previously withdrawn) for not less than 2 MONTHS.

•	 Date for possession/ commencement: See section A20.

PRICING/ SUBMISSION OF DOCUMENTS

210	PRELIMINARIES IN THE SPECIFICATION

•	 The Preliminaries/ General conditions sections (A10-A56 inclusive) must not be

relied on as complying with SMM7.

250	PRICED DOCUMENTS

•	 Alterations: Do not alter or qualify the priced documents without written consent.

Tenders containing unauthorised alterations or qualifications may be rejected.

•	 Measurements: Where not stated, ascertain from the drawings.

•	 Deemed included: Costs relating to items, which are not priced, will be deemed to

have been included elsewhere in the tender.

•	 Submit: With tender.

310	TENDER

•	 General: Tenders must include for all work shown or described in the tender

documents as a whole or clearly apparent as being necessary for the complete

and proper execution of the Works.

A30 TENDERING/

SUBLETTING/ SUPPLY

440	SCHEDULE OF RATES

•	 Schedule of rates (unpriced): Included with the tender documents. The Contractor

may insert additional items. All items must be fully priced.

•	 Fully priced copy: Submit within one week of request.

500	TENDER STAGE METHOD STATEMENTS

•	 Method statements: Prepare, describing how and when the following is to be

carried out:

- Complete Installation

•	 Statements: Submit within one week of request.

510	ALTERNATIVE METHOD TENDERS

•	 General: In addition to and at the same time as tendering for the Works as defined

in the tender documents, alternative methods of construction/ installation may be

submitted for consideration. Alternatives, which would involve significant changes

to other work, may not be considered.

•	 Alternative tenders: Such alternatives will be deemed to be alternative tenders and

each must include a complete and precise statement of the effects on cost and

programme.

•	 Safety method statement: Carry out a health and safety risk assessment for each

alternative and where appropriate provide a safety method statement suitable for

incorporation in the Health and Safety Plan.

•	 Full technical data: Submit for each alternative together with details of any

consequential amendments to the design and/ or construction of other parts of the

Works.

•	 Submit: Within one week of request.

530	SUBSTITUTE PRODUCTS

•	 Details: If products of different manufacture to those specified are proposed,

submit details with the tender giving reasons for each proposed substitution.

Substitutions, which have not been notified at tender stage, may not be

considered.

•	 Compliance: Substitutions accepted will be subject to the verification requirements

of clause A31/200.

550	HEALTH AND SAFETY INFORMATION

•	 Content: Describe the organisation and resources to safeguard the health and

safety of operatives, including those of subcontractors, and of any person whom

the Works may affect.

•	 Include:

-	A copy of the contractor's health and safety policy document, including risk

assessment procedures.

-	Accident and sickness records for the past five years.

-	Records of previous Health and Safety Executive enforcement action.

-	Records of training and training policy.

-	The number and type of staff responsible for health and safety on this project

with details of their qualifications and duties.

•	 Submit: Within one week of request.

A30 TENDERING/

SUBLETTING/ SUPPLY

570	OUTLINE CONSTRUCTION PHASE HEALTH AND SAFETY PLAN

•	 Content: Submit the following information within one week of request:

-	Method statements on how risks from hazards identified in the pre-tender health

and safety plan and other hazards identified by the contractor will be addressed.

-	Details of the management structure and responsibilities.

-	Arrangements for issuing health and safety directions.

-	Procedures for informing other contractors and employees of health and safety

hazards.

-	Selection procedures for ensuring competency of other contractors, the self-

employed and designers.

-	Procedures for communications between the project team, other contractors and

site operatives.

-	Arrangements for cooperation and coordination between contractors.

-	Procedures for carrying out risk assessment and for managing and controlling

the risk.

-	Emergency procedures including those for fire prevention and escape.

-	Arrangements for ensuring that all accidents, illness and dangerous occurrences

are recorded.

-	Arrangements for welfare facilities.

-	Procedures for ensuring that all persons on site have received relevant health

and safety information and training.

-	Arrangements for consulting with and taking the views of people on site.

-	Arrangements for preparing site rules and drawing them to the attention of those

affected and ensuring their compliance.

-	Monitoring procedures to ensure compliance with site rules, selection and

management procedures, health and safety standards and statutory

requirements.

Review procedures to obtain feedback.

SUBLETTING/ SUPPLY

630	DOMESTIC SUBCONTRACTS

•	 General: Comply with the Construction Industry Board 'Code of Practice for the

selection of subcontractors'.

A31 PROVISION, CONTENT

AND USE OF DOCUMENTS

A31 PROVISION, CONTENT AND USE OF DOCUMENTS

DEFINITIONS AND INTERPRETATIONS

110	DEFINITIONS

•	 Meaning: Terms, derived terms and synonyms used in the preliminaries/ general

conditions and specification are as stated therein or in the appropriate British

Standard or British Standard glossary.

120	COMMUNICATION

•	 Definition: Includes advice, inform, submit, give notice, instruct, agree, confirm,

seek or obtain information, consent or instructions, or make arrangements.

•	 Format: In writing to the person named in clause A10/140 unless specified

otherwise.

•	 Response: Do not proceed until response has been received.

130	PRODUCTS

•	 Definition: Materials, both manufactured and naturally occurring, and goods,

including components, equipment and accessories, intended for the permanent

incorporation in the Works.

•	 Includes: Goods, plant, materials, site materials and things for incorporation into

the Works.

135	SITE EQUIPMENT

•	 Definition: All appliances or things of whatsoever nature required in or about the

construction for completion of the Works but not materials or other things intended

to form or forming part of the Permanent Works.

•	 Includes: Construction appliances, vehicles, consumables, tools, temporary works,

scaffolding, cabins and other site facilities.

A31 PROVISION, CONTENT

AND USE OF DOCUMENTS

160	TERMS USED IN SPECIFICATION

•	 Remove: Disconnect, dismantle as necessary and take out the designated

products or work and associated accessories, fastenings, supports, linings and

bedding materials. Dispose of unwanted materials. Excludes taking out and

disposing of associated pipework, wiring, ductwork or other services.

•	 Fix: Unload, handle, store, place and fasten in position including all labours and

use of site equipment.

•	 Supply and fix: Includes all labour and site equipment for unloading, handling,

storing and execution. All products to be supplied and fixed unless stated

otherwise.

•	 Keep for reuse: Do not damage designated products or work. Clean off bedding

and jointing materials. Stack neatly, adequately protect and store until required by

the Employer or for use in the Works as instructed.

•	 Make good: Execute local remedial work to designated work. Make secure, sound

and neat. Excludes redecoration and/ or replacement.

•	 Replace: Supply and fix new products matching those removed. Execute work to

match original new state of that removed.

•	 Repair: Execute remedial work to designated products. Make secure, sound and

neat. Excludes redecoration and/ or replacement.

•	 Refix: Fix removed products.

•	 Ease: Adjust moving parts of designated products or work to achieve free

movement and good fit in open and closed positions.

•	 Match existing: Provide products and work of the same appearance and features

as the original, excluding ageing and weathering. Make joints between existing

and new work as inconspicuous as possible.

•	 System: Equipment, accessories, controls, supports and ancillary items, including

installation, necessary for that section of the work to function.

170	MANUFACTURER AND PRODUCT REFERENCE

•	 Definition: When used in this combination:

-	Manufacturer: The firm under whose name the particular product is marketed.

-	Product reference: The proprietary brand name and/ or reference by which the

particular product is identified.

•	 Currency: References are to the particular product as specified in the

manufacture's technical literature current on the date of the invitation to tender.

A31 PROVISION, CONTENT

AND USE OF DOCUMENTS

200	SUBSTITUTION OF PRODUCTS

•	 Products: If an alternative product to that specified is proposed, obtain approval

before ordering the product.

•	 Reasons: Submit reasons for the proposed substitution.

•	 Documentation: Submit relevant information, including:

-	manufacturer and product reference;

-	cost;

-	availability;

-	relevant standards;

-	performance;

-	function;

-	compatibility of accessories;

-	proposed revisions to drawings and specification;

-	compatibility with adjacent work;

-	appearance;

-	copy of warranty/ guarantee.

•	 Alterations to adjacent work: If needed, advise scope, nature and cost.

•	 Manufacturers' guarantees: If substitution is accepted, submit before ordering

products.

210	CROSS REFERENCES

•	 Accuracy: Check remainder of the annotation or item description against the

terminology used in the section or clause referred to.

•	 Related terminology: Where a numerical cross-reference is not given the relevant

sections and clauses of the specification will apply.

•	 Relevant clauses: Clauses in the referred to specification section dealing with

general matters, ancillary products and execution also apply.

•	 Discrepancy or ambiguity: Before proceeding, obtain clarification or instructions.

220	REFERENCED DOCUMENTS

•	 Conflicts: Specification prevails over referenced documents.

230	EQUIVALENT PRODUCTS

•	 Inadvertent omission: Wherever products are specified by proprietary name the

phrase 'or equivalent' is to be deemed included.

250	CURRENCY OF DOCUMENTS

•	 Currency: References to published documents are to the editions, including

amendments and revisions, current on the date of the Invitation to tender.

260	SIZES

•	 General dimensions: Products are specified by their co-ordinating sizes.

•	 Timber: Cross section dimensions shown on drawings are:

-	Target sizes as defined in BS EN 336 for structural softwood and hardwood

sections.

-	Finished sizes for non-structural softwood or hardwood sawn and further

processed sections.

A31 PROVISION, CONTENT

AND USE OF DOCUMENTS

DOCUMENTS PROVIDED ON BEHALF OF THE EMPLOYER

410	ADDITIONAL COPIES OF DRAWINGS/ DOCUMENTS

•	 Additional copies: Issued free of charge.

440	DIMENSIONS

•	 Scaled dimensions: Do not rely on.

450	MEASURED QUANTITIES

•	 Ordering products and constructing the Works: The accuracy and sufficiency of the

measured quantities is not guaranteed.

•	 Precedence: The specification and drawings shall override the measured

quantities.

460	THE SPECIFICATION

•	 Coordination: All sections must be read in conjunction with Main Contract

Preliminaries/ General conditions.

DOCUMENTS PROVIDED BY CONTRACTOR/ SUBCONTRACTORS/

SUPPLIERS

510	CONTRACTOR'S DESIGN DOCUMENTS

•	 Master programme: Make reasonable allowance for completing design/production

information, submission (including to the Planning Supervisor), comment,

inspection, amendment, resubmission and reinspection.

•	 Design/ production information: Submit two copies, one can be returned with

comments. Ensure that any necessary amendments are made without delay.

•	 Contractor's changes to Employer's Requirements: Support request for

substitution or change with all relevant information.

•	 Employer's amendments to Employer's Requirements: If considered to involve a

change, which has not already been acknowledged as a change, notify without

delay (maximum period 7 days), and do not proceed until instructed. Claims for

extra cost, if made after it has been carried out, may not be allowed.

•	 Final version of design/production information: Submit within 2 weeks of request.

600	CONTRACTOR'S DESIGN INFORMATION

•	 Contractor's designed work: Include: Builders work in connection and coordination.

•	 Format: 2 copies of Paper and electronic.

620	AS BUILT DRAWINGS AND INFORMATION

•	 General: Provide the following Drawings/ information:

- Installation drawings.

•	 Submit: At least two weeks before date for completion.

630	TECHNICAL LITERATURE

•	 Information: Keep on site for reference by all supervisory personnel:

-	Manufacturers' current literature relating to all products to be used in the Works.

-	Relevant British, EN or ISO Standards.

A31 PROVISION, CONTENT

AND USE OF DOCUMENTS

640	MAINTENANCE INSTRUCTION AND GUARANTEES

•	 Components and equipment: Obtain or retain copies, register with manufacturer

and hand over on or before completion of the Works.

•	 Emergency call out services: Provide subcontractors telephone numbers for use

after completion.

A32 MANAGEMENT OF THE

WORKS

A32 MANAGEMENT OF THE WORKS

GENERALLY

110	SUPERVISION

•	 General: Accept responsibility for coordination, supervision and administration of

the Works, including subcontracts.

•	 Coordination: Arrange and monitor a programme with each subcontractor,

supplier, local authority and statutory undertaker, and obtain and supply

information as necessary for coordination of the work.

120	INSURANCE

•	 Documentary evidence: Before starting work on site submit details, and/ or policies

and receipts for the insurances required by the Conditions of Contract.

130	INSURANCE CLAIMS

•	 Notice: If any event occurs which may give rise to any claim or proceeding in

respect of loss or damage to the Works or injury or damage to persons or property

arising out of the Works, immediately give notice to the Employer, the person

named in clause A10/140 and the Insurers.

•	 Failure to notify: Indemnify the Employer against any loss, which may be caused

by failure to give such notice.

140	CLIMATIC CONDITIONS

•	 Information: Record accurately and retain:

-	Daily maximum and minimum air temperatures (including overnight).

-	Delays due to adverse weather, including description of the weather, types of

work affected and number of hours lost.

150	OWNERSHIP

•	 Alteration/ clearance work: Materials arising become the property of the Contractor

except where otherwise stated. Remove from site as work proceeds.

PROGRAMME/ PROGRESS

210	PROGRAMME

•	 Master programme: Immediately when requested and before starting work on site

submit in an approved form a master programme for the Works, which must

include details of:

-	Planning and mobilisation by the Contractor

-	Subcontractor's work.

-	Running in, adjustment, commissioning and testing of all engineering services

and installations.

-	Work resulting from instructions issued in regard to the expenditure of

provisional sums.

-	Work by others concurrent with the Contract.

•	 Submit with one of request.

A32 MANAGEMENT OF THE

WORKS

245	START OF WORK ON SITE

•	 Notice: Before the proposed date for start of work on site give minimum notice

of one week.

250	MONITORING

•	 Progress: Record on a copy of the programme kept on site.

•	 Avoiding delays: If any circumstances arise which may affect the progress of the

Works submit proposals or take other action as appropriate to minimize any delay

and to recover any lost time.

260	SITE MEETINGS

•	 General: Site meetings will be held to review progress and other matters arising

from administration of the Contract.

•	 Frequency: Every two weeks.

•	 Location: Site.

•	 Accommodation: Ensure availability at the time of such meetings.

•	 Attendees: Attend meetings and inform subcontractors and suppliers when their

presence is required.

•	 Chairperson (who will also take and distribute minutes): Contract Administrator.

280	PHOTOGRAPHS

•	 Number of locations: Through out the premises.

•	 Frequency of intervals: Weekly.

•	 Image format: JPEG.

•	 Number of images from each location: 1.

•	 Other requirements: na

290	NOTICE OF COMPLETION

•	 Requirement: Give notice of the anticipated dates of completion of the whole or

parts of the Works.

•	 Associated works: Ensure necessary access, services and facilities are complete.

•	 Period of notice (minimum): Two weeks.

310	EXTENSIONS OF TIME

•	 Notice: When a notice of the cause of any delay or likely delay in the progress of

the works is given under the contract, written notice must also be given of all other

causes which apply concurrently.

•	 Details: As soon as possible submit:

-	Relevant particulars of the expected effects, if appropriate, related to the

concurrent causes.

-	An estimate of the extent, if any, of the expected delay in the completion of the

Works beyond the date for completion.

-	All other relevant information required.

CONTROL OF COST

420	REMOVAL/ REPLACEMENT OF EXISTING WORK

•	 Extent and location: Agree before commencement.

•	 Execution: Carry out in ways that minimize the extent of work.

A32 MANAGEMENT OF THE

WORKS

430	PROPOSED INSTRUCTIONS

•	 Estimates: If a proposed instruction requests an estimate of cost, submit without

delay and in any case within seven days.

440	MEASUREMENT

•	 Covered work: Give notice before covering work required to be measured.

450	DAYWORK VOUCHERS

•	 Before commencing work: Give reasonable notice to person countersigning

daywork vouchers.

•	 Content: Before delivery each voucher must be:

-	Referenced to the instruction under which the work is authorised.

-	Signed by the Contractor's person in charge as evidence that the operatives'

names, the time daily spent by each and the equipment and products employed

are correct.

•	 Submit: By the end of the week in which the work has been executed.

460	INTERIM VALUATIONS

•	 Applications: Include details of amounts due under the Contract together with all

necessary supporting information.

•	 Submission: At least seven days before established dates.

470	PRODUCTS NOT INCORPORATED INTO THE WORKS

•	 Ownership: At the time of each valuation, supply details of those products not

incorporated into the Works which are subject to any reservation of title

inconsistent with passing of property as required by the Conditions of Contract,

together with their respective values.

•	 Evidence: When requested, provide evidence of freedom of reservation of title.

A33 QUALITY STANDARDS/

CONTROL

A33 QUALITY STANDARDS/ CONTROL

STANDARDS OF PRODUCTS AND EXECUTIONS

110	INCOMPLETE DOCUMENTATION

•	 General: Where and to the extent that products or work are not fully documented,

they are to be:

-	Of a kind and standard appropriate to the nature and character of that part of the

Works where they will be used.

-	Suitable for the purposes stated or reasonably to be inferred from the project

documents.

Contract documents: Omissions or errors in description and/ or quantity shall not

vitiate the Contract nor release the Contractor from any obligations or liabilities

under the Contract.

120	WORKMANSHIP SKILLS

•	 Operatives: Appropriately skilled and experienced for the type and quality of work.

•	 Registration: With Construction Skills Certification Scheme.

•	 Evidence: Operatives must produce evidence of skills/ qualifications when

requested.

130	QUALITY OF PRODUCTS

•	 Generally: New. (Proposals for recycled products may be considered).

•	 Supply of each product: From the same source or manufacturer.

•	 Whole quantity of each product required to complete the Works: Consistent kind,

size, quality and overall appearance.

•	 Tolerances: Where critical, measure a sufficient quantity to determine compliance.

•	 Deterioration: Prevent. Order in suitable quantities to a programme and use in

appropriate sequence.

135	QUALITY OF EXECUTION

•	 Generally: Fix, apply, install or lay products securely, accurately, plumb, neatly and

in alignment.

•	 Colour batching: Do not use different colour batches where they can be seen

together.

•	 Dimensions: Check on-site dimensions.

•	 Finished work: Without defects, e.g. not damaged, disfigured, dirty, faulty, or out of

tolerance.

•	 Location and fixing of products: Adjust joints open to view so they are even and

regular.

A33 QUALITY STANDARDS/

CONTROL

140	COMPLIANCE

•	 Compliance with proprietary specifications: Retain on site evidence that the

proprietary product specified has been supplied.

•	 Compliance with performance specifications: Submit evidence of compliance,

including test reports indicating:

-	Properties tested.

-	Pass/ fail criteria.

-	Test methods and procedures.

-	Test results.

-	Identity of testing agency.

-	Test dates and times.

-	Identities of witnesses.

-	Analysis of results.

150	INSPECTIONS

•	 Products and executions: Inspection or any other action must not be taken as

approval unless confirmed in writing referring to:

-	Date of inspection.

-	Part of the work inspected.

-	Respects or characteristics which are approved.

-	Extent and purpose of the approval.

Any associated conditions.

160	RELATED WORK

•	 Details: Provide all trades with necessary details of related types of work. Before

starting each new type or section of work ensure previous related work is:

-	Appropriately complete.

-	In accordance with the project documents.

-	To a suitable standard.

-	In a suitable condition to receive the new work.

•	 Preparatory work: Ensure all necessary preparatory work has been carried out.

170	MANUFACTURER'S RECOMMENDATIONS/ INSTRUCTIONS

•	 General: Comply with manufacturer's printed recommendations and instructions

current on the date of the Invitation to tender.

•	 Changes to recommendations or instructions: Submit details.

•	 Ancillary products and accessories: Use those supplied or recommended by main

product manufacturer.

•	 Agrément certified products: Comply with limitations, recommendations and

requirements of relevant valid certificates.

180	WATER FOR THE WORKS

•	 Mains supply: Clean and uncontaminated.

•	 Other: Do not use until:

-	Evidence of suitability is provided.

-	Tested to BS EN 1008 if instructed.

A33 QUALITY STANDARDS/

CONTROL

210	SAMPLES

•	 Products or executions: Comply with all other specification requirements and in

respect of the stated or implied characteristics either:

-	To an express approval.

To match a sample expressly approved as a standard for the purpose.

220	APPROVAL OF PRODUCTS

•	 Submissions, samples, inspections and tests: Undertake or arrange to suit the

Works programme.

•	 Approval: Relates to a sample of the product and not to the product as used in the

Works. Do not confirm orders or use the product until approval of the sample has

been obtained.

•	 Complying sample: Retain in good, clean condition on site. Remove when no

longer required.

230	APPROVAL OF EXECUTION

•	 Submissions, samples, inspections and tests: Undertake or arrange to suit the

Works programme.

•	 Approval: Relates to the stated characteristics of the sample. (If approval of the

finished work as a whole is required this is specified separately). Do not conceal,

or proceed with affected work until compliance with requirements is confirmed.

•	 Complying sample: Retain in good, clean condition on site. Remove when no

longer required.

ACCURACY/ SETTING OUT GENERALLY

320	SETTING OUT

•	 General: Submit details of methods and equipment to be used in setting out the

Works.

•	 Levels and dimensions: Check and record the results on a copy of drawings. Notify

discrepancies and obtain instructions before proceeding.

•	 Inform: When complete and before commencing construction.

330	APPEARANCE AND FIT

•	 Tolerances and dimensions: If likely to be critical to execution or difficult to

achieve, as early as possible either:

-	Submit proposals; or

-	Arrange for inspection of appearance of relevant aspects of partially finished

work.

•	 General tolerances (maximum): To BS 5606, tables 1 and 2.

360	RECORD DRAWINGS

•	 Site setting out drawing: Record details of all grid lines, setting-out stations,

benchmarks and profiles. Retain on site throughout the contract and hand over on

completion.

A33 QUALITY STANDARDS/

CONTROL

SERVICES GENERALLY

410	SERVICES REGULATIONS

•	 New or existing services: Comply with the Byelaws or Regulations of the relevant

Statutory Authority.

420	WATER REGULATIONS/ BYELAWS NOTIFICATION

•	 Requirements: Notify Water Undertaker of any work carried out to or which affects

new or existing services and submit any required plans, diagrams and details.

•	 Consent: Allow adequate time to receive Undertaker's consent before starting

work. Inform immediately if consent is withheld or is granted subject to significant

conditions.

440	GAS INSTALLATION CERTIFICATE

•	 Before the completion date stated in the contract: Submit a certificate stating:

-	The address of the premises.

-	A brief description of the new installation and/ or work carried out to an existing

installation.

-	Any special recommendations or instructions for the safe use and operation of

gas appliances and flues.

-	The Contractor's name and address.

-	A statement that the installation complies with the Gas Safety (Installation and

Use) Regulations.

-	The name and signature of the Gas Safe registered individual responsible for

checking compliance.

The date on which the installation was checked.

445	SERVICE RUNS

•	 General: Provide adequate space and support for services, including unobstructed

routes and fixings.

•	 Ducts, chases and holes: Form during construction rather than cut.

•	 Coordination with other works: Submit details of locations, types/ methods of fixing

of services to fabric and identification of runs and fittings.

450	MECHANICAL AND ELECTRICAL SERVICES

•	 Final tests and commissioning: Carry out so that services are in full working order

at completion of the Works.

SUPERVISION/ INSPECTION/ DEFECTIVE WORK

525	ACCESS

•	 Extent: Provide at all reasonable times access to the Works and to other places of

the Contractor or subcontractors where work is being prepared for the Contract.

•	 Designate: Contract Administrator.

A33 QUALITY STANDARDS/

CONTROL

540	DEFECTS IN EXISTING WORK

•	 Undocumented defects: When discovered, immediately give notice. Do not

proceed with affected related work until response has been received.

•	 Documented remedial work: Do not execute work which may:

-	Hinder access to defective products or work; or

Be rendered abortive by remedial work.

560	TESTS AND INSPECTIONS

•	 Timing: Agree and record dates and times of tests and inspections to enable all

affected parties to be represented.

•	 Confirmation: One working day prior to each such test or inspection. If sample or

test is not ready, agree a new date and time.

•	 Records: Submit a copy of test certificates and retain copies on site.

580	CONTINUITY OF THERMAL INSULATION

•	 Method: Infra-red thermography inspection to BRE Report 176.

•	 Compliance: Submit inspection report.

610	DEFECTIVE PRODUCTS/ EXECUTIONS

•	 Proposals: Immediately any work or product is known, or appears, to be not in

accordance with the Contract, submit proposals for opening up, inspection, testing,

making good, adjustment of the Contract Sum, or removal and re-execution.

•	 Acceptability: Such proposals may be unacceptable and contrary instructions may

be issued.

WORK AT OR AFTER COMPLETION

710	WORK BEFORE COMPLETION

•	 General: Make good all damage consequent upon the Works.

Temporary markings, coverings and protective wrappings: Remove unless

otherwise instructed.

•	 Cleaning: Clean the Works thoroughly inside and out, including all accessible

ducts and voids. Remove all splashes, deposits, efflorescence, rubbish and

surplus materials.

•	 Cleaning materials and methods: As recommended by manufacturers of products

being cleaned, and must not damage or disfigure other materials or construction.

•	 COSHH dated data sheets: Obtain for all materials used for cleaning and ensure

they are used only as recommended by their manufacturers.

•	 Minor faults: Touch up in newly painted work, carefully matching colour and

brushing out edges. Repaint badly marked areas back to suitable breaks or

junctions.

•	 Moving parts of new work: Adjust, ease and lubricate as necessary to ensure easy

and efficient operation, including doors, windows, drawers, ironmongery,

appliances, valves and controls.

A33 QUALITY STANDARDS/

CONTROL

720	SECURITY AT COMPLETION

•	 General: Leave the Works secure with, where appropriate, all accesses closed

and locked.

•	 Keys: Account for and adequately label all keys and hand over to Employer with

itemised schedule, retaining duplicate schedule signed by Employer as a receipt.

730	MAKING GOOD DEFECTS

•	 Remedial work: Arrange access with Contract Administrator.

•	 Rectification: Give reasonable notice for access to the various parts of the Works.

•	 Completion: Notify when remedial works have been completed.

A34 SECURITY/ SAFETY/

PROTECTION

A34 SECURITY/ SAFETY/ PROTECTION

SECURITY, HEALTH AND SAFETY

110	PRETENDER HEALTH AND SAFETY PLAN

•	 Location: Integral with the project Preliminaries, including but not restricted to the

following sections:

-	Description of project: Sections A10 and A11.

-	Client's consideration and management requirements: Sections A12, A13 and

A36.

-	Environmental restrictions and on-site risks: Section A12, A35 and A34.

-	Significant design and construction hazards: Section A34.

-	The Health and Safety File: Section A37.

120	EXECUTION HAZARDS

•	 Common hazards: Not listed. Control by good management and site practice.

•	 Significant hazards: The design of the project includes the following:

-	Hazard: Vehicle movement adjacent to boiler house.

-	Specification reference: -.

-	Drawing reference: -.

130	PRODUCT HAZARDS

•	 Hazardous substances: Site personnel levels must not exceed occupational

exposure standards and maximum exposure limits stated in the current version of

HSE document EH40: Occupational Exposure Limits.

•	 Common hazards: Not listed. Control by good management and site practice.

•	 Significant hazards: Specified construction materials include the following:

-	Hazard: -.

-	Material: -.

-	Specification reference: -.

140	CONSTRUCTION PHASE HEALTH AND SAFETY PLAN

•	 Submission: Present to the Employer/ Client not less than two weeks before

commencement on site.

•	 Confirmation: Do not start construction work until the Employer has confirmed in

writing that the Construction Phase Health and Safety Plan includes the

procedures and arrangements required by CDM Regulation 15(4).

•	 Content: Develop the plan from and draw on the Outline Construction Phase

Health and Safety Plan, clause A30/570, and the Pre-tender Health and Safety

Plan.

A34 SECURITY/ SAFETY/

PROTECTION

150	SECURITY

•	 Protection: Safeguard the site, the Works, products, materials, and any existing

buildings affected by the Works from damage and theft.

•	 Access: Take all reasonable precautions to prevent unauthorized access to the

site, the Works and adjoining property.

•	 Special requirements: Ensure alarms are enabled at the end of each day.

170	OCCUPIED PREMISES

•	 Extent: Existing buildings will be occupied and/ or used during the Contract as

follows: Authorised personnel only.

•	 Works: Carry out without undue inconvenience and nuisance and without danger

to occupants and users.

•	 Overtime: If compliance with this clause requires certain operations to be carried

out during overtime, and such overtime is not required for any other reason, the

extra cost will be paid to the Contractor, provided that such overtime is authorized

in advance.

180	PASSES

•	 Controlled areas: Passes will be required for access to Fitters and sub contractors.

•	 Authorized persons: Submit a list of the names of all persons requiring passes

together with any other related information reasonably required.

•	 Return of passes: When requested or on completion of the work to which the pass

relates.

200	MOBILE TELEPHONES

•	 Use: Not permitted in the following areas:

- All areas.

210	EMPLOYER'S REPRESENTATIVES SITE VISITS

•	 Safety: Submit details in advance, to the Employer or the person identified in

clause A10/140, of safety provisions and procedures (including those relating to

materials, which may be deleterious), which will require their compliance when

visiting the site.

•	 Protective clothing and/ or equipment: Provide and maintain on site for the

Employer and the person stated in clause A10/140 and other visitors to the site.

A34 SECURITY/ SAFETY/

PROTECTION

PROTECT AGAINST THE FOLLOWING

330	NOISE CONTROL

•	 Standard: Comply generally with the recommendations of BS 5228-1, clause 9.3 to

minimize noise levels during the execution of the Works.

•	 Noise levels from the Works: Maximum level: 50 dB (A) when measured from rooms.

•	 Equipment: Fit compressors, percussion tools and vehicles with effective silencers

of a type recommended by manufacturers of the compressors, tools or vehicles.

•	 Restrictions: Do not use:

Pneumatic drills and other noisy appliances without consent during the hours of 	   9.00am to 3.00pm.

Radios or other audio equipment or permit employees to use in ways or at times

that may cause nuisance.

340	POLLUTION

•	 Prevention: Protect the site, the Works and the general environment including

streams and waterways against pollution.

•	 Contamination: If pollution occurs inform immediately, including to the appropriate

Authorities and provide relevant information.

360	NUISANCE

•	 Duty: Prevent nuisance from smoke, dust, rubbish, vermin and other causes.

•	 Surface water: Prevent hazardous build-up on site, in excavations and to

surrounding areas and roads.

370	ASBESTOS CONTAINING MATERIALS

•	 Duty: Report immediately any suspected materials discovered during execution of

the Works.

-	Do not disturb.

Agree methods for safe removal or encapsulation.

380	FIRE PREVENTION

•	 Duty: Prevent personal injury or death, and damage to the Works or other property

from fire.

•	 Standard: Comply with Joint Code of Practice 'Fire Prevention on Construction

Sites', published by the Construction Confederation and The Fire Protection

Association (The 'Joint Fire Code').

390	SMOKING ON SITE

•	 Smoking on site: Not permitted.

400	BURNING ON SITE

•	 Burning on site: Not permitted.

A34 SECURITY/ SAFETY/

PROTECTION

410	MOISTURE

•	 Wetness or dampness: Prevent, where this may cause damage to the Works.

•	 Drying out: Control humidity and the application of heat to prevent:

-	Blistering and failure of adhesion.

-	Damage due to trapped moisture.

Excessive movement.

420	INFECTED TIMBER

•	 Removal: Where instructed to remove timber affected by fungal/ insect attack from

the building, minimize the risk of infecting other parts of the building.

430	WASTE

•	 Includes: Rubbish, debris, spoil, containers and surplus material.

•	 Minimize: Keep the site and Works clean and tidy.

•	 Remove: Frequently and dispose off site in a safe and competent manner:

-	Non-hazardous material: In a manner approved by the Waste Regulation

Authority.

-	Hazardous material: As directed by the Waste Regulation Authority and in

accordance with relevant regulations.

•	 Voids and cavities in the construction: Remove rubbish, dirt and residues before

closing in.

•	 Waste transfer documentation: Retain on site.

440	ELECTROMAGNETIC INTERFERENCE

•	 N/A

A34 SECURITY/ SAFETY/

PROTECTION

PROTECT THE FOLLOWING

510	EXISTING SERVICES

•	 Confirmation: Notify all service authorities, statutory undertakers and/ or adjacent

owners of proposed works not less than one week before commencing site

operations.

•	 Identification: Before starting work, check and mark positions of mains/ services.

Where positions are not shown on drawings obtain relevant details from service

authorities, statutory undertakers or other owners.

•	 Work adjacent to services:

-	Comply with service authority's/ statutory undertaker's recommendations.

-	Adequately protect, and prevent damage to services: Do not interfere with their

operation without consent of service authorities/ statutory undertakers or other

owners.

•	 Identifying services:

-	Below ground: Use signboards, giving type and depth;

-	Overhead: Use headroom markers.

•	 Damage to services: If any results from execution of the Works:

-	Immediately give notice and notify appropriate service authority/ statutory

undertaker.

-	Make arrangements for the work to be made good without delay to the

satisfaction of service authority/ statutory undertaker or other owner as

appropriate.

-	Any measures taken to deal with an emergency will not affect the extent of the

Contractor's liability.

•	 Marker tapes or protective covers: Replace, if disturbed during site operations, to

service authorities/ statutory undertaker’s recommendations.

520	ROADS AND FOOTPATHS

•	 Duty: Maintain roads and footpaths within and adjacent to the site and keep clear

of mud and debris.

•	 Damage caused by site traffic or otherwise consequent upon the Works: Make

good to the satisfaction of the Employer, Local Authority or other owner.

570	EXISTING WORK

•	 Protection: Prevent damage to existing property undergoing alteration or

extension.

•	 Removal: Minimum amount necessary.

•	 Replacement work: To match existing.

580	BUILDING INTERIORS

•	 Protection: Prevent exposure to weather during course of alteration work.

610	ESPECIALLY VALUABLE/ VULNERABLE ITEMS

•	 Protection: Ensure provision and maintenance of special protective measures to

prevent damage to the following:

- Computers.

•	 Method statement: Submit within one week of request describing special

protection to be provided.

A34 SECURITY/ SAFETY/

PROTECTION

630	EXISTING STRUCTURES

•	 Duty: Check proposed methods of work for effects on adjacent structures inside

and outside the site boundary.

•	 Supports: During execution of the Works:

-	Provide and maintain all incidental shoring, strutting, needling and other

supports as may be necessary to preserve stability of existing structures on the

site or adjoining, that may be endangered or affected by the Works.

-	Do not remove until new work is strong enough to support existing structure.

-	Prevent overstressing of completed work when removing supports.

•	 Adjacent structures: Monitor and immediately report excessive movement.

•	 Standard: Comply with BS 5975.

A35 SPECIFIC LIMITATIONS

ON METHOD/  SEQUENCE/

TIMING

A35 SPECIFIC LIMITATIONS ON METHOD/  SEQUENCE/  TIMING

130	METHOD/ SEQUENCE OF WORK

•	 Specific Limitations: Include the following in the programme:

All work within Council offices plant room is to comply with item 170, unless approved by the Mathew Lineham, Facilities Manager 01832 742000.

170	WORKING HOURS

•	 Specific limitations: Mon – Fri 8am – 5pm, Weekends by agreement.

A36 FACILITIES/

TEMPORARY WORK/

SERVICES

A36 FACILITIES/ TEMPORARY WORK/ SERVICES

GENERALLY

ACCOMMODATION

- TEMPORARY ACCOMMODATION/STORAGE

•	 Facilities: Sanitary accommodation will be provided for the duration of the Contract

as follows: Use approved Council office facilities. Details to be provided later.

TEMPORARY WORKS

320	TEMPORARY WORKS

•	 Employer's Specific Requirements: None

340	NAME BOARDS/ ADVERTISEMENTS

•	 Name boards/ advertisements: Not permitted.

SERVICES AND FACILITIES

410	LIGHTING

•	 Finishing work and inspection: Provide temporary lighting, the intensity and

direction of which closely resembles that delivered by the permanent installation.

420	LIGHTING AND POWER

•	 Supply: Electricity from the Employer's mains may be used for the Works as

follows:

-	Metering: Free of charge.

-	Point of supply: Local.

-	Available capacity: hand tools only.

-	Frequency: 50 Hz.

-	Phase: Single.

-	Current: Alternating.

•	 Continuity: The Employer will not be responsible for the consequences of failure or

restriction in supply.

A36 FACILITIES/

TEMPORARY WORK/

SERVICES

430	WATER

•	 Supply: The Employer's mains may be used for the Works as follows:

-	Metering: Free of charge.

-	Source: Mains.

-	Location of supply point: Boiler room.

-	Conditions/ Restrictions: None.

•	 Continuity: The Employer will not be responsible for the consequences of failure or

restriction in supply.

440	TELEPHONES

•	 Direct communication: As soon as practicable after the Date of Possession provide

the Contractor's person in charge with a mobile telephone.

A37 OPERATION/

MAINTENANCE OF THE

FINISHED BUILDING

A37 OPERATION/ MAINTENANCE OF THE FINISHED BUILDING

GENERALLY

110	THE BUILDING MANUAL

•	 Purpose: The Building Manual (incorporating the Health and Safety File) is to be a

comprehensive information source and guide for the Employer and end users

providing a complete understanding of the building and its systems to enable

efficient and safe operation and maintenance.

•	 Compilation:

-	Prepare all information for Contractor designed or performance specified work

including as-built drawings.

-	Obtain or prepare all other information to be included in the Manual.

•	 Reviewing the Manual: Submit a complete draft. Amend in the light of any

comments and resubmit. Do not proceed with production of the final copies until

authorized.

•	 Final copies of the Manual:

-	Number of copies: 3.

-	Latest date for submission: One week before the date for completion stated in

the contract.

•	 As-built drawings:

-	Number of copies: 3.

Medium: CD Rom and paper.

120	THE HEALTH AND SAFETY FILE

•	 Purpose: To provide information about the structure or materials used, which might

affect the health or safety of anyone if construction works, (including cleaning,

maintenance, alterations, refurbishment and demolition) are carried out.

•	 Contractor designed and performance specified work: Obtain or prepare details of

construction methods and materials, general maintenance instructions and as-built

drawings.

•	 Other information: Obtain or prepare details of utilities and services, materials

hazards, access requirements/restrictions and maintenance and decommissioning

instructions.

•	 Number of copies: Submit 2 copies to CA.

•	 Latest date for submission: one weeks before the date for completion stated in the

contract.

A37 OPERATION/

MAINTENANCE OF THE

FINISHED BUILDING

155	CONTENT OF THE BUILDING MANUAL

•	 General: Details of the property, the parties, fire safety strategy, operational

requirements and constraints of a general nature.

•	 Building fabric: Design criteria, maintenance details, product details, and

environmental and trafficking conditions.

•	 Building services: Description and operation of systems, diagrammatic drawings,

record drawings, identification of services, product details, equipment settings,

maintenance schedules, consumable items, spares and emergency procedures.

•	 Documentation: Guarantees, warranties, maintenance agreements, test

certificates and reports.

160	PRESENTATION OF BUILDING MANUAL

•	 Format: A4 size, plastics covered, loose leaf, four ring binders with hard covers,

each indexed, divided and appropriately cover titled.

•	 Selected drawings needed to illustrate or locate items mentioned in the Manual:

Where larger than A4, to be folded and accommodated in the binders so that they

may be unfolded without being detached from the rings.

•	 As-built drawings: The main sets may form annexes to the Manual.

A54 PROVISIONAL WORK/

ITEMS

A54 PROVISIONAL WORK/ ITEMS

210	PROVISIONAL SUMS FOR UNDEFINED WORK

•	 Item: NA

•	 Description of work:

•	 Provisional Sums:

•	 Allow for general attendance.

- CONTINGENCIES

Item: Unforeseen works

•	 Provisional sum: Include: £5000.00

NBS TECHNICAL SPECIFICATION

&

MECHANICAL APPENDICES

Table of Contents

Title

A	Preliminaries/ General conditions

A1	Standard clauses

B	Scope of Works

B1	Scope of Works

C	Demolition/ Alteration/ Renovation

C20	Demolition

P	Building fabric sundries

P1	Builders work

P12	Fire stopping systems

P31	Holes/ Chases/ Covers/ Supports for Services

P32	Services painting systems

S	Piped supply systems

S10	Hot and cold water supply systems

S32	Natural gas supply systems

T	Mechanical heating, cooling and refrigeration

T10	Heating systems

T20	Gas and oil fired boilers

T30	Heat emitters

U	Ventilation and air conditioning systems

U60	Local air conditioning systems

V	Electrical

V30	Low voltage distribution systems

V50	General lighting systems

V59	Luminaires and lamps

V81	Earthing and bonding systems

W	CONTROL AND WIRING STANDARDS

W6	Controls

Y	General engineering services

Y10	Pipelines

Y11	Pipeline ancillaries

Y12	Mechanical cleaning and chemical treatment

Y20	Pumps

Y30	Mechanical thermal insulation

Y31	Vibration isolating mountings

Y32	Mechanical plant and equipment identification

Y40	Central controls and building management systems

Y50	Mechanical testing and commissioning

Y60	Conduit & trunking

Y63	Cable supports

Y65	Electrical accessories

A

Preliminaries/ General conditions

Standard clauses A1

A1

Standard clauses

Standard clauses A1

A1 Standard clauses

10	GENERAL STANDARDS

GENERAL TERMS

30	EXTENT OF WORKS

The works covered by this specification and the accompanying schedules and

drawings include for the execution of all works, together with the supply and fixing

of all materials necessary for the completion of the mechanical installation within

the above development. The complete mechanical installation as specified must

be installed, commissioned and maintained in accordance with the current editions

of Engineering codes of Practice and British standards. The Contractor will be

deemed to have visited the site and satisfied himself as to local conditions,

accessibility, nature and layout of the site and all other matters which might affect

his tender in any way.  The Contractor shall be responsible for all site

measurements and preparation of the schedules of materials necessary for the

purpose of proper execution of the works.  No claims on the grounds of insufficient

knowledge will be entertained. The Contractor is advised that, although every

effort has been made to give installation heights and positions of accessories in

the specification, drawings and schedules, small variations may be required.

Therefore they shall, before installation work commences, agree with the CA

the final positions required and will have been deemed to have made due

allowance in their tender sum. The Works shall be carried out in accordance with

the requirements of the Main Contractor's programme in co-operation with other

trades and the Contractor shall ensure that an adequate supply of skilled labour

and materials are available on site whenever required by the Main Contractor. The

Contractor must ensure safety to all persons on the premises at all times.  Tools,

ladders, fitting and materials etc., liable to cause injury, must be stored away,

unless in use, and likewise must not be left in such a manner as to cause injury

whilst in use.

40	SUPERVISION

The Contractor shall at all times during the progress of the works be required to

employ on the site a competent foreman, to be responsible for the proper

supervision and direction of the works.  Such foreman shall be invested with the

authority to receive verbal or written instructions from the Contractor, which may

from time to time be issued by the CA.  The foreman will be nominated by

the Contractor at the commencement of the works and shall not be withdrawn from

employment on the works without the prior written approval of the CA.

Standard clauses A1

45	PLANT

The Contractor shall provide all tools, tackle, special scaffolding, haulage, labour

and apparatus necessary for the delivery, off loading, distribution and handling into

position of the plant on site.

50	VARIATIONS TO THE WORKS

No variation shall vitiate the Contract. No variation to the contract shall be carried

out without a written instruction from the Contractor, based upon instructions from

the CA.  The Contractor shall submit with his tender a schedule of rates upon

which the tender is based, which may be used for the pricing of variations where

necessary. The rates submitted shall be deemed to include the cost of all

materials, labour allowances, and a percentage for profit and overheads. Where it

is mutually agreed between the Contractor and the CA that the schedule of

rates are not relevant to the particular item of variation works under consideration,

then such work may be priced on a daywork basis

60	SCHEDULE OF RATES

Within fourteen days of request by the CA and prior to the order being

placed, the Contractor shall furnish a Billed Schedule of Rates for the complete

contract, broken down into sections as indicated in the Summary of Tender and

totalling the same.  In the event of non-submission of a Schedule of Rates, rates

will be assessed by the CA, whose decision will be final.

- DRAWINGS

- The drawings listed shall be read in conjunction with this specification and

schedules. The mechanical drawings generally indicate the arrangement of the

installation required, are for guidance in tendering and for use on the site when the

work is put in hand.  They may not necessarily cover in every detail the whole of

the work involved. Any point shown on the drawing but not included on the

schedules and, conversely, any point included in the schedules but not shown on

the drawing shall be included for within the Contractor's tender sum.

80	BOILER PLANT……………No  ENC011/M01

SCHEMATTIC…………….No  ENC011/M02

Standard clauses A1

ALLOCATION OF DESIGN RESPONSIBILITY

Not Used, however the contractor shall have design responsibility for all supports, allowance for expansion and execution of all works.

90	COORDINATION

The Mechanical Services Contractor will co-ordinate services with the main

contractor and sub contractors.

100	MAUFACTURERS DRAWINGS AND LITERATURE

For all items of equipment the following procedure shall apply:

Confirm each item with the CA

Obtain manufacturer's drawings and catalogues

Crosscheck all dimensions, connection sizes and, where necessary, relate items

of equipment to each other.

Produce installation drawings and submit for comment.

Order equipment and verify delivery periods.

Notify any difficulties arising from above.

Install, test and commission.

The CA will accept no claims if the foregoing is not strictly adhered to.

110	SPECIFIED EQUIPMENT

Any products that have been specified and are referred to by Quotation numbers

are to be included in the Tender. (It is possible that, post-tender, consideration will

be given to alternative equipment for cost or technical advantages). The

information given is intended to assist the Contractor in the preparation of his

Tender. However, it is emphasised that the references are given only as an

indication of the Council's technical requirements. The Contractor should verify

prices and deliveries as they may differ from those indicated to the Council.

Specific conditions and terms is a matter between the Contractor and the supplier

and as such should be taken into account when tendering. It must be clearly

understood that it is the responsibility of the tenderer to ensure that the quotation

fully complies with the requirements of the schedules and that all items are

included.

120	WORKING DRAWINGS

Contractor shall produce manufacturing detail drawings and submit to the CA for comment

The contractor shall allow 5 working days for the CA comments to be returned.

Standard clauses A1

COMMISSIONING

140	PRE COMMISSIONING CLEANING CHECKS

Tubes and all items of equipment shall be delivered stored and maintained in

storage with their open ends effectively plugged, capped or sealed. Tubes shall be

stored upon a properly constructed pipe rack. All fittings, valves and sundry items

shall be stored in clean bins or bagged and stowed in suitable racks. All such

items shall be maintained under weatherproofed cover to be supplied by the

Contractor until they are ready for incorporation in the works. Particular care shall

be taken to ensure that electrical equipment and components are kept clean and

dry. Before installations are handed over or subjected to the inspection and tests

required in this specification the following pre-commissioning procedure should be

adopted.

Clearance of 'snags'

Systems cleaning

Pipe work flushing/scavenging

Check that stems are 'commissionable'

•	Clearance of Snags:

Static systems must be snagged and all items cleared before proceeding further.

•	Systems Cleaning:

Ensure that all systems are thoroughly cleaned of all deleterious materials.

•	Pipe work Flushing/Scavenging:

The Contractors proposals for flushing out/scavenging must be notified to the

CA at least 7 days before commencement of the operation. The CA or

his representative must witness systems flushing/scavenging. After removal or

isolation of terminal units, filters, pumps meters and other items susceptible to

damage by the cleaning operation, each system shall be: Water Circuits Back

flushed with a high-pressure hose for a minimum period of 15 minutes; the flushing

velocity must not fall below 1 m/s. Continue flushing until all traces of sediment

have been removed. Following a dynamic flush to pumped systems, using the

circulating pumps, creating 'high' pressure in each section by isolating all but one

sub-circuit in rotation so that each is subjected to the full pump duty. Gas Circuits

Gas lines shall be thoroughly scavenged by use of compressed air.

The systems shall be thoroughly flushed employing a specialist contractor for this 	purpose An 	independent tank and pump system shall be employed which shall run 	continuously until the specialist contractor declares the existing systems to be clean. 	No chemicals shall be used. The tenderers shall notify the ENC of the proposed 	cleaning/flushing subcontractor.

•	Ready for Commissioning

Ensure that systems are ready for commissioning. Check prime movers free to

rotate; correct direction of rotation and flow. Filter media in position (Note: One set

to be used for commissioning etc., a New set to be provided and installed at

handover). All items lubricated in accordance with manufacturers

recommendations. Open ductwork and plant inspection doors to ensure systems

clear of debris and that dampers function correctly and are open. Open valves,

check that motorised valves installed correctly. Test control panels to prove that

fuses actually defuse stated circuits; neutral continuity; power cable tightness;

correct fuse ratings; Electrical supplies available at motorised valves and equipment.

. Commissioning

The contractor shall allow for the re-commissioning of all equipment employed by the boiler plant on completion.

Standard clauses A1

150	INSPECTION TESTS ON COMPLETION

•	Programme for Testing & Commissioning

Works to be completed to a pre-arranged programme properly integrated into the

overall programme of site activities in a systematic and progressive fashion such

that at the time of handover all testing, setting to work, commissioning and

demonstrating of the works to the user has been completed.

•	Appointment of Commissioning Engineer

Contractor is to appoint an approved Engineer from his own staff or an

independent commissioning company, who shall be fully conversant with the

operation of the works and competent to supervise the whole of these procedures

which shall be carried out by persons fully trained in the operation of specialist

installations and equipment.

•	Pressure Tests

Boiler plant, tanks, cylinders, pumps etc., specified to comply with BS shall be

subject to tests at works as are provided for in the BS. Where there is no BS, such

plant shall be subjected to a hydraulic test of 2 times the maximum working

pressure or of 1.4 bar (20 lb/in2) whichever is the greater, for a period of 30

minutes. Test certificates for works tests required by BS shall be submitted in

duplicate to the CA. On completion of the pre-commissioning cleaning of

each heating installation or domestic hot water supply installation, the systems

shall be recharged with clean water and then subjected to a hydraulic test of 2

times the working pressure for a period of not less than 30 minutes. Items of

equipment e.g. safety valves set to operate at or below this test pressure shall be

isolated or removed prior to applying this test. On completion of the pre-

commissioning cleaning of each cold-water installation, the system shall be

recharged with clean water and then tested as follows. Storage cisterns and

distributing pipe work shall be absolutely watertight under working conditions of

pressure with all draw-off taps closed. Accessible water mains and service pipe

work shall be subjected to a hydraulic test pressure of 90 m or 2 times the

maximum working pressure of the pipe work installed, whichever is the greater.

This pressure shall be maintained without measurable loss for at least 60 minutes.

Inaccessible water mains and service pipe work shall be subjected to a hydraulic

test pressure of 90 m or 2 times the maximum working pressure of the pipe work

installed, whichever is the greater. This pressure shall be maintained without

measurable loss for at least 60 minutes. On larger installations the tests shall be

carried out in the presence of and to the requirements of the local Water Authority.

On completion of each gas installation an air pressure test shall be carried out.

Service pipe work shall be tested to twice the maximum working pressure or to a

pressure of 50 mb (20 in wg) whichever is the greater. Installation pipe work shall

be tested to a pressure of 30 mb (12 in wg). For pipes up to and including 50mm

size the test shall be applied for three minutes. No fall in pressure shall be

registered in the readings during the last two minutes of the test. For larger pipes

the tests shall be carried out to the requirements of the local Gas Authority. Any

component of equipment liable to be damaged by the application of these tests

shall first be isolated. A normal working test under design conditions shall then be

Standard clauses A1

carried out for a period of not less than six hours. Installation or sections thereof

which will be embedded in the structure or concealed in permanently sealed ducts,

trenches, roof spaces etc., shall in addition to the above specified tests be

individually tested as they are laid and before being embedded or concealed.

All pressure tests specified above shall be carried out before the application of

thermal insulation, but where this would prejudice the completion of the installation

of the section concerned shall be individually tested before the application of the

insulation. All tests shall be witnessed and test certificates provided accordingly.

•	Combustion Tests

The Contractor shall include for and arrange for a combustion efficiency test to be

carried out on each boiler by the boiler manufacturer. The tests shall demonstrate

to the CA in whose presence the tests shall be carried out, that the

combustion efficiency of each boiler is not less than that guaranteed by the boiler

manufacturer. The combustion efficiency test shall be based on flue gas losses

taken at the flue gas exit from each boiler and shall be carried out when the boilers

and flues are at normal working temperatures. In the event of the results of the

tests not being acceptable to the CA, the boiler manufacturer at the

Contractor's expense shall make the necessary adjustment to the boiler plant until

an acceptable result is obtained. The results of the final test shall be recorded on a

boiler combustion efficiency test sheet, signed copies of which shall be submitted

to the CA in duplicate. The test sheet shall provide the following information:

-

Gas Fired Boilers

1  Ambient air temperature in boiler room

2  Flue gas temperature at smoke outlet from boiler (s)

3  CO2 content of flue gasses at smoke outlet from boiler (s) before

Draught diverter is fitted

4  Input gas flow rate and pressure related to low and high fire settings where

appropriate

5  Draught in mm water at boiler front and at smoke outlet (not applicable to

atmospheric boilers).

•	Boiler Log Book

NOT USED

•	Cleaning Systems

NOT USED

Standard clauses A1

•	Chemical cleaning pipe work Treatment

NOT USED

The existing distribution systems shall be cleaned/flushed but only with clean water. This shall 	be carried out by a specialist contractor employing a special tank and dedicated pump sets. 	The name of this sub-contractor along with all other sub-contractors  shall be provided by the 	principle contractor at the pre contract meeting.

•	Test Information

The Contractor is to accurately record the following test and inspection

information:

1 Plant, section and installation under test

2 Manufacturers reference number where applicable

3 Date, time, duration of test (and weather conditions if appropriate)

4 Test results with itemised readings; if the first inspection or test fails, repeat the

procedure within a reasonable time, adhering to the time cycles and

other requirements as specified for the first test.

160	COMMISSIONING

Follow procedures in accordance with CIBSE relevant codes. Each installation

shall be fully static and dynamically commissioned. For the purpose of this

specification, commissioning shall include the correct adjustment and setting of all

plant and equipment, valves, sensors, actuators, air regulating dampers and other

mechanisms, as required to achieve the design performance specified.

The contractor shall allow for the re-commissioning of all equipment employed by the boiler plant on completion.

Standard clauses A1

OPERATING INSTRUCTIONS

180	PLANT OPERATING INSTRUCTION FOR USERS

Immediately prior to practical completion of the works or part of the works, the

Contractor shall carry out the following procedure:

•	 Instruct the East Northants Council staff in the safe operation and maintenance by

running, maintaining and supervising the installation for three days under

normal working conditions.

•	 Apply to the CA for names of the trainees before preparing the arrangements

for the instruction period.

•	 Provide a draft set of record drawings and maintenance manuals at the

commencement of the instruction period. The tenderer shall allow for such labour

in the tender, which shall be related to the complexity of the works. Upon

completion of the familiarisation and instruction process the Contractor shall obtain

a signed acknowledgement from the prospective plant operator that he/she is

satisfied with the instruction received and fully understands the operation of the

installations.

Standard clauses A1

190	OPERATING AND MAINTENANCE MANUALS AND RECORD DRAWINGS

The Contractor shall provide a Mechanical Services Operating & Maintenance

Manual to be incorporated in the Building Manual, submitted via the Main Contract.

A complete draft of this manual must be submitted not less than two weeks before

the date for the submission of the final copies of the Manual. Amend the draft

manual in the light of any comments and re-submit to the CA. Do not

proceed with the production of final copies until authorised to do so by the

CA. Final copies (four copies) of the manual shall be provided to the

CA not less than four weeks before practical completion. This handbook shall

also be duplicated in its entirety including manufacturers literature in electronic

PDF format on a CD ROM that also includes the electronic AutoCAD LT record

drawings in DWG format. The Contractor shall also provide a more basic operating

manual for use by the building operator (e.g.) caretakers or similar, that will deal

with day-to-day operation in layman's terms covering only those aspects they

would normally be concerned with. The description should deal with all the

foreseen circumstances which the building user may be presented with, for

example Summer use, Winter use, use outside normal working hours, partial use

of the building, building closures for holidays in summer or winter, water/gas

leakages or emergency shut downs. The Mechanical Services handbook shall

incorporate the following and shall be in accordance with BS4884 and BS4899 and

BSRIA Technical Note TN 1/84_Guidelines for building services operating and

maintenance manuals_ 1984: -

Section 1 shall comprise an introduction to the building systems installed and an

outline of its intended function. This section shall include all abbreviations, Health

& Safety at Work Act and all warning notices.

Section 2 shall comprise a full description of each respective installation, modes of

operation and operation of any control system associated with any system.

Section 3 shall comprise the complete technical data on all items of plant or

electrical equipment e.g. manufacturer's name and address, types, sizes of

mechanical or electrical equipment, serial numbers, order numbers, performance

and duty details, standards of quality i.e. British Standards ISO, ANSI, etc.,

Section 4 shall describe in detail, the operation procedures necessary for starting-

up, running and shutting down mechanical or electrical installations and their

respective control as necessary.

Section 5 shall describe the maintenance operations on a daily, weekly, monthly

and annual basis for all mechanical and electrical installations and equipment. This

section shall be in accordance with the applicable British or ISO Standards, and

manufacturer's advice and recommendations.

Section 6 shall be a copy of the Health & Safety File, in accordance with the

Construction and Design Management Regulations 1994, describing all safety

procedures for undertaking any aspect of operation or maintenance of any part of

any system, whether mechanical or electrical. This section shall also include

emergency procedures and emergency call out procedures, both for in and out of

hours working.

Standard clauses A1

Section 7 shall comprise the recommended actions on mechanical or electrical

systems malfunction, to assist both the user and Maintenance Engineer in the

event of a fault developing in a system by indicating the nature of the fault and the

recommended action. This section shall also include a faultfinding schedule for

each system.

Section 8 shall comprise a list of recommended spares for all mechanical and

electrical installations and lubricants for any mechanical plant. The preparation of

this section shall be carried out by obtaining the manufacturer's recommendations

and also incorporating the Client's requirements regarding spares.

Section 9 shall comprise a schedule of the record drawings, together with reduced

copies to A4 size. The drawings shall be filed in numerical order, with a drawing

schedule preceding the drawings themselves.

Section 10 shall comprise all Test Certificates and Commissioning Reports.

Section 11 shall comprise a list of manufacturers, including addresses and

telephone numbers and equipment supplied. The manufacturer's list shall be

compiled in alphabetical order. The manufacturer's literature shall also be included

in this section, and shall be arranged in alphabetical order to suit. In combined

Mechanical and Electrical O & M Manuals, the Mechanical Section shall be

separate from the Electrical Section and both sections shall follow the order

detailed above.

Other requirements: -

Gas Requirements The Contractor shall provide gas supply line diagrams as

required under Gas Safety Regulations, for both plant room mounting and copies

within operating manual.

Record Drawings

Record drawings shall be supplied as part of the Mechanical Services Handbook

and all notes regarding the issuing of the Handbook apply to the drawings also.

The drawings shall be of the total sub-contract incorporating all deviations and

variations from the original tender drawings. The final approved drawings shall be

supplied on A1 size heavyweight paper, folder to A4 and shall not be less than the

original tender issue. The drawings have been drawn on CAD (AutoCAD 2004).

Copies of these drawings can be supplied electronically on a CD-R as requested

by the Contractor. The Contractor should be aware that the production of written

instructions on the operation of the plant and services installed by them is a legal

requirement under the Health & Safety Regulations and failure to produce same

would place them under an obligation to run and operate the plant at their own

expense until such time as the proper written instructions are produced. See also

Clause above, "Inspection and Tests on Completion" sub-section D

Boiler Efficiency Tests.

200	BUILDING LOG BOOK

Not Used

Standard clauses A1

210	PHOTOGRAPHIC RECORD

The Contractor shall supply one set DIGITAL photographs. The number of pictures 	provided shall be 50. All to be to the satisfaction of the CA. The subject of the photographs 	shall be agreed by the CA and will comprise 50% before and 50% after the works are 	complete on	refurbishment contracts and 100% after works are completed on new build

contracts. Copyright of the pictures is to be vested in East Northants Council.

220	TOOLS AND LUBRICATION

Supply the following tools and accessories: Any special tools required for regular

maintenance of the oil and gas burners. One set of valve, grille and damper keys

for the entire installation, including radiator and manual vent keys. One set of

boiler tools and cleaning brushes complete with wall rack.

Lubricating grease and lubricating oil necessary for Sumps, motors, fans etc., on

the installation sufficient for one year's continuous operation. All tools and

accessories in a secure steel toolbox to be handed to the CA's

representative.

MAINTENANCE

240	CONTRACTORS RESPONSIBILITY

The Contractor shall allow within his tender to maintain the contracted works

for a period of twelve calendar months + one week after the date of completion.

The contractor shall make good all defects due to faulty workmanship or faulty or improper

materials. The date of completion as referred to in the preceding paragraph shall

be the date on which the premises are taken over by the CA or as directed

by the CA. While the new plant shall automatically be provided with a twelve

months' + one week warranty the Contractor is to include for twelve months' maintenance

of all 	plant, equipment and systems as a separate item. The Contractor shall allow for all

regular maintenance to manufacturers' requirements and must provide a

maintenance programme at least two months prior to completion of the works for

agreement, indicating frequency of routines and maintenance procedures against

each item of plant, equipment and system. All consumables and replacement part

costs shall be included in the maintenance cost.

Standard clauses A1

ASBESTOS

260	HEALTH AND SAFETY RESPONSIBILITY

East Northants Council has a duty under regulation 4 of the CAWR to ensure that

information about the location and condition of any known asbestos is provided to

anyone who may disturb it including Contractors who are on the premises. All

employers have a duty under Regulation 9 of the CAWR to ensure that adequate

information, instruction and training is given to those employees who are liable to

be exposed to asbestos, Contractors shall provide East Northants Council a written

policy setting out procedures for providing information, instruction and training to

their employees. Where the contractor believes that there is no reason

to suspect their staff will be exposed to asbestos during their normal work

activities, the reasons for this assumption will be given in writing. This should be

reviewed regularly, particularly when work methods change. The property has had

an asbestos survey carried out which indicates possible locations for Asbestos

Containing Material's. Prior to commencement of the project the successful

Contractor will be issued a copy for their information.

B

Scope of Works

Scope of Works B1

B1

Scope of Works

Scope of Works B1

B1 Scope of Works

10	SCOPE OF WORKS

All tenders must take into account and incorporate all and any costs implied

or otherwise by the following.

The appointed services contractor shall be the Principle Contractor and therefore

responsible for All works including Electrical, Intruder, Fire Alarm, Mechanical and

Construction. There are no other contractors and the appointed Principle

contractor shall be deemed to have included for all works that go to make a

complete, fit for purpose working system.

Heating Boiler Plant.

The installation includes but not limited to, the complete removal and replacement of the existing boilers, equipment  and pumps and the installation of new LPHW boilers and all associated equipment.

C

Demolition/ Alteration/ Renovation

Demolition C20

C20

Demolition

Demolition C20

C20 Demolition

To be read with Preliminaries/ General conditions.

GENERAL REQUIREMENTS

109A	 DESCRIPTION

Removal and disposal generally of the following:

- The existing boilers, boiler flues ( part ), pumps ( part ), control system equipment etc, and other associated equipment as shown or detailed within this specification.

•	All redundant wall brackets and fixings.

150	FEATURES TO BE RETAINED

•	 General: Keep in place and protect the following:  All remaining plant and equipment.

SERVICES AFFECTED BY DEMOLITION

Plant room, electrical, heating, natural gas, and cold water.

210	SERVICES REGULATIONS

•	 Work carried out to or which affects new or existing services: Carry out in

accordance with the Byelaws or Regulations of the relevant Statutory Authority.

220	LOCATION OF SERVICES

•	 Services affected by the Works: Locate and mark positions.

•	 Mains services: Arrange with the appropriate authorities for location and marking

of positions.

230	DISCONNECTION – ARRANGED BY CONTRACTOR

•	 General: Arrange with the appropriate authorities for disconnection of services and

removal of fittings and equipment prior to starting demolition.

260	BYPASS CONNECTIONS

•	 General: Provide as necessary to maintain continuity of services to occupied areas

of the same and adjoining properties.

•	 Notice: Give a minimum 72 hours notice to occupiers if shutdown is necessary

during changeover.

Demolition C20

270	SERVICES WHICH ARE TO REMAIN

•	 Damage: Give notice and notify service authority or owner of any damage arising

from the execution of the works.

•	 Repairs: To the satisfaction of the CA and service authority or owner.

DEMOLITION WORK

310	WORKMANSHIP

•	 Standard: Demolish structures in accordance with

•	 Operatives: Appropriately skilled and experienced for the type of work and hold or

be training to obtain relevant CITB Certificates of Competence.

•	 Site staff responsible for supervision and control of work: Experienced in the

assessment of risks involved and methods of demolition to be used.

320	GAS OR VAPOUR RISKS

•	 Precautions: Adequate to prevent fire or explosion caused by gas or vapour.

330	DUST CONTROL

•	 Method: Reduce by periodically spraying demolition works with water.

340	HEALTH HAZARDS

•	 Precautions: Protect site operatives and general public from hazards associated

with vibration, dangerous fumes and dust arising during the course of the Works.

391	ASBESTOS BASED MATERIALS

•	 Discovery: Give notice immediately of any suspected asbestos based materials

discovered during demolition work. Avoid disturbing such materials.

•	 Methods for safe removal. Submit details.

410	UNFORSEEN HAZARDS

•	 Unrecorded voids, tanks, chemicals, etc. discovered during demolition: Give

notice.

•	 Methods for safe removal, filling, etc: Submit details.

440	SITE CONDITIONS AT COMPLETION

•	 Debris: Clear away and leave the site in a tidy condition.

MATERIALS ARISING

510A	CONTRACTOR'S PROPERTY

•	 Components and materials arising from the demolition work shall be removed from

site unless detailed elsewhere in this specification.

- Remove from site as work proceeds.

P

Building fabric sundries

Builders work P1

P1

Builders work

Builders work P1

P1 Builders work

10	BUILDERS WORK

All tenders must take into account and incorporate all and any costs implied or

otherwise by the following.

Builders Work :-

All priced tenders must take into account and incorporate all and any costs implied

or otherwise by the following:

The successful contractor will be acting as the Principal Contractor and in doing so

will be responsible for all mechanical, electrical, builders work, health and safety,

and all statutory responsibility attracted by the position of Principal Contractor.

The Principal Contractor shall determine the scope of the builders works inclusive

of all enabling works in the form of penetrations, access hatches, platforms etc

together with all associated making good and reinstatement works

Costs for the following shall be included within all tenders:-

•	 Provide all general builders work attendances.

•	 To clear all rubbish and clean all internal surfaces affected by the works

•	 Provide a lockable skip for daily removal of site rubbish.  The Principal Contractor can

expect rubbish other than from the works to be deposited in the skip.

•	 Reinstate any hard or soft landscaping disturbed by the site works.

•	 Make good any damage to the structure, furniture, finishes or landscaping caused

by the actions of the contractors employees and / or subcontractors.

• The contractor shall allow for the safe removal of all removed plant and equipment

as required or shown on the drawings, including all fixings.

All tenders must take into account and incorporate all and any costs implied or

otherwise by the following.

The appointed services contractor shall be the Principle Contractor and therefore

responsible for all works including Electrical ,Mechanical and Construction.

Fire stopping systems P12

P12

Fire stopping systems

Fire stopping systems P12

P12 Fire stopping systems

To be read with Preliminaries/General conditions

GENERAL

110	FIRE STOPPING SYSTEMTO MULTIPLE SERVICE PENETRATIONS.

-  Panel material or joint filler: Submit proposals.

-  Sealant: Submit proposals.

130	FIRE STOPPING SYSTEM TO INDIVIDUAL SERVICES PENETRATIONS Pipes

and Ducts.

•	 Joint filler: Intumescent foams and Pipe collars - concealed intumescent .

- Size or thickness: Not applicable.

- Pipe outside diameter: Varies.

•	 Sealant: Fire resisting silicone.

•	   Colour: Contractor's choice .

140	FIRE STOPPING SYSTEM TO MULTIPLE SERVICES PENETRATIONS Pipes

and ducts.

•	 Panel material: All ducting Nullfire Systems J Flexible Seals supplied by Nullfire

Ltd, Torrington Avenue Coventry CV4 9TJ Tele No 0203 470022 .

- Thickness: To be oversized with sufficient space to provide fire stopping

packing sealed at both ends of the pipes..

- Number of layers: Two.

- Framing: Not required.

•	 Finish: Painting as section M60.

•	 Sealant: Fire resisting silicone.

•	 Colour: Submit proposals.

SYSTEM PERFORMACE

210	DESIGN

•	 Design: Complete the design of the fire stopping system.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturers' literature.

240	FIRE RESISTANCE Pipe stops.

•	 Fire resistance:

•	 Rating to BS 476-20: 30/30, 60/60 and 120/120.

- Rating to BS EN 13501-2: EI 30, EI 60 and EI 120.

•	 Surface spread of flame to BS 476-7: Class 0.

•	 Smoke resistance:

•	 Air leakage rate (maximum): 3 m³/m²·hr.

PRODUCTS

305	PRODUCT CERTIFICATION

•	 Certification: For products specified generically, submit evidence of compliance

with the specification.

Fire stopping systems P12

•	 Acceptable evidence: Agrément certificate.

310	BOARDS - CALCIUM SILICATE FIBRE REINFORCED

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals .

330	FIRE STOP LAMINATES

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

335	INTUMESCENT FOAMS

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

340	INTUMESCENT MORTARS

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

350	INTUMESCENT PUTTIES

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

360	MINERAL WOOL RIGID BATTS

•	 Standard: To BS 3958-5.

•	 Manufacturer: Submit proposals.

-  Product reference: Submit proposals.

370	PIPE COLLARS - CONCEALED INTUMESCENT

•	 Manufacturer: Submit proposals.

-  Product reference: Submit proposals.

375	PIPE COLLARS - INSULATED WRAP

•	 Manufacturer: Submit proposals.

-  Product reference: Submit proposals.

380	PIPE COLLARS - SURFACE MOUNTED INTUMESCENT

•	 Manufacturer: Submit proposals.

Product reference: Submit proposals.

385	SEALANT BACKING MATERIAL

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

390	SEALANTS - FIRE RESISTING SILICONE

•	 Standard: To BS 5889 Type A.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

395	SEALANTS - ONE-PART FIRE RESISTING ACRYLIC

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

Fire stopping systems P12

410	SEALANTS - TWO-PART FIRE RESISTING POLYSULFIDE

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

EXECUTION

620	WORKMANSHIP GENERALLY

•	 Gaps: Seal gaps between building elements and services, to provide fire

resistance and resist the passage of smoke.

•	 Adjacent surfaces: Prevent overrun of sealant or mortar on to finished surfaces.

640	INSTALLING BOARDING

•	 Position of boarding: Across face of opening.

•	 Framing: Provide framing to all edges of boarding.

•	 Bedding: Bed boarding on fire resisting silicone.

•	 Double layers of board: Staggered butt joints.

- Joints: Seal with vermiculite adhesive.

•	 Fixing: Spiral screws.

660	INSTALLING INTUMESCENT FOAM

•	 New joints: Remove builder's debris, mortar droppings, grease, and the like.

•	 Old joints: Clean and remove existing sealant from the joint.

•	 Priming: Lightly moisten substrate with water.

•	 Application: Fill joint to approximately half its depth, allowing foam to expand to

face of joint.

•	 Trimming: Do not trim or cut the face of the cured foam.

670	APPLYING INTUMESCENT MORTAR

•	  Sequence: Install mortar after services are permanently installed.

•	 Loose dust and combustible materials: Remove from the opening.

•	 Shuttering: Install suitable shuttering panels to the faces of the opening.

•	 Temperature: Do not apply mortar when it could be damaged by frost.

•	 Powder: water ratio: 2:1 for trowel grade by volume.

•	 Mortar cure: Do not disturb mortar before final set has taken place.

•	 Shuttering: Remove after mortar has cured.

690	APPLYING INTUMESCENT PUTTY

•	 Sequence: Install putty after services are permanently installed.

•	 Loose dust and combustible materials:  Remove from the opening.

710	INSTALLING  BATTS

•	 Installing batts: Fit tight into void between the floor or wall and the penetrating

services.

•	 Face of batts: Flush with the surface of wall, floor or soffit.

•	 Joints: Sealed with acoustic intumescent sealant.

•	 Gaps between services and bulkhead: Seal with fire resisting sealant.

730	FIXING INTUMESCENT PIPE COLLARS

•	 Collar fixing: Contractor's choice .

•	 Gap around collar: Seal with intumescent foam.

•	 Length of wraps: Project 50 mm from each side of the element.

Fire stopping systems P12

750	APPLYING SEALANT TO JOINTS

•	 De-greasing: Submit proposals

•	 Priming: Submit proposals

•	 Depth of sealant: 20 mm.

•	 Temperature: Do not apply water based sealants when they could be damaged by

frost.

COMPLETION

910	CLEANING

•	 Masking tapes: Remove.

•	 Cleaning: Clean off splashes and droppings. Wipe down finishes.

920	INSPECTION

•	 Notice for inspection (minimum): 5 days.

P31

Holes/ Chases/ Covers/ Supports for Services

Holes/ Chases/ Covers/

Supports for Services P31

P31 Holes/ Chases/ Covers/ Supports for Services

To be read with Preliminaries/General conditions

DESCRIPTION

The contractor is the main contractor responsible for the complete repair , making

good and redecoration of finishes associated with the installation of heating and

hot and cold water pipe work.

The contractor shall be responsible for all builders work in connection and allow for

all necessary costs to ensure the building is reinstated back to its original condition

prior to the heating contractor starting on site.

Builders work shall include all penetrations through walls and slabs, diamond

drilling through concrete, structural supports of plant, removal of old boxing/ducts,

boxing in of pipes, painting boxing with primer, under coat and two coats of Matt

finish, painting of walls behind radiators and chases and all exposed

pipes/radiators as per clauses P1 - P32.

The contractor shall include for all necessary bases for plant, brackets, weathering

of external wall penetrations and shall be responsible for coordinating, marking up

building works drawings and finishes.

110	COORDINATION Locations and dimensions of holes and chases for services:

Submit details Provide all builders works.

150	HOLES AND CHASES IN IN-SITU CONCRETE

•	 Cast in: Holes larger than 10 mm diameter and chases.

•	 Cutting and drilling:

- Permitted for holes not larger than 10 mm diameter.

- Not permitted for holes larger than 10 mm diameter except as indicated on

drawings.

185	HOLES, RECESSES AND CHASES IN MASONRY

•	 Locations: To maintain integrity of strength, stability and sound resistance of

construction.

•	 Sizes: Minimum needed to accommodate services.

- Holes (maximum): 300 x 300 mm.

•	 Walls of hollow or cellular blocks: Do not chase.

•	 Walls of other materials:

- Vertical chases: No deeper than one third of single leaf thickness, excluding

finishes.

- Horizontal or raking chases: No longer than 1 m. No deeper than one sixth of

the single leaf thickness, excluding finishes.

•	 Chases and recesses: Do not set back to back. Offset by a clear distance at least

equal to the wall thickness.

•	 Cutting: Do not cut until mortar is fully set. Cut carefully and neatly. Avoid spalling,

cracking and other damage to surrounding structure.

Holes/ Chases/ Covers/

Supports for Services P31

220	PREFORMED HOLES IN MASONRY

•	 Holes bigger than width 300 mm.

•	 Submit proposals for bridging over Pipes.

230	NOTCHES AND HOLES IN STRUCTURAL TIMBER

•	 General: Avoid if possible.

•	 Sizes: Minimum needed to accommodate services.

•	 Position: Do not locate near knots or other defects.

•	 Notches and holes in same joist: Minimum 100 mm apart horizontally.

•	 Notches in joists: Locate at top. Form by sawing down to a drilled hole.

- Depth (maximum): 0.125 x joist depth.

- Distance from supports: Between 0.07 and 0.25 x span.

•	 Holes in joists: Locate on neutral axis.

- Diameter (maximum): 0.25 x joist depth.

- Centres (minimum): 3 x diameter of largest hole.

- Distance from supports: Between 0.25 and 0.4 of span.

•	 Notches in roof rafters, struts and truss members: Not permitted.

•	 Holes in struts and columns: Locate on neutral axis.

- Diameter (maximum): 0.25 x minimum width of member.

- Centres (minimum): 3 x diameter of largest hole.

- Distance from ends: Between 0.25 and 0.4 of span.

310	PIPE SLEEVES FOR	SERVICE PENETRATIONS OF FLOORS

•	 Material Steel tube to BS 1387.

•	 Sleeves: Extend through full thickness of wall or floor. Position accurately.

- Clearance around service (maximum): 20 mm or diameter of service,

whichever is the lesser.

- Installation: Bed solid.

•	 Space between service and sleeve: Seal with intumescent sealant pointing to a

depth (minimum) of 10 mm at both ends of sleeve.

•	 Where exposed to view: Finish bedding and sealing neatly.

320	INTUMESCENT COLLARS For services through slab

•	 Manufacturer Contractor to submit proposals.

- Product reference Contractor to submit proposals.

•	 Pipeline nominal sizes As drawings.

•	 Fixing Self adhesive.

- Fixings must not incorporate plastics materials.

•	 Fire resistance As drawings.

•	 Integrity: Fit tightly and accurately to structure and pipe to maintain fire resistance.

Fill gaps between collar and structure and/ or pipe with intumescent material.

340	SEALING AROUND SERVICES

•	 Service As drawings.

•	 Location As drawings.

•	 Sealing material Silicone sealant.

•	 Method As required.

•	 Requirement Watertight.

Services painting systems P32

P32

Services painting systems

Services painting systems P32

P32 Services painting systems

To be read with Preliminaries/General conditions/builderswork

110	WALL COATING Plant room - NA to this project

•	 Sealant: Submit proposals.

- Colour: To be selected from manufacturers' standard range .

•	 Initial coats: Basecoat, water-borne and Primer, sealer.

- Number of coats: 2

- Colour: Pure white RAL Classic 9010.

•	 Finishing coats: Water-borne mould-resistant emulsion.

- Number of coats: 2

- Colour: Magnolia

- Finish: Satin.

120	FLOOR, BUND AND PLINTH COATING Plant room floor…

•	 Initial coats: Submit proposals and Recommended by finishing coat manufacturer.

- Colour: Concrete grey RAL Classic 7023.

•	 Finishing coats: Solvent based, low odour high build epoxy .

- Number of coats: 2

- Colour: Concrete grey RAL Classic 7023.

- Finish: Gloss.

SYSTEM PERFORMANCE

209A	GENERAL

The contractor shall include for painting all un-insulated internal pipes with 	primer/undercoat and one coats of gloss.

All wall finishes shall be made good with appropriate filler and prepared with

adequate sanding, primers and sealants to ensure good adhesion of paints.

210	DESIGN

•	 General: Complete the design of the coating systems in accordance with BS 6150.

•	 Proposals: Submit schedules, drawings and manufacturer's literature.

Services painting systems P32

220	DESIGN LIFETO METAL SURFACE COATINGS

•	 Design life (assuming reasonable wear and tear, and regular maintenance):  15

years

•	 Environment category in accordance with BS 6150: Interior moderate.

- Chemical and liquid resistance: Acids and alkalis, Fresh and salt water, Oils,

fats and grease and Solvents.

PRODUCTS

310	COATING RANGE

•	 Manufacturers and product references:

- Select one from the following: Dulux.

•	 Selected manufacturer: Submit proposed name and product references before

commencing coating work.

310A	COATING RANGE

To supports and pipes.

•	 Selected manufacturer: Submit proposed name and product references before

commencing coating work.

312	SEALANT, WATER-BORNE ACRYLIC

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

315	UNDERCOAT - THINNED WATER-BORNE

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

320	BASECOAT, WATER-BORNE

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

330	PRIMER- ALKALI RESISTING.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

340	BITUMEN BASED COATING- BLACK PAINT

•	 Standard: To BS 6949.

- Without fillers: Type 1.

- With fillers: Type 2.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

350	WATER-BORNE COATING- EMULSION.

•	 Manufacturer: Dulux.

- Product reference: Submit proposals.

370	SOLVENT-BORNE COATING- CHLORINATED RUBBER .

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

Services painting systems P32

380	TAR BASED BLACK PAINT

•	 Standard: To BS 1070.

- Required to dry in 8 h: Type A.

- Required to dry in 4 h: Type B.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

EXECUTION

610	PREPARATION GENERALLY

•	 Substrates: Sufficiently dry and sound in depth to suit coating.

•	 Efflorescence: Remove.

•	 Dirt, grease and oil: Remove.

- Give notice if surfaces and/ or substrates have been contaminated.

•	 Joints, cracks, holes and other depressions:

- Fill with stoppers and/ or fillers. Work well in and finish off flush with surface.

- Provide smooth finish.

•	 Water-borne stoppers and fillers:

- Apply before priming unless recommended otherwise by manufacturer.

- If applied after priming: Patch prime.

•	 Oil based stoppers and fillers: Apply after priming.

•	 Surface irregularities: Finish smooth.

•	 Dust, particles and residues from abrasion: Remove.

•	 'Wet paint' signs and barriers: Locate where necessary.

635	SERVICE EQUIPMENT, FIXTURES AND FITTINGS

•	 Preparation:

- Items to be removed: Grilles, cover plates and other surface mounted fixtures.

and Plant labels and/ or signage.

- Surfaces to be cleaned: Prefinished fixtures, fittings and service fittings.

- Surfaces not to be coated: Radiator valves and stop valves and Hinges.

•	 Finishing coat: Do not apply before services equipment second fix.

All tenders must take into account and incorporate all and any costs implied or

otherwise by the following.

The appointed services contractor shall be the Principle Contractor and therefore

responsible for all works including Electrical, Mechanical and Construction.

Services painting systems P32

645	PREPARING PREVIOUSLY COATED SURFACES

•	 Removing coatings: Do not damage substrate and adjacent surfaces or adversely

affect subsequent coatings.

•	 Existing coatings on ironmongery:

- Remove old coating marks. Clean and polish.

- Do not remove hinges.

- Refix ironmongery on completion.

•	 Loose, flaking or otherwise defective areas: Carefully remove to leave a firm

surface.

•	 Alkali affected coatings: Completely remove.

•	 Problematic substrates: Give notice of the following:

- Coatings suspected of containing lead.

- Substrates suspected of containing asbestos.

- Significant rot, corrosion or other degraded substrates.

•	 Retained coatings: Remove dirt, grease and contaminants.

•	 Gloss coated surfaces: Make a key.

•	 Partly removed coatings:

- Additional preparatory coats: Apply to restore original film thicknesses.

- Junctions: Make surfaces flush.

•	 Completely stripped surfaces: Prepare as for uncoated surfaces.

655	PREPARING PREVIOUSLY COATED STEEL

•	 Existing defective coatings including primers: Remove to leave a firm edge and

clean bright metal.

•	 Sound coatings: Make a key.

•	 Corrosion and loose scale: Remove to leave bare metal.

•	 Residual rust: Remove.

•	 Remaining areas: Degrease.

•	 Bare areas: Re-prime.

665	PREPARING UNCOATED STEEL - MANUAL CLEANING

•	 Oil and grease: Remove.

•	 Corrosion, loose scale, welding slag and spatter: Remove.

•	 Residual rust: Treat using a proprietary removal solution.

•	 Primer: Apply as soon as possible.

680	PREPARING UNCOATED ALUMINIUM OR COPPER OR LEAD

•	 Surface corrosion: Remove and provide suitable surface for coating.

705	PREPARING UNCOATED MASONRY AND/ OR RENDERING

•	 Loose and flaking material: Remove.

710	PREPARING UNCOATED PLASTER

•	 Nibs, trowel marks and plaster splashes: Scrape off.

•	 Overtrowelled 'polished' areas:  Leave surface suitable for coating.

715	PREPARING UNCOATED PLASTERBOARD

•	 Depressions around fixings: Fill with stoppers and/ or fillers.

Services painting systems P32

730	PREPARING AND DEALING WITH ORGANIC GROWTHS

•	 Loose growths and infected coatings: Scrape off and remove.

•	 Treatment biocide: Apply appropriate solution to growth areas and surrounding

surfaces.

•	 Dead growth: Scrape off and remove.

•	 Residual effect biocide: Apply appropriate solution to inhibit re-establishment of

growths.

740	PREPARING AND APPLYING SEALENTS

•	 General: Apply sealant to junctions of walls and ceilings with architraves, skirtings,

movement joints and other trims.

•	 Preparation and application: As section Z22.

760	APPLYING COATINGS GENERALLY

•	 Conditions: Maintain suitable temperature, humidity and air quality during

application and drying.

•	 Surfaces: Clean and dry at time of application.

•	 Thinning and intermixing of coatings: Not permitted unless recommended by

manufacturer.

•	 Overpainting: Do not paint over intumescent strips or silicone mastics.

•	 Priming coats:

- Thickness: To suit surface porosity.

- Application: As soon as possible on same day as preparation is completed.

•	 Finish:

- Even, smooth and of uniform colour.

- Free from brush marks, sags, runs and other defects.

- Cut in neatly.

770	COATING CONCEALED METAL SURFACES

•	 General: Apply additional coatings to surfaces that will be concealed when fixed in

place.

COMPLETION

910	REMOVED ITEMS

•	 General: Refix.

920	DOCUMENTATION

•	 Maintenance instructions: Submit.

•	 Record drawings: Submit.

930	SPARES AND CONSUMABLES

•	 Coatings: Supply 2 L of each type.

•	 Labels on containers: Required.

S

Piped supply systems

Hot and cold water supply

systems S10

S10

Hot and cold water supply systems

Hot and cold water supply

systems S10

S10 Hot and cold water supply systems

NOT USED

Natural gas supply systems

S32

S32

Natural gas supply systems

Natural gas supply systems

S32

S32	 Natural gas supply systems

To be read with Preliminaries/ General conditions

12	SCOPE OF WORKS… The contractor shall supply install test and commission the

internal natural gas installation as per the tender drawings.

Internal gas pipe work shall distribute to the new gas fired  boilers

from points on the existing gas supplies as shown on the drawings. The contractor 		shall include for all necessary purging and commissioning of the complete gas installation.

GENERAL

SYSTEM PERFORMANCE

PRODUCTS

310	SECONDARY GAS.  N/A

330	LOW PRESSURE GAS SUPPLY PIPELINES Above Ground

•	 Standards: To BS EN 1775 and in accordance with IGE/UP/2.

•	 Materials: Steel, medium weight.

•	 Fittings: Malleable cast iron.

340	GAS SOLENOID VALVES Plant room… NOT USED

400	SAFETY AND CONTROL DEVICES

•	 Standard: To BS EN 13611.

Natural gas supply systems

S32

410	BALL VALVES, MANUALLY OPERATED Gas valves.

•	 Standard: To BS EN 331.

•	 Type: Lever operated.

•	 Manufacturer: Crane or Hattersley.

- Product reference: Contractor's choice.

•	 Material: Bronze or dezincification resistant brass (DZR).

•	 Connections: Threaded.

420	PLUG VALVES, CAST IRON Incoming entry point

•	 Standard: To BS 5158.

•	 Type: Regular.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Connections: Flanged.

•	 Options: Wrench.

EXECUTION

610	STRIPPING OUT

•	 Extent of stripping out: Part installation as indicated on the drawings..

620	INSTALLATION GENERALLY

•	 Installation: In accordance with IGE/UP/10.

630	INSTALLING SECONDARY GAS METERS

•	 Standard: To BS 6400.

650	COMMERCIAL AND INDUSTRIAL GAS PIPELINES

•	 Installation: In accordance with BS EN 1775.

COMPLETION

920	SMALL LOW PRESSURE COMMERCIAL AND INDUSTRIAL GAS

INSTALLATIONS

•	 Soundness testing and purging: In accordance with IGE/UP/1A.

930	COMMERCIAL AND INDUSTRIAL GAS PIPELINES

•	 Testing, purging and commissioning: In accordance with BS EN 1775.

940	COMMERCIAL AND INDUSTRIAL GAS INSTALLATIONS

•	 Soundness testing and purging: In accordance with IGE/UP/1.

950	COMMERCIAL AND INDUSTRIAL GAS FIRED PLANT

•	 Commissioning: In accordance with IGE/UP/4.

Natural gas supply systems

S32

960	DOCUMENTATION

•	 Manufacturers' operating and maintenance instructions: Submit for equipment and

controls.

•	 System operating and maintenance instructions: Submit for the systems as a

whole giving optimum settings for controls.

•	 Record drawings: Submit drawings showing the location of circuits and operating

controls.

970	OPERATING TOOLS

•	 Tools: Supply tools for operation, maintenance and cleaning purposes.

•	 Valve keys: Supply keys for valves and meter housing.

- Quantity: 1 of each type.

980	MAINTENANCE

•	 Servicing and maintenance: Undertake.

- Duration: Until 12 months + one week after Practical Completion.

T

Mechanical heating, cooling and refrigeration

Heating systems T10

T10

Heating systems

Heating systems T10

T10 	Heating

To be read with Preliminaries/ General conditions.

GENERAL

The contractor shall supply, install, test and commission 4 x LTHW heating boilers and associated plant All works to be carried out in accord with the current British Standards and codes of practice.

The mechanical contractor shall include for all necessary materials, tools, labour

and equipment to supply install commission and put into operation the following

installations as indicated on the tender drawings.

•	 Provide and install gas fired boilers, connecting pipe work, flue connections,

supports and all necessary controls.

•	 Provide steel LTHW heating pipes. The contractor must notify the CA of types.

•	 Provide drain cocks at low level and manual vents with 15mm valved discharges

dropping to LL

•	 Provide reinforced foil faced thermal mineral wool insulation through out including the 				distribution system.

•	 Provide all valve, flange and other plant and equipment with insulated muffs, new as well as 			 existing in order that all surface are insulated,

•	 Provide all necessary fixings and support

•	 Testing and commissioning of all services

•	 Provide coordinated construction and builders work drawings for comments and

approval.

•	 Provide operating and maintenance manuals

Heating systems T10

109B	SCOPE OF WORK

The contractor shall supply install test and commission the complete LTHW

heating installation in accordance with EU, CIBSE & British Standards.

•	Boiler Rooms

Provide 4 x new gas fired boilers.

Provide all necessary connecting pipe work from the boilers to the existing distribution systems

Supply and install all necessary controls and wiring in order to provide a fully functional and complete boiler plant control system.

All tenders must take into account and incorporate all and any costs implied or

otherwise by the following.

The appointed services contractor shall be the Principle Contractor and therefore

responsible for all works including Electrical, Mechanical and Construction.

Heating systems T10

- LOW TEMPERATURE HOT WATER HEATING SYSTEM

•	 Type: Two pipe.

•	 Heat source: Gas fired  boiler, as section T20.

•	 Fuel: Gas.

•	 Pressurization units: As section Y20.

•	 Feed and expansion tanks: Not required.

•	 Pipelines: As section Y10.

•	 Pipelines ancillaries: As section Y11.

•	 Pumps ...See contract drawing

•	 Heat emitters… See contract drawing

•	 Thermal insulation: As section Y30.

•	 Vibration isolation: Not required.

•	Central Trend and wiring of controls and equipment shall be undertaken by John Grimes of Control Services or equal and approve.

•	 Accessories: Submit design and cost proposals.

•	 Completion:

- Cleaning and chemical treatment: Flushing and chemical treatment, as section

Y12. and detailed on the drawings.

- Plant and equipment identification: Mechanical plant and equipment

identification, as section Y32.

- Commissioning: Performance testing, as section Y50.

115	THERMOSTATIC RADIATOR VALVES…NOT USED

SYSTEM PERFORMANCE

210	DESIGN AND DETAILING

•	 Design: Complete the design of the heating system.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturers' literature.

220	BASIC DESIGN TEMPERATURES

•	 Design temperatures: 82/71 Existing radiator design.

•	 External air temperature: -3°C.

250	SYSTEM OPERATING PARAMETERS

•	 Design flow temperature: Maximum 82°C.

•	 Temperature difference across primary heating circuit: 11°C.

•	 Temperature difference across primary hot water circuit: 11°C.

•	 Water velocity: Maximum 1.5 m/s.

280	ELIMINATION OF GRAVITY CIRCULATION

•	 Requirement: Design and install heating system to prevent gravity circulation.

EXECUTION

610	STRIPPING OUT

•	 Extent of stripping out: Boiler Rooms and associated, pipe work, flue connections, plant

and controls.

Heating systems T10

620	INSTALLING WATER BASED HEATING SYSTEMS

•	 Standard: To BS 5449 or BS EN 14336.

COMPLETION

905	HYDRAULIC PRESSURE TESTING OF LOW TEMPERATURE HOT WATER

HEATING SYSTEMS

•	 Testing: In accordance with HVCA TR/6.

•	 Notice (minimum): 48 h

•	 Pressure: 2 times working pressure.

•	 Duration of test: 2 h.

910	DOCUMENTATION

•	 Operation and maintenance instructions/health and safety file: Submit.

•	 Record drawings: Submit.

920	OPERATING TOOLS

•	 Tools: Supply tools for operation, maintenance and cleaning purposes.

•	 Keys: Supply keys for valves and vents.

930	MAINTENANCE

•	 Servicing and maintenance: Undertake.

- Duration: Until 12 months and one week after Practical Completion.

Gas and oil fired boilers T20

T20

Gas and oil fired boilers

Gas and oil fired boilers T20

T20 Gas and oil fired boilers

PRODUCTS - NA to this project

320A	GAS FIRED CONDENSING BOILERS Plant room

•	 Standard: To BS EN 677.

•   Manufacturer: Broag commercial

- Product reference: Quinta 115 pro output..

•	 Boiler load (maximum): Not applicable.

•	 Seasonal efficiencies (minimum): 96%.

•	 Thermal performance testing: To BS 845-1.

•	 NOx emissions (maximum): <34 mg/kW·h.

•	 Safety: To BS 5978.

•	 Mounting: Wall (Steel Frame) Mounted.

•	 Output: See schedule.

•	 Flow and return temperatures: 82/71°C.

•	 Operating pressure: 1.5 Bar.

•	 Test pressure: On new pipework 2 x System pressure ( existing pipework must be isolated.)

•	 Materials:

- Heat exchanger:. Manufacturer's standard

- Casing: Manufacturer's standard.

•	 Fuel: Natural gas.

•	 Burner: pressure jet..

•	 Burner control: Modulating.

•	 Electrical supply type: Single phase.

•	 Integral controls: Spark ignition.

•	 Flues and chimneys: Non-integral, as section Y35.

•	 Accessories:

-   Pressure gauge;

-  Safety valve; and

-  Temperature gauge.

322	BOILER FLUE

The contractor shall allow for the design and installation of all boiler flue systems in accord with the manufactures recommendations. This shall include the confirmation of the details as shown on the tender/contract drawings.

.

Gas and oil fired boilers T20

325	PRIMARY PRESSURISATION SET Plant rooms. NOT USED

PRESSURISATION SET Plant room …

•	 Manufacturer:- Flamco Flexcon ( not any other manufacture )

•	 Standards: To BS 4814. - LPHW

General:

•	 Arrangement: [Diaphragm expansion tank ]. 400 lit acceptance

•	 Static head: [6metres].

•	 Plant rating: [35metres].

•	 System water content: [assume expansion vessel volume on 1Litres per Kw on

secondary side].

•	 Operating temperatures:

- Flow: [82].

- Return: [71].

•	 Operating pressure: [1.0 bar].

Gas and oil fired boilers T20

327	PLATE HEAT EXCHANGER…NOT USED

Manufacturer: - The contractor is to allow for the collection of a stainless steel plate heat exchanger from

Quote…NA

Area Served…NA

Type No KW	Inlet Operating temperatures:

- Flow: [86].

- Return: 75].

Secondary Outlet Operating temperatures:

- Flow: [82].

- Return: [71].

Flow rate.

Pressure Drop (Maximum pressure drop 20 KPa)

Maximum Operating pressure 3.5 Bar

327B	LOUVRES    NA

327C	EXISTING DOOR LOUVRES   NA

- DOSING

Chemical dosing to be Sentinal x-100 or

Fernox Copal.

Gas and oil fired boilers T20

328A	AIR SEPARATOR  NA

329	CONTROLS see previous statements and drawings - NA

Manufacturer:- Submit proposals

.

400	AIR SUPPLY TO APPLIANCES

•	 Standards: To BS 5440-2 and BS 6644.

•	 Sizes Submit proposals.

•	 Location: Submit proposals.

EXECUTION

610	INSTALLING BOILERS -

•	 Standards:

- Gas fired boilers: To BS 6798 and BS 6644.

- Oil fired boilers: In accordance with BS 5410.

•	 Fixing of equipment, components and accessories: Fix securely on purpose-made

bases or supports.

•	 Preparation: Immediately before installation of lagging and casing, pressure test

joints.

- Results: Submit.

•	 Space around the boiler: Adequate:

- to ensure sufficient air circulation for draught diverter operation;

- to ensure sufficient air for combustion and cooling; and

- for maintenance and servicing.

•	 Location: Minimum 75 mm from combustible material.

•	 Access: Provide for inspection and servicing of boilers and ancillary equipment.

U

Ventilation and air conditioning systems

Local air conditioning systems

U60

U60

Local air conditioning systems

Local air  systems

U60

U60 Local air systems

To be read with Preliminaries/ General conditions

GENERAL

109A N/A

V

Electrical

Low voltage distribution

systems V30

V30

Low voltage distribution systems

Low voltage distribution

systems V30

V30 Low voltage distribution systems

To be read with Preliminaries/ General conditions

Low voltage distribution

systems V30

GENERAL

109A	SCOPE OF WORKS

All tenders must take into account and incorporate all and any costs implied or

otherwise by the following.

The appointed services contractor shall be the Principle Contractor and therefore

responsible for all works including Electrical, Mechanical and Construction.

The contractor will find that the premises maintains the

alarm systems the contacts and details may be obtained whilst carrying out your

site survey.

Any data cabling or trunking must not be touched. It can however be built into the

pipe boxing in order to maintain access. The contractor must demonstrate access

to this item from 3 points as requested by the Engineer.

The successful contractor shall submit proposals / designs for approval prior to

any installation.

All tenders must take into account and incorporate all and any costs implied or

otherwise by the following.

Low voltage distribution

systems V30

•	 Commission and test electrics in accordance with current IEE regulations

110	LOW VOLTAGE DISTRIBUTION SYSTEMGENERALLY

•	 Connection to low voltage supply: Existing.

•	 Switchgear: Provide new Three phase switch fuse.

•	 Cable type: Multi-core PVC/ SWA/ PVC, as section V32.

•	 Rewireable installation: Not required.

•	 Concealed installation: Not required.

•	 Containment:

-  Cable ladders, as section Y63;

-  Cable trays, as section Y63; and

-  Protective covers, as section Y63.

•	 Accessories: Cable cleats, as section Y63.

•	 Completion:

- Electrical identification: As section V80.

- Testing and inspection: To BS 7671.

SYSTEM PERFORMANCE

210	DESIGN

•	 Standard: To BS 7671.

•	 Design: Complete the design of the low voltage distribution system.

•	 Spare capacity throughout the low voltage distribution system: None.

•	 Scope: Provide electrical supplies to equipment requiring power.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturers' literature.

•	 Switchgear drawings: To BS EN 61082-1.

EXECUTION

410	STRIPPING OUT

•	 Extent of stripping out: Old Control panel power wiring.

420	INSTALLING LOW VOLTAGE DISTRIBUTION SYSTEMS

•	 Standard: To BS 7671.

•	 Layout: Position cabling and equipment to provide safe and easy access for

operation and maintenance.

450	CONNECTION TO THE INCOMING SUPPLY

•	 Customer's installation: Connect to the incoming point of supply.

Low voltage distribution

systems V30

COMPLETION

920	DOCUMENTATION

•	 Operation and maintenance instructions: Submit.

•	 Record drawings: Submit.

- Number of copies: 2.

930	MAINTENANCE

•	 Servicing and maintenance: Undertake.

- Duration: Until 12 months + one week after Practical Completion.

General lighting systems V50

V50

General lighting systems

General lighting systems V50

V50 General lighting systems…NOT USED

GENERAL… NA

110	GENERAL LIGHTING SYSTEMGENERALLY

•	 Origin of supply: Existing board.

•	 Final circuit cabling:

- Types: PVC singles, as section V32.

- Sizes: Submit design and cost proposals.

•	 Containment: Rigid conduit, as section Y60.

•	 Rewireable installation: Required.

•	 Concealed installation: Not required.

•	 Partial installation: Required.

•	 Connections to luminaires: Submit design and cost proposals.

•	 Luminaires and lamps: As schedule below.

- Luminaire types: As Luminaire schedule.

- Luminaire accessories: NA.

•	 Operating voltage: Low voltage.

•	 Lamp types: As Luminaire schedule.

- Colour rendering index (Ra) (minimum): As schedule.

•	  Control gear: High frequency, as section V59.

•	 Lighting controls: Manual.

•	 Completion:

- Electrical identification: To BS 7671.

General lighting systems V50

SYSTEM PERFORMANCE

210	DESIGN

•	 Standard: In accordance with CIBSE Code for lighting.

•	 Design: Complete the design of the general lighting systems.

•	 Average power density energy consumption (maximum): 20 W/m².

•	 Initial circuit luminous efficacy (minimum): 45 lm/W.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturers' literature.

220	PERFORMANCE

•	 Lighting performance: As Lighting performance schedule.

230	MAINTENANCE FACTOR CALCULATIONS

•	 Proposals for luminaire maintenance: Submit.

•	 Proposals for lamp replacement: Submit with calculations and manufacturers'

literature.

•	 Maintenance factors: Submit.

240	LUMINAIRE AND LAMP MAINTENANCE PROPERTIES General

•	 Lamp replacement method: Spot replacement.

•	 Lamp lumen maintenance factor: Submit proposals.

•	 Lamp survival factor: Submit proposals.

•	 Luminaire maintenance class: Submit proposals.

•	 Luminaire cleaning interval: 1 y.

•	 Luminaire maintenance factor: Submit proposals.

•	 Room surface cleaning interval: 1 y.

•	 Room surface maintenance factor: Submit proposals.

250	LIGHTING CALCULATIONS

•	 Type: Computer generated point calculations with contribution from inter-reflected

light.

•	 Submit the following:

- Luminaire layout drawings.

- Luminaire photometric data including flux fraction ratios, polar intensity curves

and utilisation factors.

- Lamp technical information.

- Room surface reflectance values.

- Maintenance factor calculations.

- Isolux contour plots for working plane and room surfaces.

- Schedule of design and calculated maintained average illuminance values.

- Schedule of wall-working plane illuminance ratios.

- Schedule of ceiling-working plane illuminance ratios.

- Schedule of design and calculated uniformity values.

- Schedule of design and calculated glare index values.

- Power density and efficacy of the installation.

General lighting systems V50

PRODUCTS

EXECUTION

610	INSTALLING GENERAL LIGHTING SYSTEMS

•	 Standard: To BS 7671.

620	STRIPPING OUT

•	 Extent of stripping out: N/A

630	MODIFYING EXISTING LIGHTING SYSTEMS

•	 Existing luminaires: Clean.

•	 Existing lamps: Replace.

640	LIGHTING CIRCUITS

•	 Rooms smaller than 4 m²: Restrict lighting circuits to one electrical phase.

650	MANUAL CONTROLS

• Location: By exit.

•Staircases: N/A

COMPLETION

905	TESTING AND INSPECTION OF FIXED ELECTRICAL WIRING

•	 Testing and inspection: To BS 7671.

•	 Test results: Submit.

- Number of copies: 2.

910	TESTING AND COMMISSIONING OF GENERAL LIGHTING SYSTEMS

•	 Commissioning: In accordance with CIBSE Commissioning code L

•	 Controls: Check operation.

•	 Lamps: Check operation.

•	 Test results: Submit.

- Number of copies: 2.

930	DOCUMENTATION

•	 Operation and maintenance instructions: Submit.

•	 Record drawings: Submit.

- Number of copies: 2.

940	MAINTENANCE

•	 Servicing and maintenance: Undertake.

- Duration: Until 12 months after completion.

Luminaires and lamps V59

V59

Luminaires and lamps

Luminaires and lamps V59

V59 Luminaires and lamps…NOT USED

To be read with Preliminaries/General conditions.

PRODUCTS

310	LAMPS GENERALLY

•	 Manufacturer: As recommended by luminaire manufacturer.

•	 Lamps of the same type and rating: Same manufacturer.

•	 Fluorescent ballasts: Separate for each lamp.

330	TUBULAR FLUORESCENT LAMPS

•	 Standards:

- Single-capped lamps: To BS EN 60901 and BS EN 61199.

- Double-capped lamps: To BS EN 60081 and BS EN 61195.

•	 Lamp diameter: 16 mm.

•	 Colour temperature: 6500K.

•	 Colour rendering index: 70-80.

370	LAMP BALLASTS

•	 Control gear generally: To BS EN 61347-1.

•	 Fluorescent lamp ballasts:

- Switched start: To BS EN 60921 and BS EN 61347-2-8.

- High frequency (A.C supplied): To BS EN 60929 and BS EN  61347-2-3.

- High frequency (D.C supplied): To BS EN 60925 and BS EN 61347-2.4.

•	 Discharge lamp ballasts: To BS EN 61347-2-9 and BS EN 60923.

•	 Emergency lighting ballasts: BS EN 60925 and BS EN 61347-2-7.

392	FLUORESCENT LAMP HOLDERS

•	 Standard: To BS EN 60400.

400	LUMINAIRES

•	 Standards: To BS EN 60598-1 and BS EN 55015.

•	 Approval: Kitemark certified.

•	 Photometric performance: To BS 5225-1.

•	 Ballasts CELMA energy efficiency index (minimum): A3.

•	 Control gear: Integral within luminaire.

•	 Supply circuit conductor connections: Screw terminals.

•	 Fuse holders and fuses: Required for incoming circuit phase connections. Label

with circuit reference.

410	POWER FACTOR CORRECTION

•	 Luminaires: Correct power factor to a minimum 0.9 lagging.

EXECUTION

610	SAMPLES

•	 Samples: Before ordering, supply samples of the following luminaires: NA.

•	 Submittals: Include manufacturer's technical information with each sample.

•	 Identification: Label samples with the luminaire references.

Luminaires and lamps V59

620	INSTALLING LUMINAIRES AND LAMPS GENERALLY

•	 Standard: To BS 7671.

•	 Location: Plant room.

•	 Orientation: Parallel with ceiling.

•	 Lamps and accessories: Provide.

•	 Supports: Adequate for weight of luminaire.

630	LUMINAIRE CABLE CONNECTIONS

•	 Cable connection size (minimum): 1.5 mm².

•	 Conduit mounted: Terminate in a terminal block within a conduit box, with an HR

PVC/ PVC cord final connection.

•	 Trunking mounted: NA.

•	 Suspended trunking: From cable connection mounted on side of trunking.

- Type: NA.

•	 Rod or chain suspended: NA.

- Cable type: HR PVC/ PVC cord, clipped to chain or rod. Do not pass cord

through chain links.

•	 Cable entry: Grommet.

•	 Class 1 earth connections: Connect to luminaire circuit protective conductor.

•	 Wiring within luminaires: Minimize. Clip at 300 mm intervals.

670	INSTALLING CONTROLGEAR

•	 Location: Adjacent to luminaire.

•	 Fixing: Secure to building fabric.

690	INSTALLING LUMINAIRE SUPPORTS

•	 Support and fixing arrangement: Submit proposals

•	 Luminaire suspensions: Vertical.

- Multiple suspensions: Provide as necessary.

•	 Levelling: Adjust the length of suspensions so that luminaires are level.

- Levelling tolerance: ± 3 mm.

•	 Conduit supports:

- Size (minimum): 20 mm.

- Type: Match cable containment.

- Conduit boxes: Provide for each luminaire suspension point.

•	 Rod supports: Continuously threaded rods.

•	 Chain supports: Steel chain with conduit box hook and cover.

•	 Ball and socket: Provide as top support and fix cover to circular conduit box. Route

cable from conduit box through ball and socket.

•	 Number of supports for luminaires longer than 600 mm (minimum):

- Luminaire width<300 mm: 2.

- Luminaire width >300 mm: 4.

COMPLETION

910	CLEANING

•	 Luminaires and lamps: Clean when building works are complete.

920	TESTING AND COMMISSIONING

•	 Luminaires and lamps: Check operation.

Luminaires and lamps V59

930	SPARE LAMPS N/A

Earthing and bonding systems

V81

V81

Earthing and bonding systems

Earthing and bonding systems

V81

V81 Earthing and bonding systems

To be read with Preliminaries/ General conditions.

GENERAL

110	EARTHING AND BONDING SYSTEMS GENERALLY

•	 Main incoming earth: NA.

•	 Size of main earthing conductor: NA.

•	 Main earth electrode type: NA.

•	 Main equipotential bonding

- Connect the following to the main earthing terminal: check and fix existing

bonding to gas, water services and heating.

- Cable type: PVC singles, as section V32.

- Size: To BS 7671 Regulation 547-02-01

•	 Supplementary equipotential bonding: Bond the following: To all new services.

- Cable type: PVC singles, as section V32.

- Size: Minimum of 2.5 mm² if sheathed or where mechanical protection is

provided, otherwise 4 mm².

•	 Circuit protective conductors

- Type: Submit design and cost proposals.

- Size: To BS 7671 Regulation 543-01-03.

•	 Earth terminal: As existing.

•	 Earthing of metal fencing around substations: Not required.

•	 Accessories: Earth clamps

SYSTEM PERFORMANCE

210	DESIGN

•	 Standards: To BS 7671 and in accordance with BS 7430.

•	 Design: Complete the design of the earthing and bonding systems.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturer's literature.

PRODUCTS

310	PRODUCTS GENERALLY

•	 Standards: To BS 7671 and in accordance with BS 7430.

330	FUNCTIONAL EARTH CABLES

•	 Standard: To BS 6701.

•	 Sheath colour: Cream to BS 6746C.

440	EARTH CLAMPS

•	 Standard: To BS 951.

EXECUTION

610	GENERAL INSTALLATION

•	 Standards: To BS 7671 and in accordance with BS 7430 .

Earthing and bonding systems

V81

620	STRIPPING OUT

•	 Extent of stripping out: Existing bonding.

630	EXISTING INSTALLATIONS

•	 External earth fault loop impedance: Direct measurement.

•	 Earth fault loop impedance: Measure.

- Method: Calculate from measurement of the sum of the resistance of the phase

conductor and the resistance of the circuit protective conductor.

- Locations: Origin, switchgear, fixed equipment and outlets, and circuit

extremities.

•	 Results: Submit.

720	INSTALLING MAIN EQUIPOTENTIAL BONDING CONDUCTORS

•	 Separate and continuous connections: Install between each service and the main

earth terminal.

•	 Earth connections at main earth terminal: Connect with compression lugs and

phosphor bronze nuts and bolts.

730	INSTALLING SUPPLEMENTARY BONDING CONDUCTORS

•	 Earth connections: Connect with compression lugs.

750	DISSIMILAR METALS

•	 Connecting dissimilar metals: Prevent electrolytic action.

COMPLETION

910	INSPECTION AND TESTING

•	 Standards: To BS 7671 and in accordance with BS 7430.

•	 Notice before commencing tests (minimum): 24 h.

•	 Continuity of protective conductors:

- Parallel earth paths: Isolate before testing.

- Equipment: Continuity tester with short circuit current not less than 200 mA,

and a no load d.c. or a.c. voltage between 4 V and 24 V.

•	 External earth fault loop impedance: Direct measurement.

•	 Earth fault loop impedance:

- Method: Direct measurement.

- Measurement locations: Origin, switchgear, fixed equipment and outlets, and

circuit extremities.

940	DOCUMENTATION

•	 Operation and maintenance instructions: Submit.

•	 Record drawings: Submit.

W

CONTROL AND WIRING STANDARDS

Controls W6

W6

Controls

Controls W6

W6 Controls

10	CONTROL WIRING AND CONTAINMENT

1.0 	AUTOMATIC CONTROLS

1.1 	EXTENT OF WORKS

The appointed services contractor shall be the Principle Contractor and therefore

responsible for all works including Electrical, Mechanical and Construction.

The successful contractor shall submit proposals / designs for approval prior to the

commencement of any installation.

The contractor shall allow within his tender for the Installation of  all control and power wiring and equipment that is required for the full and complete running of the boilers and equipment described in this specification. The contractor shall employ the specialist controls company listed below to carry out the works.

installation

- Control Services Ltd, Northants… John Grimes

The contractor may propose a controls contractor providing that they are HVAC Control systems and TREND specialist.

The Contractor is reminded that they will be responsible for the works carried out

by the Specialist Sub-Contractor(s), which includes full documentation of the final

installation and all necessary instruction of how the system operates to the

Centre’s' representative. Allowances for the documentation and instruction of

operations are included in the specification.

Other companies will be considered for these works

The electrical contractor will be responsible for all new power and control wiring to

the new control panel, ancillary fittings, plant and sensors The electrical sub-

contractor will be responsible for wiring outside the plant room back to the new

control panel. The specialist controls contractor will be responsible for the supply,

final connections, testing and commissioning of controls and power wiring to plant.

The Mechanical Contractor shall allow for a specialist controls Sub-Contractor to

carry out the design, installation, programming, commissioning and setting to work

of a BMS (Building Energy Management System) Controls System to monitor and

control the plant and equipment as installed under this Contract and detailed under

this Specification.

The controls specialist shall include for detailed field wiring drawings indicating all

control and power wiring, containment, sensors, brackets and supports in the

teaching, corridor communication areas and plantrooms. The drawings shall be

made available for comment by the contract administrator two weeks prior to

installation on site and shall be issued to the electrical contractor as free issue.

2.0 	CONTROLS DESCRIPTION

2.1 	OBJECTIVES

To install the 4 x Quinta boilers and pumps as described and integrate these within the existing 	Trend control panel and system employing the existing control philosophy

  - GENERAL

2.3 	SCOPE OF WORKS

The controls specialist is to include for all necessary tools labour materials and

equipment to supply, install and fully commission the controls and power wiring the new equipment as shown on the contract drawings.

2.3.1 Provide new controls and wiring for :-

a) Boilers

b) pumps

2.3.2 Provide all necessary software for the control of plant.

2.3.3 Provide all temperature sensors and pockets, if found neccessary.

2.3.4 NA

2.3.5 Provide fire panel interface connections for emergency shut down of plant.

2.3.6 Final connections of all controls and power wiring from the control panel to all

mechanical services equipment.

2.3.7 Provide all necessary wiring diagrams.

2.3.8 Commission wiring and controls.

2.3.9 Prepare all necessary operating and maintenance manuals together with "as

installed" drawings.

2.3.10 Prepare all necessary builder's work details and drawings.

2.3.11 Liaise with other trades.

2.3.12 All necessary testing, balancing and commissioning.

2.3.13 Undertake user instruction.

3.1 	CONTROL REQUIREMENTS - HEATING AND VENTILATION

SYSTEMS

vi) Boilers

The gas fired boiler shall operate at the dictates of the heating system

enable signal, as directed by the optimiser or time switch override to maintain a

heating flow temperature of 82 o C, as measured by the sensor in the boiler

primary flow.

Boiler water circulation must be proven and maintained through the boiler

module prior to the boiler firing.

Boiler circulation must be maintained throughout the firing period and to disperse

heat within the boiler for a short period after the boiler has been switched off. A

temperature sensor in the flow and return connection from each boiler shall

monitor the flow through the boiler

vii) Boiler Control

The  boiler shall modulate  to maintain the set point temperature of 82 o C in the

boiler primary flow header.

viii) 	Boiler Fault Control

The boiler shall be give indication of fault condition via the Siemens controller.

a) Heating System High Temperature

Should the common boiler flow temperature exceed its set point by + 4 o C, a

category 4 critical alarms shall be raised and all boilers shall be disabled.  The

heating pumps shall remain open and heating pumps shall continue to operate to

dissipate heat.

b) Heating System Low Temperature

Should the common boiler flow temperature be less than its set point by - 13 o C

during occupancy hours, a category 2 alarm shall be raised.

(a) Power supply to control panels

(b) Controls and wiring to the building

4.2 	GENERAL

The components and installation shall comply with the recommendations of :-

(a)  	The IEE Wiring Regulations for the Electrical Installations 17th Edition

(BS7671)

(b)  	Current British Standards Specification and Codes of Practise

(i)  	The Electricity Act

(ii)  	The Electricity Supply Regulations

(iii)  	The Factories Act

(iv)  	The Building Regulations

4.3 	INCOMING SUPPLY

The electrical sub contractor shall provide a power supply local to the control

panel. All controls.

4.4      NOT USED

4.5 	FIRE ALARM

The fire alarm installation shall be retained to serve the new control

panel.

4.6 	EARTHING

Supplementary bonding conductors shall be provided and connected from

exposed conductive parts to all extraneous conductive metalwork and shall comply

with the IEE Wiring Regulations 413-02 & 547-03. Wherever possible

supplementary bonding shall be mechanically protected.

4.7 	CABLE TRAY

(a) Perforated cable trays for widths up to 300mm shall be manufactured from 16

s.w.g. mild steel and from 14 s.w.g. mild steel for widths greater than 300mm.  All

cable trays shall be galvanised finished unless otherwise specified in the General

(b) The minimum width of cable tray shall be 75mm but in all cases the width shall

be 25mm greater than necessary for the cables being installed therein.

(c) Where changes in level or direction of trays runs occur, the manufacturer's

preformed bends shall be used as far as practicable.  Each length shall be bonded

to give earthy continuity throughout the entire length.

(d) Care should be taken to avoid damage to the galvanised finish covering of the

cable tray; all nuts and bolts through the tray shall be fitted with washers.

(e) The cable tray, together with any necessary mild steel brackets, etc. required to

support the tray, shall be supplied and installed by the Contractor, the tray shall be

fixed at intervals of not greater than 900mm, joins between sections shall be

smooth.  The brackets supporting the cable tray shall be painted, to prevent

rusting, before the erection of same.

No fixing materials are to be used that will set up chemical action with the

galvanising of the tray or corrosion thereof.

(f) The cables shall be secured to the tray by multiple clips, the tray being of

adequate width for disposing the cables at single depth with a width allowance of

25% for additional cables.

4.8 	STEEL CONDUITS AND CONDUIT FITTINGS

(a) 	General

All rigid conduits and conduit fittings used throughout the installation shall be in

accordance with BS 31 and BS 4568.  All flexible conduits shall comply with BS

731.

(b) Conduit

The conduit shall be of heavy gauge screwed, welded steel manufacture.  Where

installed internally, the conduit and conduit fittings shall be black enamelled, but

where installed externally or otherwise specified shall be galvanised by the hot

process both inside and out.

(c) Flexible Conduit

Where flexible conduits are to be used, at motor terminal boxes, etc., they shall be

complete with brass conduit adaptors securely attached by soldering or other

approved means, and suitable bending terminals to be provided at point of flexible

conduit termination.  All flexible conduits shall be sheathed with black PVC

compound.

(d) Conduit Fittings

The conduit boxes shall be of malleable iron, screwed, circular type, with entry

spouts suitable for the type of fixing saddle used For sunk work, the ceiling point

boxes shall be of the circular type medium size (64mm dia. x 32mm deep) and

shall not have more than three entry ways.

All conduit fittings not carrying lighting or other fittings are to be supplied with

suitable cast iron covers, securely fixed in position with brass round-head screws,

No solid or inspection elbows, tees or bends may be installed without the

necessary instruction in writing from the Engineer.

All adaptable boxes are to be constructed of cast iron and must be of suitable size

to avoid undue packing of cables.  A minimum space of 15mm must be left

between all conduit holes.

For sunken work, brass compression washers shall be used with all adaptable and

'looping-in' boxes, together with conduit couplings and brass smooth bore male

thread bushed to ensure rigid connection and metallic continuity of the conduit

system.

Conduit boxes from which conduit suspended lighting fittings are to be suspended

shall be fitted with ball and socket cover plate.

(e) 	Draw-in Boxes

Draw-in boxes or through boxes must be provided to give access to all conduits for

the drawing-in or out of any cable after the installation is completed.  The draw-in

boxes must be of ample size to enable the cables to be neatly diverted from one

conduit to another without undue cramping.  Overlapping cover plates shall be

provided.

(f) 	Fixings

All saddles for surface work shall be of the single unit distance pattern, galvanised

where required.

All screws for galvanised conduit and fittings shall be carried out using either

serialised steel or brass as required.

4.9 	ISOLATORS

Isolators shall comply with the requirements of BS: 5419 1977 and be of the

cubicle or surface pattern type as detailed on the drawings.

Isolating switches shall be 500v pattern. Switchblades shall be mounted on a bar

of solid insulation material, this being actuated by a quick make or break

movement, the spring being in tension or compression only during the operation of

making or breaking contact.

Switch cases shall be either sheet steel or high impact plastic with hinged dust

tight lid fully interlocking to prevent opening or closing the cover in any position

other then off.

Isolators for motors, special circuits, etc., to be of the requisite number of poles or

rated capacity as specified for the equipment.

All isolators shall be of the type capable of padlocking in the off position.

5.0 	MOTOR CONTROL PANELS (MCP'S

10.0 CONTROLS

10.1 MOTOR CONTROLS

Controls plant room :-

The following equipment shall be supplied, fitted and wired.

Per Boiler x 4

1No 5 amp SP&N contactors

1No On/ off/Auto

HRC Fuses

Per Boiler primary pump x 4

1 No 15 Amps SP&N starters

HRC Fuses

Secondary Heating  Pump x 2 dual head

2 No XX kW starters SP&N

2No On/Off/auto switches

HRC fuses

10.5 Pressure differential valves…existing mechanical

10.6 Three port valve… existing

10.7 Emergency Gas solenoid existing …

All existing control equipment shall  be retained and remain in operation in accord with 	their original use.

Y

General engineering services

Pipelines Y10

Y10

Pipelines

Pipelines Y10

Y10 Pipelines

To be read with Preliminaries/ General conditions.

TYPES OF PIPELINE

110	STEEL PIPELINES	FOR LOW TEMPERATURE HOT WATER HEATING

SYSTEMS

•	 Thickness series for tubes to BS 1387: Heavy.

•	 Quality for tubes to BS EN 10216-1 and BS EN 10217-1: TR1.

•	 Finish: Varnish.

•	 Jointing method:

- Permanently concealed: Welded class 1.

- Accessible: Screwed up to and including 50 mm.

115	BELOW GROUND HEATING PIPES (BLOCK 10)-

-Manufacturer Duratan or similar up to 100mm NB

-Type: Pipe in pipe

-Pre insulated with phenoloic foam and vapour seal.

-Leak detection

-Plastic encapsulated pipes and heat sealed joints

-Provide identification slabs along route.

120A	COPPER PIPELINES FOR COLD WATER SUPPLY SYSTEMS.

•	 Standard: To BS EN 1057.

•	 Grade: R250.

Finish: Plain.

Jointing method:

- Permanently concealed: Brazed.

- Accessible: Capillary up to 67 mm for pressure up to 6 bar and 110?C.

130	PLASTICS PIPELINESFOR COLD WATER SUPPLY SYSTEMS

•	 Manufacturer: Contractor's choice.

- Product reference: Submit proposals.

Tube: PE to BS EN 1555-2.

- Classification to BS EN ISO 15874, BS EN ISO 15875, BS EN ISO 15876 or

BS EN ISO 15877: Submit proposals.

- Classification to BS 7291: Submit proposals.

•	 Colour: Blue.

•	 Jointing method: Electrofusion.

•	 Fittings: PE for water supply.

Pipelines Y10

130A	PLASTICS PIPELINESFOR GAS SUPPLY SYSTEMS

•	 Manufacturer: Contractor's choice.

- Product reference: Submit proposals.

Tube: PE to BS EN 1555-2.

- Classification to BS EN ISO 15874, BS EN ISO 15875, BS EN ISO 15876 or

BS EN ISO 15877: Submit proposals.

- Classification to BS 7291: Submit proposals.

•	 Colour: Yellow.

•	 Jointing method: Electrofusion.

•	 Fittings: PE for gaseous fuels.

PRODUCTS

310	STEEL TUBES

•	<  150 mm: To BS 1387.

•	 > 150 mm: To BS EN 10216-1 and BS EN 10217-1.

320	JOINTING MATERIALS FOR STEEL TUBES

•	 Jointing compound: To BS 6956-5.

•	 PTFE tape: To BS EN 751-3.

•	 Flange jointing rings: To BS EN 1514-4.

•	 Elastomeric gaskets: To BS EN 681-1.

•	 Welding rods: To BS EN 12536.

330	FITTINGS FOR STEEL TUBES

•	 Malleable: To BS 143 and BS 1256.

•	 Flanged: To BS EN 1092-1.

•	 Welded: To BS 1965-1 or BS EN 10253-1.

•	 Mechanical couplings: Manufacturer's standard.

340	COPPER TUBES

•	 Standard: To BS EN 1057.

- Buried R220.

- Above ground R250.

345	COPPER TUBES

•	 Standard: To BS EN 13348.

-  	Up to 54 mm R250.

76 mm and above R290.

350	JOINTING MATERIALS FOR COPPER TUBES

•	 Solder for capillary fittings: To BS EN 29453.

•	 Lead free solder for capillary fittings: To BS EN 29453.

•	 Brazing filling: To BS EN 1044.

•	 Flange jointing rings: To BS EN 1514-4.

360	FITTINGS FOR COPPER TUBES

•	 Capillary to BS EN 1254-1.

•	 Compression to BS EN 1254-2.

•	 Flanges to BS EN 1092-3.

Pipelines Y10

370	PLASTICS TUBES

•	 Chlorinated polyvinylchloride (PVC-C): To BS EN ISO 15877-2.

•	 Polybutylene (PB): To BS 7291-2 or BS EN ISO 15876-2.

•	 Polyethylene for gaseous fuels (PE): To BS EN 1555-2.

•	 Polyethylene for water supply (PE): To BS EN 12201-2.

•	 Cross linked polyethylene (PE-X):  To BS 7291-3 or BS EN ISO 15875-2.

•	 Polypropylene (PP): To BS 4991.

•	 Polypropylene for hot and cold water (PP): To BS EN ISO 15874-2.

•	 Unplasticised polyvinylchloride (PVC-U): To BS EN 1452-2.

380A	FITTINGS FOR PLASTICS TUBES

•	 Method:

- Electrofusion: To BS EN 12201-3.

•	 Fittings:

- PE for gaseous fuels: To BS EN 1555-3.

- PE for water supply: To BS EN 12201-3.

430	MASKING PLATES

•	 Material:

- All pipes except chromium plated copper: Plastic.

- Chromium plated copper pipes: Chromium plated.

•	 Type: Split.

EXECUTION

605	PIPELINES INSTALLATION GENERALLY

•	 Standard: In accordance with the latest edition of HVCA TR/20 'Installation and

testing of pipework systems'

- Part 1: Low temperature hot water heating.

- Part 2: Medium temperature hot water heating.

- Part 3: High temperature hot water heating.

- Part 4: Hot water service.

- Part 5: Cold water service.

- Part 6: Chilled water.

- Part 7: Condenser and cooling water.

- Part 8: Steam and condensate.

- Part 9: Natural gas.

- Part 10: Oil.

•	 Appearance: Install exposed pipe runs parallel with other pipe or service runs and

building structure, taking account of gradients for draining or venting. Set vertical

pipes plumb, or follow building line.

•	 Gradients: Install with gradients to allow drainage and air release.

•	 Air venting: Provide vents at high points.

•	 Draining: Provide drains at low points.

•	 Pipeline expansion and contraction: Arrange supports and fixings to accommodate

pipeline movement caused by the thermal changes. Allow for movement at branch

connections.

•	 Pipeline support: Arrange supports and accessories for equipment, appliances and

ancillary fitments in pipelines, so that no undue strain is imposed upon pipes.

Pipelines Y10

•	 Dirt, insects and rodents: Prevent ingress.

610	SPACING OF PIPELINES

•	 Minimum clearance between insulated pipelines and:

- Wall finish: 25 mm.

- Ceiling finish or soffit: 100 mm.

- Floor finish: 150 mm.

- Electrical services: 150 mm.

- Adjacent services: 100 mm.

- Uninsulated pipeline: 75 mm.

- Another insulated pipeline: 25 mm.

•	 Minimum clearance between uninsulated pipelines and:

- Wall finish: 25 mm.

- Ceiling finish or soffit: 100 mm.

- Floor finish: 150 mm.

- Electrical services: 150 mm.

- Adjacent services: 150 mm.

- Another uninsulated pipeline: 25 mm.

620	PIPELINE SUPPORTS	Pipes

•	 Type: Submit proposals.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

- Material: Brass.

621	PIPELINE SUPPORT BRACKETS

•	 Type: Submit proposals.

•	 Finish: Match pipeline supports.

625	PIPELINE FITTINGS

•	 Reductions and enlargements:

- On horizontal pipeline runs: Eccentric.

- On vertical pipeline runs: Concentric.

•	 Bushes: Use only at radiators.

•	 Square tees: Provide at vent and drain points.

•	 Square elbows: Do not use.

•	 Fabricated junctions and fittings: Same material as the main pipeline.

•	 Demountable joints: Regularly spaced along pipeline runs and at items of

equipment.

630	PIPELINE SLEEVES

•	 Sleeves: Fit to pipes passing through building fabric.

•	 Material: Match pipeline.

•	 Size: One or two sizes larger than pipe to allow clearance.

•	 Finish: Install sleeves flush with building finish. In areas where floors are washed

down, install protruding 100 mm above floor finish.

•	 Masking plates: Fit at visible penetrations, including through false ceilings of

occupied rooms.

635	DISSIMILAR METALS

•	 Electrolytic corrosion: Prevent.

Pipelines Y10

640	ANCHORS GENERALLY

•	 Design: To resist axial stress transmitted by flexure of horizontal and vertical pipe

runs, and loading on vertical pipes.

•	 Fixings: Provide associated backing plates, nuts, washers and bolts for attachment

to, or building into building structure.

•	 Building structure: Suitable for transmitted stress.

650	ANCHORS FOR COPPER PIPES

•	 Anchor: Two flanges fixed to copper female adaptors.

•	 Anchor fixing: Bolted to building structure.

•	 Pipe restraints: Saddle clamps.

660	SLIDE GUIDES

•	 Expansion and contraction: Direct movement from pipe anchor points towards

loops, bellows or flexible inserts.

•	 Thrust: Linear relative to the axis of pipe.

•	 Friction: Apply a friction reducing material between metal faces subjected to

movement.

665	WELDING STEEL PIPEWORK GENERALLY

•	 Class 1 welds: To BS 1821 and BS 2633.

•	 Class 2 welds: To BS 2640 and BS 2971.

•	 Competence: Use skilled operatives in possession of a current Certificate of

Competence appropriate to type and class of work.

- Evidence: Submit certificate of competence.

•	 Marking: Mark each weld to identify operative.

•	 Specimen welds: Submit specimen welds, representative of joints and conditions

of site welding.

- Quantity per operative: 10%.

•	 Non-destructive tests: Approximately 10% of butt weld joints and 5% of other joints.

•	 Painting: Wire brush and paint welds with red oxide paint when complete.

670	FLANGED JOINTS IN STEEL PIPES

•	 Preparation:

- Flange mating faces: Parallel.

- Flange peripheries: Flush with each other.

- Bolt holes: Align correctly.

•	 Welded flanges: Weld neck and bore of 'slip on' flanges. Butt weld neck of welding

neck flanges.

•	 Screwed flanges: Apply jointing materials. Screw on flange. Expand tube into

flange.

•	 Making and sealing: Insert jointing between flange mating faces. Tighten joint

equally all round.

675	SCREWED JOINTS IN STEEL PIPES

•	 Preparation of plain ends: Cut square. Ream out bore. Screw, taper thread.

•	 Making and sealing: Coat male pipe threads with jointing compound and hemp, or

PTFE tape on small sizes. Immediately after connect with female end of socket or

fitting, and tighten. Remove coating intruding into pipe. Leave joint clean.

Pipelines Y10

685	BRONZE WELDED JOINTS IN COPPER PIPES

•	 Preparation, making and sealing: To BS 1724.

•	 Filler rod: Not subject to dezincification.

690	BRAZED JOINTS IN COPPER AND COPPER ALLOY PIPES

•	 Preparation, marking and sealing: In accordance with BS EN 14324.

•	 Brazing alloy filler: Silver.

700	CAPILLARY JOINTS IN COPPER PIPES

•	 Standard: To BS EN 1254-1.

•	 Preparation: Cut square and deburr. Clean plain ends using fine steel wool.

•	 Making and sealing: Do not use excess flux. Make joint. Clean off traces of flux

when completed.

710	COMPRESSION JOINTS IN COPPER PIPES

•	 Standard: To BS EN 1254-2.

•	 Preparation: Cut square and deburr.

•	 Making and sealing:

- Type A: Compress ring onto the wall of the tube.

- Type B: Compress the formed portion of the tube against the formed end of the

fitting.

750	FUSION JOINTS IN POLYETHYLENE PIPES

•	 Preparation: Cut plain ends square. Form pipe ends for socket type joints.

755	MECHANICAL FITTINGS FOR POLYETHYLENE PIPES

•	 Preparation: Cut plain ends square. Check wall thickness and pressure rating of

fitting.

765	PROTECTION OF UNDERGROUND PIPEWORK

•	 Protection: Apply an anticorrosive, non- cracking, non-hardening, waterproof

sealing tape.

•	 Application: After cleaning pipework wrap two layers contra wise spirally around the

pipe, with 50% minimum overlap.

770	PROTECTION OF BURIED PIPES

•	 Earth cover (minimum):

- Water pipework: 900 mm, 1200 mm maximum.

- Fuel oil and gas: 500 mm.

- Under roadways: 900 mm.

•	 Marker tape: Provide to identify buried pipe services.

Pipeline ancillaries Y11

Y11

Pipeline ancillaries

Pipeline ancillaries Y11

Y11 Pipeline ancillaries

To be read with Preliminaries/ General conditions.

PRODUCTS

302A	CONNECTIONS FOR ANCILLARIES

•	 Capillary: To BS EN 1254-1.

•	 Flanged for copper alloy: To BS EN 1092-3.

•	 Threaded:

- Where pressure-tight joints are made on the threads: To BS 21 or BS EN

10226-1.

- Where pressure-tight joints are not made on the threads: To BS EN ISO 228-1

304	AUTOMATIC AIR VENTS Heating

•	 Type: Vertical inlet with integral lockshield isolating valve.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

•	 Material: Gunmetal.

•	 Connections: Threaded.

334	DOSING POTS	Heating

•	 Capacity: 18 L.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Material: Mild steel.

•	 Integral accessories :Tundish, vessel, inlet, outlet and drain valves.

336	DRAINING TAPS	All low points

•	 Standard: To BS 2879.

•	 Type: 1.

•	 Manufacturer: Hattersley, Crane, Pegler.

- Product reference: Contractor's choice.

•	 Material: Bronze.

•	 Connections: Threaded.

358	FLEXIBLE HOSES	Connections to local pressurisation set valves

•	 Type: Stainless steel braided.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

•	 Material: Stainless steel 1.44401 (316).

•	 Connections:

- Rubber cored: Full male union.

- Stainless steel: Fixed flange.

Pipeline ancillaries Y11

362A	GATE VALVES

VALVES AND COCKS

A. 	Heating main isolating valves for boilers, calorifiers, indirect cylinders

and circulating pumps for sizes 65mm to 300mm inclusive

Crane Reference  		F624

Hattersley Reference  		970

Overntrop Reference  		104 80

B. 	As A above for sizes up to and including 50mm inclusive:

Crane reference  		D171

Hattersley Reference  		100

Oventrop Reference  		107 90

C. 	All other heating isolating valves within boiler house or plant rooms

for 65mm and above:

Crane Reference  		F621

Hattersley Reference  		950

Oventrop Reference  		104 60

D. 	As C above for sizes up to and including 50mm inclusive:

Crane Reference  		D171

Hattersley Reference  		100

Oventrop Reference  		107 90

E. 	HWS and TCWS for sizes 65mm and above:

Crane Reference  		F624

Hattersley Reference  		M599 PN16

Oventrop Reference  		104 80

F. 	HWS and TCWS for sizes up to and including 50mm inclusive:

Crane Reference  		D171(T) / (LS)

Hattersley Reference  		100 (CT) / (CLS)

Oventrop Reference  		107 91 / 107 92

G. 	LTH Heating Circuits

Crane Reference  		D171T

Hattersley Reference  		100(T)

Oventrop Reference  		107 91

H. 	LTHW Heating Circuits Regulation

Crane Reference  		D931 up to 50mm: DM930 65mm and over OR D921

+ D901 FMD up to 50mm: DM940 65mm and over.

Hattersley Reference  		1700 up to 50mm: M737 65mm and over OR

1432 + 1000(C) up to 50mm: M733DR + M2000 65mm and over.

Oventrop Reference  		106 02 up to 50mm: 106 26 65mm or over OR

106 01 + 106 72 up to 50mm: 106 72 + 106 07 + 104 50 65mm and over.

I. 	Radiators (return Pipes), Fan assisted convectors, Natural convectors,

unit heaters and Heating coils:

Crane Reference  		D880 POL, D890 POL, D881 POL or D891 POL

Hattersley Reference  		2386, 2407, 2386LS or 2407LS

Pipeline ancillaries Y11

Oventrop Reference  		119 00, 119 01, 109 06 or 109 07 (Radiators)

Danfoss Reference  		RLV-S range 15 or 20 angle or straight pattern

(Radiators)

Hertz Reference  		HERZ-RL-5 return valves with pre-setting (Radiators)

J. 	Thermostatic radiator valves (flow pipes all Radiators):

Oventrop Reference  		Angled Pattern / Straight Pattern Series AZ

both single and two pipe systems with Fixed sensing head Uni-LGH + Reinforcing

Cap OR  		Fixed head remote sensor Uni-LGH remote sensor +

reinforcing cap OR Remote adjustable sensor Uni-LGH with remote control.

Danfoss Reference  		Angled Pattern / Straight Pattern / Straight Pattern

two pipe systems RA-FN one pipe system RA-G. Both valve types with Fixed

sensing  		head RA2920 OR Fixed head remote sensor RA2922 OR

Remote adjustable sensor RA5062.

Herz Valves Reference  		Angled Pattern two pipe system Herz 7724:

one pipe system Herz 7724E. Straight Pattern two pipe system Herz 7723: one

pipe system  		Herz 7723E. All valve types with Fixed sensing head 9860

OR Fixed head remote sensor 7430 OR Remote adjustable sensor 7330

K. 	Pipeline Strainers:

Crane Reference  		D297 or FM 276

Hattersley Reference  		807 or 810

Oventrop Reference  		112 00 or 112 20

L. 	Fire mains (hose reel supplies) and boosted pressure CWS:

Crane Reference  		F624

Hattersley Reference  		M598 PN16

Oventrop Reference  		104 80

M. 	Gas service for 125mm (5") and above:

Crane Reference  		F611

Hattersley Reference  		201MG with sealing compound No.17

Oventrop Reference  		104 81 (65mm and above): 104 61

N. 	Gas Service for up to and including 100mm (4")

Crane Reference  		D191

Hattersley Reference  		100YL (50mm): 201MG with sealing

compound No.17

Oventrop Reference  		301 64 (up to 50mm)

O. 	Safety Valves:

Nabic Manufacture only 542 (Open Systems): 500 (Closed Systems)

P. 	3-Way vent cocks:

Crane Reference  		D351

Hattersley Reference  		85

Q. 	Stopcocks on internal MCWS:

Yorkshire IMI Manufacture only YP 508 DZR: YP514 DZR

R. 	Stopcocks on external MCWS:

Pipeline ancillaries Y11

Yorkshire IMI Manufacture only YP 159 with turnkey.

S.  	Drain Cocks:

Crane Reference  		D340

Hattersley Reference  		371

Oventrop Reference  		103 35

T. 	Check valves for sizes up to and including 50mm:

Crane Reference  		D138: D140

Hattersley Reference  		47

Oventrop Reference  		107 50

U. 	Check valves for sizes up to 65mm and over:

Crane Reference  		For Heating FM469 for HWS FM492

Hattersley Reference  		For Heating M651 For HWS 5870

Oventrop Reference  		107 30

V. 	Pressure Reducing Valve:

Arrow Valves Reference Pressure Reducing valve 1310

RWC Reference315 Series Dial-up pressure reducing valve + pressure gauge.

W. 	Reduced Pressure Zone (RPZ) Valve:

Arrow Valves RPZ (BA) Option F (isolating valve, semi-automatic strainer, non-

return valve, RPZ valve and isolating valve). Installation of this valve should be

registered with the local water Authority. The valve shall be fully commissioned

prior to handover and the certificate included in the project O&M manual.

374	GAUGES, PRESSURE AND ALTITUDE Heating and Water

•	 Standard: To BS EN 837.

•	 Diameter: 100 mm.

•	 Manufacturer: Stewart -Buchanan Gauges Ltd 01236 821533.

- Product reference: Submit proposals.

•	 Case: Black steel.

•	 Connections: 'U' pattern siphon and gauge cock.

376	GAUGES, TEMPERATURE

Heating and Water.

•	 Standard: To BS EN 13190.

•	 Type: Bi-metallic.

•	 Manufacturer: [Stewart -Buchanan Gauges Ltd 01236 821533.

-  	Product reference: Submit proposals .

•	 Case: Brass .

•	 Connections: Straight stem .

•	 Integral accessories: 100 mm immersion length pocket.

400	TEST POINTS	Heating and DHW secondary return pumps

•	 Type: Self sealing.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Material: Brass.

•	 Connections: 6 mm (¼ inch) standard length.

Pipeline ancillaries Y11

410	TUNDISHES Condensate

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

•	 Material: Copper sheet.

•	 Connections: Diameter to suit drain line.

FABRICATION

510	CONTRACTOR FABRICATED ANCILLARIES

•	 Proposals: Submit.

•	 Content: Include the following:

- Overall dimensions.

- Shop fabrication drawings.

520	EXPANSION LOOPS, COPPERGENERALLY

•	 Standard: To BS EN 1057.

•	 Type: Formed bends from single pipe length.

EXECUTION

610	INSTALLATION OF VALVES GENERALLY

•	 Installation: In accordance with BS 6683.

•	 Location: As shown on drawings.

•	 Isolation and regulation valves: Provide at equipment and on sub circuits.

•	 Access: Locate valves so they can be readily operated and maintained. Locate

next to equipment which is to be isolated.

•	 Connection to pipework: Fit with joints that suit the pipe material.

620	INSTALLATION OF DOUBLE REGULATING VALVES

•	 Locations: Provide10 diameters of straight pipe upstream of valve and 5 diameters

downstream.

630	INSTALLATION OF THERMOSTATIC RADIATOR VALVES

•	 Locations: In areas which represent the space temperature, e.g. not behind

curtains or enclosed in heating or radiator panels.

640	INSTALLATION OF MEASUREMENT VALVES

•	 Locations: Provide straight length of pipe upstream and downstream.

645	INSTALLATION OF COMBINED AIR AND DIRT SEPARATORS

•	 Locations: Fit with dirt drain at lowest point for removing dirt that sinks.

650	INSTALLATION OF CONTROL COMPONENTS

•	 Locations: As shown on drawings.

•	 Insulation: Submit details of proposed insulation method where control

components are on insulated pipelines.

•	 Supports: Do not strain components.

•	 Access: Adequate for operation and maintenance.

660	INSTALLATION OF VENT COCKS

•	 Discharge pipes: Provide at outlets of vent cocks.

Pipeline ancillaries Y11

670	VALVE STUFFING BOXES

•	 Adjustment: Carry out at normal plant operating temperature and pressure. Do not

impair valve action, e.g. by over-tightening.

680	INSTALLATION OF DISCHARGE CONNECTIONS

•	 Safety and relief valves: Terminate at a safe discharge point.

•	 Vent cocks: Terminate 150 mm above floor level.

•	 Air bottles: Terminate with air cock or needle valve in a convenient position.

•	 Automatic air vents: Terminate over a suitable gully or drain line in a visible

location.

690	INSTALLATION OF EXPANSION LOOPS

•	 Location: Submit proposals.

•	 Stress: Minimize.

700	INSTALLATION OF EXPANSION COMPENSATORS

•	 Location: As per drawings.

•	 Anchors and guides: Locate to contain movement and resist maximum imposed

loads.

710	INSTALLATION OF FLEXIBLE CONNECTIONS

•	 Location: Close to the source of vibration.

COMPLETION

910	VALVE TESTS

•	 Standard: To BS EN 12266-1.

920	KEYS

•	 Tee handled short shank keys: Supply for valve spindle shanks.

- Number: 2.

•	 Lever pattern keys: Supply for drain cocks.

- Number: 2.

930	HOSE UNIONS

•	 Spares: Supply for drain cocks.

- Number: 2.

Mechanical cleaning and

chemical treatment Y12

Y12

Mechanical cleaning and chemical treatment

Mechanical cleaning and

chemical treatment Y12

Y12 Mechanical cleaning and chemical treatment

To be read with Preliminaries/ General conditions.

EXECUTION

610	GENERALLY

•	 Water analysis: Analyse water samples before treatment.

•	 Preliminary checks: Before cleaning or chemical treatment, complete pressure

tests, pre- commissioning and commissioning.

•	 Disposal of waste: Neutralize waste products and dispose to drain.

620	FLUSHING OF HOT AND COLD WATER SYSTEMS…NA

•	 Standard: To BS 6700.

•	 Installation checks: Thoroughly inspect pipework.

•	 Drainage: Provide adequate drainage, preferably direct to manhole.

630	FLUSHING OF HEATING AND CHILLED WATER SYSTEMS…NA

•	 : In accordance with BSRIA application guide 1/2001.

•	 Installation checks: Thoroughly inspect pipework.

•	 Drainage: Provide adequate drainage, preferably direct to manhole.

640	PURGING GAS PIPEWORK

•	 Standards: To IGE/UP/1 and IGE/UP/1A.

650	WATER TREATMENT FOR HOT AND COLD WATER SYSTEMS…NA

•	 Standard: To BS 6700.

•	 Samples for analysis: Provide after flushing.

660	WATER TREATMENT FOR HEATING SYSTEMS…

•	 Treatment: In accordance with BSRIA AG 2/93.

•	 Chemicals:

- Corrosion inhibitors: Submit proposals.

- pH control: Submit proposals.

- Scale inhibitors: Submit proposals.

690	CLEANING OF VENTILATION SYSTEMS…NA

•	 Cleaning: In accordance with HVCA DW/TM2 and TR/17 and CIBSE Guide B3.

•	 Level of cleanliness: Basic.

•	 Cleaning process: Dry cleaning.

COMPLETION

910	WATER QUALITY TESTS

•	 Standard: To BS 6700.

•	 Samples: Submit samples for bacteriological analysis.

- Water temperature: Record the temperature of the water at each sampling

point, at the time of taking the sample.

•	 Test results: Submit.

Mechanical cleaning and

chemical treatment Y12

920	VERIFICATION OF CLEANLINESS OF VENTILATION SYSTEMS…NA

•	 Verification: In accordance with HVCA TR/17.

•	 Method: Vacuum test.

•	 Completion report: Submit.

Pumps Y20

Y20

Pumps

Pumps Y20

Y20 Pumps…

To be read with Preliminaries/ General conditions

PRODUCTS…

310	PUMP SELECTION

•	 General: Select pump at or near the most efficient part of the performance curve

for required duty.

320	PUMPS GENERALLY

•	 General safety standards: To BS EN 809.

•	 Electrical safety: To BS EN 60335-2-51.

•	 Dynamic balance: To BS ISO 2953.

•	 Test standards: To BS EN ISO 9906 and in accordance with BS EN ISO 5198.

•	 Belts and pulleys: To BS 3790.

•	 Rotodynamic pumps: To BS EN 1151.

•	 Connections:

- Flanged, copper alloy and composite: To BS EN 1092-3.

- Flanged, cast iron: To BS EN 1092-2.

- Threaded: To BS 21 or BS EN 10226-1.

330 CLOSE COUPLED IN LINE PUMPS FOR HEATING SYSTEM

•	 Arrangement: Pipeline mounted Single Boiler Primary Pumps ( shunt ).

•	 Manufacturer: Grundfos.

- Product reference: Magna 1.

•	 Flow rate: As Pump details on the drawings.

•	 System resistance: As Pump indicated on the drawings.

•	 Motor and impeller speed (maximum): 1500 rpm.

•	 Electrical supply: single phase.

•	 Speed control: Variable.

•	 Casing material:

•	 Accessories: Matching flanges.

•	 Connections: Flanged.

360B	CLOSE COUPLED IN LINE PUMPS FOR HEATING SYSTEM

•	 Arrangement: Pipeline mounted Single Secondary Pump.

•	 Manufacturer: Grundfos.

- Product reference: Magna 1 x 2No

•	 Flow rate: As Pump details on the drawings.

•	 System resistance:. As Pump details on the drawings

•	 Motor and impeller speed (maximum): 1500 rpm.

•	 Electrical supply: Single phase.

•	 Speed control: Variable.

•	 Casing material:

•	 Accessories: Matching flanges.

•	 Connections: Flanged.

Pumps Y20

EXECUTION

610	INSTALLATION OF PUMPS GENERALLY

•	 Pipeline connections: Arrange to prevent transmission of pipeline forces to pump

casing.

•	 Pressure gauge tappings: Provide in flow and return pipeline connections and in

common suction and delivery pipeline.

•	 Brackets: Support pipeline mounted pumps on purpose made brackets lined with

vibration absorbent material.

•	 Alignment: Align and balance to minimize vibration.

•	 Belt tension: Correctly tension drive belts.

•	 Access: Provide adequate space for service and maintenance.

•	 Identification plate: Engrave showing

- manufacturer's name and address;

- serial number;

- duty and maximum head;

- speed; and

- electrical loading.

620	VIBRATION ISOLATION

•	 Flexible connections: As section Y11.

•	 Anti-vibration mountings: As section Y31.

630	INSTALLING PRESSURIZATION UNITS

•	 Location of expansion vessel: In the system return pipeline close to the heat

source or chilled water unit.

COMPLETION

920	COMMISSIONING

•	 In-line pumps: Change impeller if necessary.

•	 Test certificates and performance curves: Submit.

Mechanical thermal insulation

Y30

Y30

Mechanical thermal insulation

Mechanical thermal insulation

Y30

Y30 Mechanical thermal insulation

To be read with Preliminaries/ General conditions.

PRODUCTS

330	MINERAL FIBRE PIPE INSULATION

•	 Standard: To BS 3958-4.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Thermal conductivity: 0.044 W/m·K.

340	MINERAL FIBRE DUCT INSULATION

•	 Standard: To BS 3958-5.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Thermal conductivity: 0.044 W/m·K.

360	PHENOLIC FOAM INSULATION

•	 Standard: To BS EN 13166.

•	 Manufacturer: Kool Therm.

- Product reference: Submit proposals.

•	 Thermal conductivity: 0.025 W/m·K.

370	INSULATION THICKNESSES

•	 Determination: Where thickness is not given, calculate to BS 5422.

380	VAPOUR BARRIER PERMEANCE

•	 Standard: To BS 3177.

•	 Vapour permeance (maximum):

- Cold water pipework: 0.05 g/s·MN.

- Chilled water pipework: 0.015 g/s·MN.

- Refrigeration pipework: 0.010 g/s·MN.

400	INSULATION FOR HOT WATER PIPEWORK

•	 Insulation materials: As Mechanical thermal insulation schedule.

•	 Insulation thickness: As Pipework insulation thickness schedule.

410	INSULATION FOR COLD WATER PIPEWORK TO PREVENT CONDENSATION

•	 Insulation materials: To condensate.

•	 Insulation thickness: As Pipework insulation thickness schedule.

420	INSULATION FOR HEATING PIPEWORK

•	 Insulation materials: As Mechanical thermal insulation schedule.

•	 Insulation thickness: As Pipework insulation thickness schedule.

460	INSULATION FOR HEAT EXCHANGERS, CYLINDERS AND BUFFER VESSELS

•	 Insulation materials: As Mechanical thermal insulation schedule.

•	 Accessories to be insulated: Removable access covers and Cover plates..

Mechanical thermal insulation

Y30

480	INSULATION FOR VALVES AND FLANGES

•	 Insulation materials: Valve muffs…tie on type with 40mm mineral wool insulation and wipe 		clean surfaces.

495	INSULATION AT LOAD BEARING PIPE SUPPORTS

•	 Hot pipework temperatures up to 120°C: 300 mm length of high density phenolic

foam.

•	 Hot pipework temperatures above120°C: 300 mm length of calcium silicate.

•	 Cold pipework: 300 mm length of high density phenolic foam.

EXECUTION

610	INSTALLATION GENERALLY

•	 Timing: Insulate after installed system has been fully tested and joints proved

sound.

•	 Insulation: Do not enclose adjacent units together.

•	 Clearance: Maintain between pipes.

•	 Finish: Neatly finish joints, corners, edges and overlaps.

625	INSTALLATION OF FOIL FACED MINERAL FIBRE INSULATION ON PIPEWORK

•	 Joints: Close butt, seal with 50 mm wide class 0 tape on both longitudinal and

circumferential joints.

•	 At fittings: Mitre. Secure with tape.

•	 Vapour seal: Tape exposed insulation membrane. Seal vapour barrier at pipe

support with class 0 tape.

630	INSTALLATION OF NITRILE RUBBER INSULATION ON PIPEWORK

•	 Joints: Close butt, secure with adhesive.

•	 At fittings: Fabricate from mitre cut pieces. Secure with adhesive.

640	INSTALLATION OF PHENOLIC FOAM INSULATION ON PIPEWORK

•	 Joints: Close butt, seal with 50 mm wide class 0 tape on both longitudinal and

circumferential joints.

•	 At fittings: Mitre. Secure with tape.

•	 Vapour seal: Tape exposed insulation membrane. Seal vapour barrier at pipe

support with class 'O' tape.

660	INSTALLATION OF FOIL FACED MINERAL FIBRE INSULATION ON

DUCTWORK

•	 Fixing to underside of ducting: Self adhesive stick pins. Further support with 0.7–

1.0 x 50 mm mesh galvanized wire netting.

•	 Joints, pin penetrations, cut outs for test holes and supports: Seal with 100 mm

wide class 'O' foil tape.

690	INSTALLATION OF PHENOLIC FOAM INSULATION ON VESSELS

•	 Application: Install pre-formed segments or pre-slotted foil faced insulation around

the diameter of the vessel. Lay with staggered joints.

•	 Joints: Seal joints and gaps around protrusions with jointing compound.

•	 Finish: Secure with aluminium banding.

•	 Access: Allow for removal of access covers.

Mechanical thermal insulation

Y30

710	INSTALLATION OF POLYISOBUTYLENE (PIB) PROTECTION

•	 Thickness (minimum): 0.8 mm.

•	 Application: Wrap sheeting with 50 mm overlap. Solvent weld joints.

•	 Finish: Secure with aluminium banding.

720	INSTALLATION OF SHEET ALUMINIUM PROTECTION

•	 Application: Form sheet to fit circumference of insulation with 50 mm longitudinal

and circumferential overlaps. Secure overlaps with self tapping screws or rivets.

Seal joints with grey sealant.

•	 Expansion: Make provision.

730	INSTALLATION OF SHEET METAL PROTECTION

•	 Application: Form sheet to fit circumference of insulation with 50 mm longitudinal

and circumferential overlaps. Secure overlaps with self tapping screws or rivets.

•	 Expansion: Make provision.

740	INSTALLATION AT VALVES AND FLANGES

•	 Application: Do not obstruct removal of nuts and bolts, or operation of valves.

750	INSTALLATION AT LOADBEARING PIPEWORK SUPPORTS

•	 Application: Close butt to insulation.

•	 Joints: Seal with 100 mm wide class '0' foil tape.

•	 Sleeve: Provide sheet metal protection sleeve.

755	INSTALLATION AT NON-LOADBEARING PIPEWORK SUPPORTS

•	 Insulation: Carry through pipe support.

760	INSULATION NOT CARRIED THROUGH PIPEWORK SUPPORTS

•	 Insulation at supports: Provide aluminium end caps.

770	INSULATION CARRIED THROUGH DUCTWORK SUPPORTS

•	 High density phenolic foam: Close butt to insulation.

•	 Sleeve: Provide sheet metal protective sleeve.

800	VAPOUR BARRIERS

•	 Integrity: Maintain throughout.

Vibration isolating mountings

Y31

Y31

Vibration isolating mountings

Vibration isolating mountings

Y31

Y31 Vibration isolating mountings

PRODUCTS

310	MOUNTINGS GENERALLY

•	 Criteria: Ensure that vibration generated by the engineering services is not

transmitted to pipework, ductwork, the building and supporting structure.

•	 Overload capacity (minimum): 50%.

•	 Colour code: Identify for load and deflection rating.

•	 Marking: Label with load capacity.

360	FLEXIBLE HOSES	Pumps

•	 Type: Rubber.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

•	 Connections:

- Rubber cored:.

- Fixed flange.

EXECUTION

610	CAST IN SITU BASES

•	 Supported equipment: Arrange equipment on base to distribute load evenly.

COMPLETION

910	DOCUMENTATION

•	 Operation and maintenance instructions: Submit.

Mechanical plant and

equipment identification Y32

Y32

Mechanical plant and equipment identification

Mechanical plant and

equipment identification Y32

Y32 Mechanical plant and equipment identification

To be read with Preliminaries/ General conditions.

PRODUCTS

310	PLANT AND EQUIPMENT IDENTIFICATION LABELS

•	 Standard: To BS 1710.

•	 Type: Laminated plastics plates.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

•	 Information: Purpose and reference number.

320	VALVE IDENTIFICATION LABELS

•	 Standard: To BS 1710.

•	 Type: Metal plates.

•	 Manufacturer: Submit proposals.

- Product reference: Submit proposals.

•	 Information: Purpose and reference number.

•	 Colours: Basic and safety colour identification of associated system.

330	VALVE CHARTS AND SCHEMATICS

•	 Type: Plastic encapsulated.

EXECUTION

610	IDENTIFYING PIPEWORK

•	 Standards: To BS 1710.

•	 Identification type: Adhesive colour bands.

•	 Application of basic identification colour: Coloured bands as BS 1710 clause 3.3.

•	 Safety colour identification: On or next to the colour bands.

•	 Information: Colour bands as BS 1710 appendix D.

•	 Direction of flow: Indication arrow and the word FLOW or the letter F and

Indication arrow and the word RETURN or the letter R.

620	IDENTIFYING DUCTWORK

•	 Standard: To HVCA DW/144 appendix B.

•	 Identification type: Self-adhesive plastics or transfers.

•	 Direction of flow: Equilateral triangle, 150 mm length of side, with one apex

pointing in the direction of flow.

•	 Information: Space served by the duct and associated plant.

630	INSTALLING PLANT AND EQUIPMENT IDENTIFICATION

•	 Fixing: Plug and screw to wall.

•	 Location: On wall adjacent equipment.

640	INSTALLING VALVE IDENTIFICATION

•	 Fixing: Secure with metal chain.

Mechanical plant and

equipment identification Y32

650	INSTALLING VALVE CHARTS AND SCHEMATICS

•	 Fixing: Plug and screw to wall.

•	 Location: Plant room.

Mechanical testing and

commissioning Y50

Y50

Mechanical testing and commissioning

Mechanical testing and

commissioning Y50

Y50 Mechanical testing and commissioning

To be read with Preliminaries/ General conditions.

EXECUTION

610	GENERALLY

•	 Commissioning programme: Submit before commissioning commences.

- Notice: 7 days.

•	 Commissioning manager: Submit details.

620	GENERAL INSPECTION AND TESTING

•	 Inspection of joints: Cut out, cut open and inspect.

- Number of joints: 2.

•	 Safety precautions: In accordance with HSEGS4.

630	HYDRAULIC PRESSURE TESTING OF HOT AND COLD WATER SUPPLY

SYSTEMS

•	 Standard: To BS 6700.

•	 Notice  	1 week.

•	 Pressure: 2 times working pressure.

•	 Duration of test: 1 h.

640	HYDRAULIC PRESSURE TESTING OF NATURAL GAS SUPPLY SYSTEMS

•	 Standards: To BS EN 12327 and IGE/UP/1, 1Aand 4.

•	 Notice  	1 week.

•	 Pressure: 2 times working pressure.

•	 Duration of test: 1 h.

670	HYDRAULIC PRESSURE TESTING OF LOW TEMPERATURE HOT WATER

HEATING SYSTEMS

•	 Testing: In accordance with HVCA TR/6 Guide to good practice for site pressure

testing of pipework.

•	 Notice  	1 week.

•	 Pressure: 2 times working pressure.

•	 Duration of test: 1 h.

COMPLETION

910	COMMISSIONING OF HOT AND COLD WATER SUPPLY SYSTEMS

•	 Standard: In accordance with BSRIA AG 2/89 and CIBSE Commissioning Code W.

•Notice 1 week.

920	COMMISSIONING OF GAS SYSTEMS

•	 Standard: To BS EN 12327.

Mechanical testing and

commissioning Y50

• Notice  1 week.

930	COMMISSIONING OF HEATING SYSTEMS

•	 Standard: In accordance with BSRIA AG 2/89 and CIBSE Commissioning Code

W.

•	 Notice  	1 week.

940	COMMISSIONING OF BOILER PLANT

•	 Standard: In accordance with CIBSE Commissioning code B.

•	 Notice  	1 week.

980	COMMISSIONING OF CENTRAL CONTROLS AND BUILDING MANAGEMENT

SYSTEMS

•	 Standard: In accordance with CIBSE Commissioning Code C.

•	 Notice  	1 week.

985	PERFORMANCE TESTING

•	 General: Demonstrate the performance of the installations.

•	 Environmental tests: Carry out environmental testing. If necessary, use artificial

loads to simulate operating conditions.

•	 Recorders: Supply and maintain portable seven day space temperature and

relative humidity recorders, complete with charts.

- Number of recorders: 2.

- Duration of loan: 1 week.

•	 Reports: Submit.

990	INSPECTION AND TEST RECORDS

•	 Records for water systems: In accordance with BSRIA AG 2/89.

•	 Records for air systems: In accordance with BSRIA AG 3/89.

•	 Record sheets: Submit.

- Number of copies: 3.

995	DEMONSTRATIONS

•	 Running of plant: Run, maintain and supervise the installations under normal

working conditions.

- Duration: 1 week.

•	 Instruction: Instruct and demonstrate the purpose, function and operation of the

Installations to the clients representatives.

Conduit & trunking Y60

Y60

Conduit & trunking

Conduit & trunking Y60

Y60 Conduit & trunking

To be read with Preliminaries, General conditions.

GENERAL

110	CONDUIT AND TRUNKING GENERALLY

•	 Standard: To BS 7671.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturer's literature.

•	 Conduit and trunking sizes not stated: Submit proposals and calculations.

PRODUCTS

320	RIGID CONDUITGENERALLY

•	 Standard: To BS EN 50086-2-1 or BS EN 61386-21.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Material: Metal.

•	 Mechanical properties:

- Resistance to compression: Medium.

- Resistance to impact: Medium.

- Resistance to bending: Rigid.

- Tensile strength: Medium.

- Suspended load capacity: Medium.

•	 Temperature range:

- Lower temperature: -5°C.

- Upper temperature: 60°C.

•	 Electrical properties: With electrical insulating properties.

•	 Ingress protection to BS EN 60529: NA.

•	 Resistance against corrosion: Class 2, electro zinc plate.

•	 Resistance against flame propagation: Non flame propagating.

•	 Sizes (OD): 25 mm.

460	METALLIC CONDUIT FITTINGS

•	 Standards: To BS 50086-1 and BS 50086-2 or BS EN 61386-1 and BS EN 61386-

22.

•	 Manufacturer: Match conduit.

•	 Material: Steel.

•	 Conduit boxes: Fit covers of same material and finish as boxes.

•	 Plugs: Hexagonal malleable iron.

•	 Locknuts: Hexagonal malleable iron.

470	INSULATING CONDUIT FITTINGS

•	 Standards: To BS 50086-1 and BS 50086-2 or BS EN 61386-1 and BS EN 61386-

22.

•	 Manufacturer: Match conduit.

•	 Fittings: Heavy gauge, high impact rigid PVC-U fittings.

•	 Conduit boxes: Include brass earthing terminals.

Conduit & trunking Y60

EXECUTION

610	INSTALLING CONDUIT AND TRUNKING

•	 Standard: To BS 7671and in accordance with IEE Guidance note 1.

•	 Cable trunking: Provide when multiple conduits running in parallel exceed: 3.

•	 Preparation: Cut square.

- Burrs and sharp edges: Make smooth.

•	 Cross-sectional area: Maintain throughout the conduit and trunking length.

•	 Arrangement: Position vertically and horizontally in line with equipment served,

and parallel with building lines.

•	 Conduit in walls: Avoid concealed horizontal runs.

•	 Distance from other services running parallel (minimum):

- Generally: 150 mm.

- Above radiators: 1000 mm.

- Steam services: 600 mm.

•	 Fire barriers: Provide to maintain integrity of fire compartments.

•	 Rewireable installations: Enable rewiring from accessible boxes or accessories

only.

•	 Support: Independently fix and support conduit and trunking from building

structure.

•	 Cleaning: Clean insides of conduit and trunking before installing cables.

•	 Cabling: Install when conduit and trunking enclosure is complete.

•	 Submittals: Submit manufacturer's technical information and drawings showing the

proposed routes of conduit and trunking and the location of service outlets.

620	PROTECTION OF METALLIC CONDUIT AND TRUNKING

•	 Joints and ends: Remove grease, oil, dirt and rust before applying protective paint.

Paint immediately following installation.

•	 Protective paint: Compatible with conduit and trunking finish.

- Type: Galvanizing zinc rich paint, 2 coats.

Conduit & trunking Y60

630	INSTALLING CONDUIT GENERALLY

•	 Fixing: Fix securely. Fix boxes independently of conduit.

•	 Changes of direction: Conduit boxes or bends site formed by machine. Do not use

elbows, tees or inspection bends.

•	 Joints: Manufacturer's jointing fittings.

- Number of joints: Minimize.

- Lengths of conduit: Maximize.

- Open ends: Plug.

- At movement joints in structure: Manufactured expansion coupling. Install

adaptable boxes on both sides of joint at a maximum distance of 300 mm.

•	 Connections to boxes, trunking, equipment and accessories: Screwed couplings

with rubber bushes at open ends.

•	 Conduit boxes: Install flush with finished surfaces. Provide extension rings if

required.

- Fixing screws: Countersunk, or round-headed screws.

- Number of fixings (minimum): For conduit boxes use 2. Larger fittings use 4.

- Lids: Fasten with brass slot pan head screws.

•	 Rear outlet boxes: Locate where surface conduits pass through walls to external

equipment.

•	 Draw-in boxes:

- Spacing (maximum): 10 m.

- Number of bends between draw-in boxes (maximum): 2.

- Floors: Do not install draw-in boxes in floors.

•	 Suspended ceiling installations: Fasten outlet boxes to structure above ceiling.

640	INSTALLING METAL CONDUIT

•	 Fixings: Spacer bar saddle.

•	 Joints: Screwed.

•	 Threaded conduits: Tightly screw to ensure electrical continuity, with no thread

showing.

•	 Conduit connections to boxes and items of equipment, other than those with

threaded entries: Earthing coupling with male brass bush and protective

conductor.

680	CONDUIT CONNECTIONS TO EQUIPMENT

•	 Surface mounted equipment:

- Concealed conduit: Conceal the final connection.

- Exposed conduit: Contain the final connection from the conduit box within

flexible metal conduit.

•	 Equipment subject to vibration: Flexible metal conduit terminating in swivel

connectors.

- Length of conduit: Adequate for removal of equipment for maintenance.

•	 Connections to external equipment: PVC covered flexible metal conduit.

720	DRAINAGE OF CONDUIT AND TRUNKING

•	 Drainage outlets: Locate at lowest points in conduit and trunking installed

externally, and where condensation may occur.

740	CONDUIT AND TRUNKING ZONES

•	 Ceiling voids:

- Clear distance between underside of conduit and trunking and topside of ceiling

Conduit & trunking Y60

(minimum): 150 mm.

770	SUPPORTS AND FIXINGS

•	 Suspension systems: Proprietary, comprising channel sections with return lips and

accessories.

- Finish and colour: Match conduit or trunking as appropriate.

•	 Supports and fixings: Select to prevent deterioration by electrolytic action.

•	 Supports and fixings in locations where moisture may occur: Corrosion resistant.

COMPLETION

910	CLEANING

•	 Electrical equipment: Clean immediately before handover.

920	INSPECTION AND TESTING

•	 Standard: To BS 7671.

•	 Electrical properties: Measure electrical continuity and insulating properties of

conduit and trunking. Submit results.

930	DOCUMENTATION

•	 Drawings: Submit, showing the location of conduit, trunking and service outlets.

- Dimensions: Include sufficient to locate components accurately.

Cable supports Y63

Y63

Cable supports

Cable supports Y63

Y63 Cable supports

To be read with Preliminaries/ General conditions.

PRODUCTS

310	SELECTION OF CABLE SUPPORTS

•	 Standards: To BS 7671 and in accordance with IEE Guidance note 1.

•	 Proposals: Submit drawings, technical information, calculations and

manufacturer's literature.

•	 Sizes not stated: Submit proposals and calculations.

•	 Spare capacity: 20% free width.

320	CABLE BASKETS

FOR SUB-MAIN CABLING.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Material: Steel wire.

- Diameter: 4 mm.

•	 Coating material: Hot dip galvanized.

•	 Sizes:

- Width: 100 mm and 150 mm.

•	 Side height: 30 mm.

•	 Features:

- Segregation: Not required.

- Protective cover: Required.

330	CABLE LADDERS	FOR SUB-MAIN CABLING

•	 Standard: To BS EN 61537.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

•	 Material: Metal.

•	 Resistance against flame propagation: Non flame propagating.

•	 Electrical properties:

- Continuity characteristics: Contractor's choice.

•	 Conductivity characteristics: Contractor's choice.

•	 Coating material: Aluminium electroplated.

•	 Temperature properties for transport, storage, installation and application:

•	 Minimum: -5°C.

•	 Maximum: +90°C.

•	 Mechanical properties:

- Cable ladder free base area: Contractor's choice.

- Resistance to impact: Contractor's choice.

•	 Width: 100 mm and 200 mm.

•	 Features:

- Segregation: Not required.

- Protective cover: Required.

Cable supports Y63

350	CABLE SUPPORT COMPONENTS

•	 Components generally: Corrosion resistant where moisture may occur.

•	 Joints and expansion couplers: Use cable support manufacturer's products.

360	PROTECTIVE COVERS

•	 Type: Flanged.

- Profile: Peaked.

370	CABLE SUPPORT BRACKETS

•	 Standard: To BS 6946.

•	 Type: Contractor's choice.

•	 Finish: Match cable supports.

380	CABLE FASTENINGS

•	 Use and types:

- Sub main cables<95 mm²: Polyethylene one piece overlapping single fixing

clamps.

- Sub main cables >95 mm²: Aluminium two piece twin fixing clamps.

- Trefoil grouped sub main cables: Aluminium trefoil single or twin fixing clamps.

- Lighting final circuit cabling: Cable ties.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

390	CABLE TIES

•	 Type: Wrap around self locking releasable.

•	 Manufacturer: Contractor's choice.

- Product reference: Contractor's choice.

- Material: Nylon.

Cable supports Y63

EXECUTION

610	INSTALLING CABLE SUPPORTS

•	 Standards: To BS 7671and in accordance with IEE Guidance note 1.

•	 Preparation:

- Burrs and sharp edges: Make smooth.

- Cutting: Minimize. Cut square along an unperforated line. Make good edges.

- Treatment of cut surface: Extend 25 mm beyond the cut. Match finish of cable

supports.

•	 Width: Maintain throughout the cable support length.

•	 Access: Provide space around cable supports to permit access for installing and

maintaining cables.

•	 Joints and expansion couplers: Locate between the bracket support and the

quarter point.

- Number of joints: Minimize.

- Lengths of cable supports: Maximize.

- Ends: Blank with end plates

•	 Holes in cable supports for the passage of cables: Grommet.

•	 Fire barriers: Provide where required to maintain fire performance of fabric.

•	 Support: Independently fix and support from building structure.

- Clearance from building fabric (minimum): 20 mm.

- Proposals: Submit.

•	 Components: Avoid contact between dissimilar metals.

•	 Routing of cable supports: Submit drawings showing the proposed routes.

640	INSTALLING CABLE BASKET

•	 Joints:

- Cut: Adjacent cross basket wires.

- Earth conductors: Connect across joints.

•	 Accessories: Form on site and connect with basket manufacturer's coupling

components.

650	INSTALLING PROTECTIVE COVERS

•	 Location: Cables requiring mechanical protection.

660	CABLE INSTALLATION

•	 Cabling: Install when cable supports are complete.

•	 Preparation: Clear cable path of debris.

•	 Cable pulling: Submit method statement.

•	 Fastening: Secure cables, do not indent sheaths.

-  Spacing (maximum): 300 mm.

680	INSTALLING BRACKETS FOR CABLE SUPPORTS

•	 Suspensions: Threaded rod fixed to channel with shake proof washers and hex

nuts.

•	 Cable supports: Hold down with clamps and spring channel nuts.

690	CABLE SUPPORT ZONES

•	 Ceiling voids:

- Clear distance between underside of cable supports and brackets and topside

of ceiling (minimum): 150 mm.

Cable supports Y63

COMPLETION

910	INSPECTION AND TESTING

•	 Standard: To BS 7671.

•	 Electrical properties: Measure electrical continuity and insulating properties of

cable supports. Submit results.

Electrical accessories Y65

Y65

Electrical accessories

Electrical accessories Y65

Y65 Electrical accessories

To be read with Preliminaries/ General conditions.

PRODUCTS

310	PRODUCTS GENERALLY

•	 Standard: To BS 5733.

- Switches: To BS EN 60669-1.

340	LIGHT SWITCHES	GENERALLY.

•	 Application: Internal.

•	 Ingress protection to BS EN 60529: IP 67.

•	 Rating: 20 A.

•	 Actuating method: Standard rocker bar.

•	 Mounting: Surface.

•	 Poles: Double pole.

370	CABLE OUTLETSGENERALLY

•	 Standard: To BS 5733.

•	 Ingress protection to BS EN 60529: IP 4X.

•	 Flex outlet: Side entry.

EXECUTION

610	INSTALLING ELECTRICAL ACCESSORIES

•	 Standard: To BS 7671.

620	ARRANGEMENT

•	 Location: Coordinate with other wall or ceiling mounted equipment. Submit

proposals.

•	 Positioning: Accurate and square to vertical and horizontal axes.

•	 Alignment: Align adjacent accessories on the same vertical or horizontal axis.

•	 Fixing: Secure, plumb and level.

•	 Mounting heights (finished floor level to underside of accessory):

- Light switches: 1200 mm.

- Single voltage shaver outlets: 1200 mm.

- Shaver supply units: 1200 mm.

- Socket outlets: 450 mm.

- Fan isolators: Adjacent fan.

- Cooker control units: 200 mm above worktop.

- Cooker connection units: 600 mm.

•	 Separation distance between adjacent accessories: (minimum): 30 mm.

630	GRID SWITCH PLATES

•	 Spare modules: Provide blank inserts.

Electrical accessories Y65

640	INSTALLING LIGHT SWITCHES

•	 Multigang switches: Connect so that there is a logical relationship with luminaire

positions.

- Unused switch spaces: Fit with blanks.

- Segregation: Internally segregate each phase with phase barriers. Include

warning plates.

COMPLETION

910	FINAL FIX

•	 Accessory faceplates: Fit after completion of building painting.

920	SPARES

•	 Plugs (minimum): Supply 2 spare plugs for each socket outlet type.

MECHANICAL APPENDICES

| Mechanical thermal insulation schedule |  |  |  |  |  |  |  | Revision: | - |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Date: |  |
| Service | Material | Form | Temperature of contents (˚C) | External surface emissivity | Hot face temperature (˚C) | Ambient conditions (˚C) | Thickness (mm) | Finish | Protection |
| Hot water pipelines | Mineral fibre | Pipe section | 60 | n/a | n/a | n/a | As per British Standard | Aluminium foil | Plant rooms Isogenopak |
| Vessels and flat surfaces |  |  | 60 | n/a | n/a | n/a | As per British Standard | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Cold water pipelines | Mineral fibre | Pipe section | 0 | n/a | n/a | 25 | As per British Standard | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Vessels and flat surfaces |  |  |  | n/a | n/a | 25 | As per British Standard | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Heating pipelines | Mineral fibre | Pipe section | n/a | n/a |  | n/a | As per British Standard | Aluminium foil | Isogenopak Plant rooms |
| Vessels and flat surfaces |  |  | n/a | n/a |  | n/a | As per British Standard | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Chilled water pipelines to prevent condensation | Mineral fibre | Pipe section | 5 | n/a | n/a | 25 | As per British Standard | Aluminium foil | Sheet aluminium casing Boiler rooms |

| Chilled water pipelines to control heat gain | Mineral fibre |  | Pipe section |  | 5 |  | n/a | n/a |  |  | n/a | As per British Standard |  |  | Aluminium foil | Sheet aluminium casing Boiler rooms |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vessels and flat surfaces | Mineral fibre |  |  |  | 5 |  | n/a | n/a |  |  | n/a | As per British Standard |  |  | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Protection against freezing | Mineral fibre |  | Pipe section |  | Specified conditions 1 |  | n/a | n/a |  |  | n/a | To BS 5422 |  |  | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Ventilation ductwork chilled air | Mineral fibre |  | Ductwrap |  | 10 |  |  | n/a |  |  | 25 |  |  |  | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Ventilation ductwork warm air | Mineral fibre |  | Ductwrap |  | 35 |  | n/a | n/a |  |  | 10 |  |  |  | Aluminium foil | Sheet aluminium casing Boiler rooms |
| Valves and flanges | Mineral fibre |  | Removable and reusable preformed rigid covers |  | As pipelines |  | n/a | As pipelines |  |  | As pipelines | As pipelines |  |  | As pipelines | As pipelines |
| Note all external pipes to be insulated with rubberised polybutylene covering with adhesive joints and identification labels |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Pipeline insulation thickness schedule |  |  | Revision: | - |
| --- | --- | --- | --- | --- |
|  |  |  | Date: | 14-May-06 |
| Pipeline size | Hot water system | Cold water system | Heating system | Chilled water system |
| 15 | 25 | 20 | 25 | na |
| 20/22 | 25 | 20 | 25 | na |
| 25/28 | 25 | 20 | 25 | na |
| 32/35 | 25 | 25 | 25 | na |
| 40/42 | 32 | 25 | 32 | na |
| 50/54 | 32 | 25 | 32 | na |
| 65 | 32 | 25 | 32 | na |
| 80/76 | 38 | 25 | 38 | na |
| 100/108 | 38 | 25 | 38 | na |
| 125 | 50 | 32 | 50 | na |
| 150 | 50 | 32 | 50 | na |
| 200 | 50 | 32 | 50 | na |
| Based on Mineral Fibre |  |  |  |  |