Order Schedule 20 (Order Specification)

This Schedule sets out the characteristics of the Deliverables that the Supplier will be required to make to the Buyers under this Order Contract

Statement of Requirement

The Provision of a Site Co-Ordinating Installation Design Authority (SCIDA) Assurance Service to Air Sites (Air SCIDA)

CCS Ref CCZI25A02 - ITT/Contract number 712876450

| Ref | Requirement |  |
| --- | --- | --- |
| A | General Requirements |  |
| A.1 | Scope of the Requirement |  |
| A.1.a | Introduction - MOD Installation Standards Policy, and Governance of the physical and environmental aspects of MOD ICT, ensure compliance with all legal, statutory, and regulatory requirements, the Cabinet Office Information Assurance Governance Framework and HMG Security Policy Framework. These policy documents mandate Information and Communications Technology (ICT) security, resilience, Configuration Management (CM), Change Control (CC), installation design control and accreditation processes. To ensure compliance with these policies and contribute to overall Cyber Defence, all MOD sites and facilities shall have a Site Co-ordinating Installation Design Authority (SCIDA) established in accordance with the extant CIDA Governance SCIDA Framework Document. - SCIDA assures that all ICT change at site level is installed in accordance with the requirements of JSP 453: Defence ICT Installation Standard (hereafter known as JSP 453) and the installations are then governed by the appointed SCIDA. TLBs are responsible for the provision of SCIDA at their sites. From the viewpoint of co-ordination of ICT change and the regulation of ICT installation standards, an appointed SCIDA shall preferably be independent from the organisations who produce the ICT change designs and deliver the physical elements of an ICT change. - Air Command is the TLB representative for the authority for the SCIDA contract delivery within Air TLB and referred to as ‘the Authority’. The Contract Delivery Manager, hereafter known as the Contract Manager, is the Authority’s point of contact for SCIDA matters. Under the delegated authority of Assistant Chief of Staff (ACOS) RAF Digital, the Contract Manager is RAF Digital Ops Spt SO1. The Contractor will be required to report to the Contract Manager or authorised representatives for all aspects of the contract. - This Statement of Requirement (SOR) defines the scope of the SCIDA contract for Air Sites. This task shall be undertaken by the winning contractor acting as ‘Air SCIDA’ for sites/locations for which HQ Air Command (HQ Air) has SCIDA responsibility. Structure of the Statement of Requirement Requirement A. General Scope of the requirement. Requirement B1 – B5 Core SCIDA Services. Requirement B6 Provide Technical Advisor Services. Requirement B7 Provide specific Outside Plant (OSP) Services. Requirement B8 Provide a tailored support package to specific location(s) at RAF High Wycombe. Requirement B9 Provide a tailored support package to RAF High Wycombe, Sites 1, 2 and 3 inclusive. Requirement B10 Provide support to Project MARSHALL. Requirement B11 IPZ and SCIDA Process alignment (Costed Option). Requirement B12 Additional CAD and Engineering Resource (Call off contract). Annex A Air SCIDA Service Level Application. Annex B Abbreviations and Terminology. Annex C MOD Policy References. Annex D Air SCIDA Master Site List. Annex E Indicative SCIDA Personnel Site Deployment. Annex F Personnel Experience, Qualification and Training Requirements. Annex G Government Furnished Assets (GFA). Annex H Air SCIDA Configuration Management Database (CMDB) Definitions and scope. Appendix 1 to Annex H RFL Example Template. Annex I Useful Metrics and Supplementary Information. Annex J Outside Plant Task Examples. Annex K Key Performance Indicators - Criteria (Cabinet Office Reportable). Annex L Master Site List, ECR Register and Audit Report extracts. Period of Contract - The period for which this contract is required shall be 4 years and 3 Months (1/1/26 – 31/3/2030). Resourcing - The amount of SCIDA resource available through this contract is limited by the financial restraints imposed by Government, the MOD, and the RAF and therefore that resource must be targeted at the highest priority Sites, Buildings and Systems. The contractor will be required to implement this targeted approach through the allocation of Service Levels; SL 1, 2 and 3 and others as agreed, throughout the term of the contract. Application of Service Levels (SL). - The contractor will be required to meet the SL criteria as detailed at Annex A; this annex is based on the criteria detailed in the CIDA Governance SCIDA Framework Document, hereafter known as the Framework Document, however some of the criteria have been amended to meet Air needs. - At the time of writing the Framework Document version is 2.1, however Air SCIDA shall monitor changes to the Framework Document and advise the contract manager through the QPM, or earlier, if necessary, of any significant changes which impact on SCIDA service delivery and may necessitate formal agreements or Contract Amendment (CA). - Individual buildings may be allocated a single service level or, where appropriate, different service levels may be allocated to different parts of a building, depending on the operational role and level of classified processing within that area. Allocations can vary both across a single site and from site to site according to operational needs or the needs of individual sites. Site stakeholders will be required to sign a Service Level Agreement (SLA) which will detail all service level allocations attributed to areas on their site. - At contract start the Contractor will be required to adopt the existing SL allocated to each area; in the case where no SL has been allocated, the SL will be determined during the initial audit of such areas. Service levels will be re-assessed as necessary to ensure they remain appropriate to the use of the area concerned and raised or lowered as necessary; changes to SL may result from e.g., ECR work or change of operational use of an area. - Service level Variations. Some structures housing C-E/ICT/ATM equipment are fully controlled by the system supplier and therefore SCIDA responsibilities are limited or vary from the responsibilities applied to regular buildings and rooms. More details are included in Annex A. |  |
| A.1.b | Organisation and Interfaces - The Contractor will have direct interaction with the Contract Manager or an authorised representative and shall refer MOD CIDA policy matters to the Defence CIDA. However, to undertake the responsibilities and tasks defined in this SOR, the Contractor shall be required to have a close working relationship with the Site or Stn stakeholders. In addition, the Contractor shall be required to work closely with all other organisations and agencies that are involved in the provision, operation, support and development of policy regarding ICT equipment on the Air estate. - When working on these sites the contractor will be required to ensure the Head of Establishment / Officer in Charge, or their delegated representative (SHEF / 4Cs officer), is aware of the work to be conducted and that safe systems of work are in place. |  |
| A.1.c | Core Requirement. The core service expected from the contract is summarised below, with further details in Requirements B1 – B5: - Establish & Maintain a Configuration Management Database (CMDB) baseline. Retain configuration information relating to new installations and changes to existing installations for the life of the system and generate drawings to aid configuration management and control. - Employ and maintain a formal change control process. The ECR Process, a 5-stage process to assess all ICT change, authorise installations and finally sign off those installations. - Update drawings, associated configuration documents and other relevant information. Primarily the CAD Team task: generate and maintain configuration management data and control drawings in AutoCAD or similar. - Provide SCIDA advice and guidance. The SCIDA Engineers are the key POC for any ICT change on the stations. Installers and designers will call on their vast experience to assist in putting together designs for new systems and changes to existing systems. They generally have a wealth of MOD/RAF and local site knowledge which is invaluable e.g. where things are in buildings, where critical pieces of infrastructure are located, how building interconnection is achieved, who on site does what and who can help. - Conduct SCIDA inspections relevant to assigned service level(s). The ‘Audit’ task. Engineers will inspect all areas with ICT to ensure no uncontrolled change has taken place, no ICT has been moved/removed, and ICT systems remain safe and secure etc. Note: To support these and many other aspects of the contract the current team employ two staff to handle the administrative tasks associated with the delivery of the services. This includes ECR tracking and processing, issue of certificates, initial help desk POC etc. |  |
| A.1.d | Non-Core SCIDA Support. Certain sites and projects are to be provided non-core SCIDA services through this contract, these include: - Technical Advisor (TA) / Project support staff. They support work on Air Programmes, new ICT infrastructure and large ICT infrastructure change projects. TAs take on major ICT projects, often following the RIBA process, looking at the ICT requirements within new builds and major refurbishments. They often produce an ICT (CIS) specification to inform designers, builders, installers and other agencies involved what is required in terms of physical infrastructure and the associated regulations and standards to ensure that the end users of the System(s) get the ICT services they need. (Section B6). - Outside Plant (OSP) Team. As tasked by RAF Digital, the team maintain pit and duct Configuration Management (CM) records, undertake surveys and advise on minor maintenance tasks. (Section B7). - RAF High Wycombe Specific Location(s). Tailored support package RAF High Wycombe requires additional/uplifted services in some areas that go above the levels afforded to other RAF Sites. (Section B8). - RAF High Wycombe, Sites 1, 2 and 3 inclusive. Tailored support package RAF High Wycombe requires additional/uplifted services in some areas that go above the levels afforded to other RAF Sites. (Section B9). - Project MARSHALL. Tailored Support to Project Marshall, a project to deliver Air Traffic Management (ATM) services to MOD. The project requires additional/bespoke services to meet the delivery requirements for the project. Many of the sites are on commercial premises and often remote, requiring additional travel and subsistence and host-imposed access restrictions. (Section B10). - IPZ and SCIDA Process alignment (Costed Option). New Requirement to support Information Protection Zone (IPZ) management in Air. This is primarily a resource requirement to begin to assess the IPZ processes and procedures to see where they align with the primary SCIDA processes and procedures to ensure there is no duplication of effort and make best use of SCIDA resource in the future. (Section B11). - Additional CAD and Engineering Resource (Call off contract). From time-to-time Major New Projects come along unexpectedly, often at short notice and some of which require a significant amount of SCIDA or TA services above what the core, fixed price contract can deliver. This is a costed option to deliver additional resource as and when required and will require a Contract Amendment and additional funding lines to be identified. (Section B12). |  |
| A.1.e | Sites - The Sites for the delivery of all services encompass all RAF Sites and other TLB Sites, or parts thereof, where Air have the responsibility to deliver SCIDA Services, in the UK, Cyprus and Gibraltar. - All requirements are to be delivered to the sites and numbers shown in the table below (at the time of compilation (28/4/25): Site Count Total; 244. Standard Site; 95. 22Gp Trg Sites; 6. Careers Offices; 11. Air Cadets; 36. UAS/VGS; 16. Adv Trg Centres; 1. Marshall; 79. - It should be noted that the size and number of sites can vary throughout the period of the contract. Changes to the number and sites and/or size/scope of the ICT footprint of sites contained within the contract shall be discussed, and the approach formally agreed, within the mechanism of the QPM and recorded in the minutes of those meetings. A comprehensive site list is included at Annex D. - RAF Benson & RAF Odiham. These sites are currently in the process of being transferred fully back into Air TLB. ATM apart, they have not been managed by Air SCIDA for several years and may require additional effort to re-baseline the sites and update or produce the associated drawings and other CMDB information. - Blandford Camp and MOD Lyneham. These are sites where Air had a limited footprint under the Air 22Gp umbrella. It is anticipated that the Air footprint will grow over the course of the contract necessitating a new baseline to be produced and managed thereafter. - Industry Sites. From time-to-time agencies may approach Air SCIDA to undertake SCIDA Assurance on both MOD and MOD related installations on industry sites. At the time of writing, one such site is availing itself of Air SCIDA services which is limited to ECR progression and related support. Further sites can be added through consultation where size of the task, site losses and gains during the term of the contract and the flex available in the contracted resource will be considered in deciding whether and how the tasks will be added to the contract scope. - Site Losses and Gains: Throughout the duration of the contract the number of sites can increase and decrease, and the ICT footprint on individual sites can grow and shrink. Suppliers shall stipulate their preferred approach to losses and gains in the site count and footprints (via RM6264 Attachment 2 response). A flexible approach would be preferred. Examples are (list not exhaustive): - A percentage leeway (5%, 10% in site numbers, 1 large, 5 medium, 10 small etc). - Case by Case negotiation following assessment of variations over the course of the contract. Site closures. - Where a Site within the scope of this contract is closed or due to be closed, the contractor will advise, or be advised by, the contract manager, through the QPM. The contractor will ensure that all services and assets recorded under SCIDA are accounted for and the correct disposal / return procedure is followed. - Where the site is transferring to another Gov/MOD organisation who have a SCIDA Service, the contractor shall formally hand over all responsibility for the SCIDA Service delivery to that organisation along with all CMDB information. - All drawings shall be retained in Air SCIDA archive until such time as the site is permanently removed from the Defence Estate. |
| A.1.f | Workforce. - The Contract Manager reserves the right, when operational circumstances dictate, to request that the SCIDA resources declared in the winning bid be diverted to best affect overall RAF output. The Contractor shall manage the workload in such a way as to take account of any resulting priorities and deadlines that the Contract Manager may specify. - The authority has a requirement to ensure resilience of service delivery at all locations, primarily at key locations such as MOBs and HQ Air, and in roles, such as the Technical Advisors. Workforce levels shall be proposed that ensure that site knowledge of ICT facilities and projects on each site is not restricted to one person. Planning, training and resource must be put in place to ensure knowledge is shared to such a degree that the loss of one or more members of staff does not put SCIDA service delivery for any site or project at significant risk. - It is envisaged that the response to this SOR shall have personnel based across the UK. The Authority’s view on the SCIDA personnel deployment levels and locations required to deliver the contracted SCIDA Service are detailed in Annex E; these levels have been derived after assessing: - The historical workload (see data in Annex I). - Risks highlighted through QPM during the current contract and the proposed workforce uplifts required to mitigate those risks. - Geographical spread of sites. - Current engineer home basing (assuming TUPE applies). - Confirmed and predicted Major Project increases to ICT footprints. The Authority believes the workforce estimates detailed in Annex E build into the contract the required levels of service to key locations while affording a small degree of resilience, business continuity and succession planning. However, suppliers can propose alternative workforce strategies providing they deliver the required levels of service while minimizing cost; sufficient detail justifying any deviation shall be provided for the impact to be assessed. - Key Staff. DPS Order Schedule 7 details the requirements related to ‘Key Staff’. Annex E identifies the Authority’s assessment of those roles it considers ‘Key’. The contractor shall identify by name who they intend appoint to fill those Key Roles and confirm prior to the contract Start Date. Response to be included in response to RMS6264 Attachment 2. - The Contractor shall use resources that are demonstrably competent for the task for which they are responsible and have suitable experience, skills and training selected from the examples in Annex F. See also requirement A.13. - Workforce hours. The number of workforce hours expended on this contract will be recorded. Example of Workforce hours expected: Contract Working Days (per member of staff declared in the ITT response) = 210 - broken down as follows: 260 weekdays minus: Leave (avg 30 Days), Sick (up to 4 Days), Company Diversions/trg (8 Days – not contract attributable), Bank Holidays (8 Days). Hours per day (FT Staff) = 7.5 Annual Hours (FT Staff) = 1575 Annual hours FT employees = 1575 hours x Number of FT. Annual hours PT employee #1 = 1575 hours x percentage of FT I I Annual hours PT employee #n = 1575 hours x percentage of FT Whole Team Total annual hours = e.g. (1575 x 39) + (1575*80%) + (1575*60%) = 63730. It is stressed these are examples, bidders should show their own calculations used to determine workforce hours delivered by the contracted service. |  |
| A.1.g | Major New Projects - Major equipment programmes or projects affecting one or more sites where substantial SCIDA effort is required to support the project may require additional SCIDA support to be funded by the external organisation delivering the project or programme. These programmes and their support shall be discussed and agreed within the QPMs. Example: Project MARSHALL. This was the UK MOD programme to transform Air Traffic Management (ATM) at military airfields. The programme was a Contractor led, Pan-Defence joint venture between NATS and Thales. Upon completion of the programme, the function will be led by the prime Contractor Aquila. This programme had a unique SCIDA requirement that required the allocation of one dedicated engineer from core staff and supplemented by an additional engineer, funded separately by the Marshall DT and achieved through a contract amendment, to ensure full support was provided for the SCIDA elements of the project. - The contractor shall ensure that additional resource is identified and engaged to meet any additional resource requirement identified by the authority. This will, where applicable, be added to the contract through the Contract Amendment process detailed in the contract T&Cs. |  |
| A.1.h | Engineering Change Request (ECR) Procedure - ICT change may be initiated from within a site or by a Project Team (PT), a customer, contractor, or supplier; all ICT change proposals shall be documented in order to protect the integrity of the affected system. - All such change within configured boundaries at sites covered by this requirement shall be managed in accordance with the requirements of JSP 453; the process as it applies to this contract, with Air specific requirements added, is at section B2 of this SOR. - The basic ECR Process is a 5 stage ICT Change Control model for use at all MOD sites. - ECR Part 1 – Initial notification of Proposed ICT Change and Documentation Request – A form received by SCIDA from those requesting authority to carry out a change to or new ICT Services. This gives basic details and requests SCIDA provide additional information and drawings to aid the detailed design to be submitted with ECR Part 2. - ECR Part 2 – Change Proposal Design Endorsement Request - A form received by SCIDA to accompany or follow on from the associated ECR Part 1 giving a detailed design and description of the change to or new ICT Services. SCIDA will assess the design and ensure that the proposal meets all associated Statutory Requirements, National, International and MOD specific standards. This part effectively requests the issue of ECR Part 3. - ECR Part 3 – A form issued by SCIDA approving the design in ECR Part 2. This gives the installers the authority to undertake the change. Installers will undertake the change and then submit ECR part 4. - ECR Part 4 – A form received by SCIDA from installers after they have completed a change to or new ICT Services. This will usually include As-fitted drawings and other documentation to enable SCIDA to assess the physical change and look to approve the final installation via ECR Part 5. - ECR Part 5 – A form Issued by SCIDA to certify that the change has been completed in accordance with the design and all associated Statutory requirements, National, International and MOD specific standards. - Some Project Marshall ECRs have an added process in addition to those detailed in the above reference, the Beneficial Use Statement (BUS). This process enables use of an ICT installation in advance of the final ECR Pt 5 being issued. It is expected that this process will remain in place for some time and may be a process that contractors wish to consider for other projects which may justify this type of approach. - Overseas & Remote Sites (inc UK Outer Islands). Some sites are in locations where transport options are very limited, travel times can reach many hours and occasionally a trip can require a day to get there, an hour doing the SCIDA work and a day to get back; bad weather etc can, and has, further prolonged visits. Timescales for issue of ECR Pts 3 and 5 (and Audits) can be extended in these situations however these must be justified in the QPR and QPM. |  |
| A.1.i | SCIDA Briefs - The Contractor will be responsible for providing up to 32 formal SCIDA briefs per year. The briefs shall be delivered to the following audiences: - Engineer Officer Foundation Training (EOFT) course at RAF Cosford. Six briefs per year. 2-hour presentation, 1-hour consultation. Summary of brief - Overview of full-service including ECR process, auditing regime, Service Level Agreements, discussing aspects of finance and incorporating an installation design task. - Deputy Authorised Telecommunications Officer (DATO) course at RAF Cosford. Four briefs per year. Duration 1.5-hour presentation, 1-hour consultation. Summary of brief - Overview of the service and detailed examination of the ECR process and Service Level Agreements in relation to ATO services. - Deploying staff at 90 Signals Unit (SU) at RAF Leeming. 12 per year. 1-hour presentation, 0.5-hour consultation. Summary of brief - Application of configuration control, installation standards, H&S requirements, and TEMPEST measures in deployed environments. - TEMPEST Presentation for Battlespace Management Operators at RAF Fylingdales. Up to 6 briefs per year. Up to 1-hour presentation, Summary of brief - Overview of emanation security, vulnerabilities, countermeasures, and requirement for the configuration control using the ECR process. - Ad-hoc Presentations, UK wide. Up to twelve per year. Duration normally 2 hours. Summary of brief - Overview of ECR process, SLA requirements and installation standards. Any requirement for these briefs shall be requested through the Contract Manager. - The Contract Manager shall be notified of any brief which cannot be performed due to resource or other issues. |  |
| A.1.j | TEMPEST - In the context of this contract, TEMPEST Control is the Assessment of risk from compromising EM emanations from RED equipment (Secret and above) and the countermeasures or risk management necessary to mitigate them. - The contractor shall undertake a variety of tasks in support of Air TLBs TEMPEST control objectives. Air SCIDA Change Control and Auditing processes shall assess TEMPEST risks associated with a system, room, building or site and ensure the necessary countermeasures are enforced or risk managed by the appropriate risk owner. TEMPEST Countermeasures Assessments (TCA) and TEMPEST Visual Inspections (TVI) shall be incorporated into BAU SCIDA Engineering Change and Audit processes however ad-hoc requests for these tasks, or the reports and certificates associated with them, shall be fulfilled on request. Full Establishment TEMPEST Assessments and TEMPEST testing are outside the scope of this contract. - When assessing the above, it will be necessary to inspect all areas within the 3D TEMPEST Coupling Zone of a piece of RED equipment. |  |
| A.1.k | Information Protection Zones (IPZ) - IPZ and SCIDA Process alignment - Costed Option - Information Protection Zones are areas within a building where additional security controls are required to protect audio and electronic information compromise. The Key aspects of Defence ICT Installation Standard policy, most notably in terms of Service Level allocations, have recently aligned with Defence Security policy regarding IPZs. The Air SCIDA Change Control and Audit procedures shall link into the IPZ requirements contained in the associated JSPs, AP 600 and AP 3085 (RAFP) as they develop. A Costed Option is included at B11 to provide a 2-man team of SQEP to assist RAF Digital in alignment of IPZ and SCIDA processes related to this aspect of Cyber Security. Most suitable day rates from B.12 to be used if appropriate. |  |
| A.1.l | Technical Standards - The Contractor shall be certified to a BS EN ISO 9000 series quality system and perform the stated tasks in accordance with that quality system. Regarding Information Security, the contractor shall be certified to ISO 27001. - The Contractor shall assess all change to ensure compliance with all applicable Statutory Instruments, National and International standards and the relevant MOD policy. They shall ensure that their staff, installation teams delivering ICT change and MOD staff also apply the most recent version of such standards and policy. This shall include the Codes of Practice, standards, procedures and documentation called upon by JSP 453. Clarification of certain aspects is provided within the SOR. |  |
| A.1.m | Provision of Information and Technology Systems - Where a requirement exists for the storage of SCIDA documentation with a Protective Marking (PM) of SECRET or Above, the Contractor will be provided with access to the necessary accounts and associated GFA IT hardware. The Contractor will be required to provide sufficiently security cleared personnel to be able to access and utilise said GFA IT hardware and accounts. - At Official Sensitive (OS), full use shall be made of MODNet. Access will be provided by the most appropriate means (e.g. laptop); associated accounts and standard office software will be included as GFA for all team members however CAD tasks which are currently outside the capabilities of MODNet may have to be provided by other means. - The current supplier CAD LAN is located on MOD Premises with no off-site/Internet connectivity. Transfer between the LAN and MODNet is achieved through manual transfer (DVD/USB etc) between the two systems. It comprises of servers, switches/hubs, storage, workstations, plotters and printers, AutoCAD and Windows Software. Details of LAN components and peripherals can be found on the file ‘Air SCIDA LAN Assets’ included as part of the bid pack. - The LAN Network equipment is housed in a room at RAF High Wycombe which is provided as GFA, this room shall remain available for the duration of the contract or until CAD services on MODNet via AutoCAD enabled laptops or an alternative system is proposed and available. - Where alternatives are proposed, the Contractor shall be responsible for providing any additional IT systems and associated facilities required to deliver the SCIDA service (e.g. Company Systems/Equipment), throughout the period of the contract. This shall include but not be limited to, equipment, cabling, application software, consumables, maintenance, software and equipment upgrade, servicing, or other support. The IT systems shall have a specification fully suited to the task. The Contractor’s proposed hardware, software and network connectivity detail and intended up-grade philosophy shall be detailed within the bid and will also be subject to MOD ICT Accreditation prior to use. - The Contractor will be free to choose the application software to be used for storing and processing configuration control information at OFFICIAL SENSITIVE classification where MODNet is unavailable or unsuitable, but this must be MODNet compliant. - The Contractor will be provided with the existing building and other drawings. Any costs associated with converting these drawings to a format readable by the Contractor will fall to the Contractor. - The Contractor will be required to preserve the integrity of the existing dataset. - The drawing package chosen must be capable of outputting data in AutoCAD vector format and PDF. Drawings must be held in a format (or easily converted) that can be readily provided on demand to relevant parties within the MOD who hold the requisite clearance and have valid justification for the information. |  |
| A.2 | Definitions |  |
| A.2.a | In addition to the definitions detailed in the Terms and Conditions of the Contract the following definitions shall also apply. Where the definitions below contrast to those detailed in the Terms and Conditions of the Contract then the definitions within the Terms and Conditions of the Contract shall take precedence. |  |
|  | Definition | Interpretation |
|  | Contractor’s Personal Use | Any use of MOD furnished property, facilities or equipment intended for the primary benefit of the Contractor or the Contractor’s Personnel which is contrary to the MOD’s interests is considered personal use. |
|  | Contractor’s Personnel | Any employees, including sub-contractors or other agents working on behalf of the Contractor, shall be deemed the Contractor’s Personnel. |
|  | Designated Officer | The Designated Officer is the MOD representative responsible for the Requirement and is as defined at Box 2 of DEFFORM 111 of this Contract. |
| A.3 | Abbreviations and Acronyms |  |
| A.3.a | In addition to the abbreviations and acronyms detailed in the Terms and Conditions of the Contract and DPS Schedules, a comprehensive list can be found at Annex B. |  |
| A.4 | References |  |
| A.4.a | In addition to the references detailed in the Terms and Conditions of the Contract the references at Annex C shall also apply as well as any subsequent revisions and amendments to the references. This list does not absolve the Contractor from conforming to any other relevant publications. |  |
| A.5 | Processes and Related Taskings |  |
| A.5.a | N/A |  |
| A.6 | Security |  |
| A.6.a | - The Contractor is to ensure that all of the Contractor’s Personnel have a minimum of Security Check (SC) clearance. Where the Contractor’s Personnel do not have SC clearance that individual will not be allowed access to MOD facilities or data. - It should be assumed that many engineering and CAD staff will require security clearance at DV and potentially STRAP levels at some point during the contract; current numbers with DV clearance can be advised during the ITT process. Contractors must, when given adequate notice, take measures to ensure that staff with the appropriate clearance level are available to undertake tasks when required. - The SCIDA Contractor shall nominate a security officer who will act as the interface with the Contract Manager or their security representative. The contractor's security officer will ensure that the contractor meets the MOD Security requirements in line with DPS Order Schedule 9. (include in RM6264 Attachment 2 response) |  |
| A.6.b | All information related to or generated by this Contract is to be treated in the appropriate manner in accordance with Government Security Classifications. The classification of the material to be handled ranges from Official (majority) to TOP SECRET (Specific Areas/Locations). |  |
| A.6.c | All personal data processed under this Contract is to be treated in accordance with the Data Protection Act 2018. |  |
| A.6.d | - All electronic data received or produced as part of this contract must be stored in appropriate MOD storage areas when this is made available to them, except where agreed in advance with the Contract Manager. At the time of writing the exception will be SCIDA AutoCAD drawings (.dwg) which, until such time AutoCAD software is made available to contractors on MODNet, will be held on an accredited company LAN. - Where a requirement exists for the manipulation or storage of documentation of a classification Secret or above, the contractor will be provided with the required system accounts and access to suitably accredited ICT hardware (GFA). - Contractors must ensure that any data aggregation concerns are brought to the attention of the Contract Manager or PSyO and any resulting recommendations implemented. |  |
| A.7 | Site Access |  |
| A.7.a | The Contractor will be advised by the Contract Manager of the procedures and forms of identity required for initial access to sites to which the Contractor’s personnel will require access under this contract. |  |
| A.8 | Safety and Environmental Provisions |  |
| A.8.a | When on the Site the Contractor is to comply with all MOD Safety, Health and Environmental Protection regulations and policy. |  |
| A.9 | Hours of Operation and Times of Delivery |  |
| A.9.a | - All services to the Site shall normally be delivered between the hours of 0800 - 1700 on weekdays with exception of recognised UK Bank Holidays and Public Holidays. - Any requirement to provide services outside these hours will be at the contractor’s discretion and subject to negotiation between the contractor and the sites concerned; the Contract Manager shall be consulted where funding or deliverables may be impacted. |  |
| A.10 | Quality Assurance |  |
| A.10.a | QA is the subject of a DEFCON provided within the ITT Pack. Certification to current versions of ISO 9001 and 27001 will be required |  |
| A.11 | Contract Monitoring, Management and Reporting |  |
| A.11.a | For the purposes of contract monitoring, representatives of the Contractor will routinely report to the Contract Manager on the performance of the Contract. |  |
| A.11.b | The Contractor is responsible for the performance of the Contract by any sub-contractors or other agents working on behalf of the Contractor. The Contractor is to deal with any issues relating to any sub-contractors or other agents working on behalf of the Contractor, this however does not exclude sub-contractors or other agents working on behalf of the Contractor from attending any Contract Monitoring meeting or contributing to any report where it is appropriate for such sub-contractors or other agents to do so. |  |
| A.11.c | If any sub-contractors or other agents working on behalf of the Contractor are found unsuitable, for whatever reason, the Contractor is to engage with the relevant sub-contractors or other agents to broker a resolution. |  |
| A.11.d | The Contractor shall provide access to all required information and shall give assistance as necessary with independent audits to be carried out by the Contract Manager, their agents or the Defence CIDA. The Contractor shall carry out corrective action to remedy any non-conformances arising from these audits. The audits will assess whether SCIDA is delivering the optimum benefit to operations, as far as this can be achieved, through the application of configuration management processes detailed in the Framework Document and this contract. |  |
| A.11.e | The Performance Indicators (PIs) for each deliverable under the contract are stated in B1 to B12. Cabinet Office requirements mandate reporting on some KPIs, indicative KPIs for this purpose are shown at Annex K however these will be subject agreement between the Authority and the Supplier prior to contract start. The PIs represent performance targets and there may be circumstances where the Contractor is unable to meet the PI for reasons beyond their control, or because the Contract Manager has requested a concentration of resources on another deliverable under the contract. The circumstances concerning any instance where a PI is not achieved will be discussed at the relevant QPM. Where a PI in a table of requirements in this SOR is stated in days, this includes weekends and UK public holidays; where it is stated in working days, it does not include weekends or UK public holidays. Any adjustments to PI and resource allocation shall be agreed at, and recorded in, the QPM. |  |
| A.11.f | Handover & Takeover - There shall be a takeover / handover period commencing a minimum of six weeks prior to the current SCIDA contract end date. Incoming Contractor - Shall take all steps necessary to be able to take over the responsibility for the provision of the services on the contract start date. The attainment by the Contractor of an orderly phase-in programme is an essential pre-requisite to the satisfactory fulfilment of the contract and time is of the essence in respect thereof. During the phase-in period, all the provisions of the contract shall apply; save that the incoming Contractor shall not be required to provide the services until the contract start date. - There shall be an orderly transfer of Government equipment, information and responsibilities from the outgoing Contractor and, the responsibility for maintaining the documentation data set required by the Contract shall formally pass between Contractors on a date agreed between the incoming and outgoing contractor. - During the takeover period the Contractor shall formally check the accuracy, integrity and robustness of all data sets and shall sign an acceptance certificate accepting the documentation; all problems or deficiencies concerning the documentation data sets and the other requirements of this contract, shall be noted by the incoming Contractor and included in a SCIDA Takeover Action Plan to accompany the acceptance certificate. The Action Plan shall be provided to the contract manager at the end of the takeover period and shall contain firm commitments against each problem or deficiency as to when the contractor expects each problem or deficiency to be resolved. The plan shall be amended and presented at each QPM in a manner that makes it a straightforward process for the Contract Manager to audit the progress of the items on the Action Plan. Outgoing Contractor - On expiry of the contract resulting from this SoR, NO configuration control drawings, databases, or other related information, held as part of any previous SCIDA or CIDA roles shall be retained by the outgoing Contractor unless they are successful in this bid. Prior to Contract handover, the outgoing Contractor shall carry out the following actions: - Produce and handover a completed documentation data set in the format stated in the previous SOR. The documentation data set shall include current and archive material, either produced by or held by the Contractor in the performance of the Contract. Data shall include, but is not limited to, all drawings, change documentation (ECRs etc), and any contract management tools used to ensure a seamless transfer and maintenance of service delivery (e.g. spreadsheets, databases, schedules, work instructions…); data shall include all paper print, computer magnetic or optical media. The electronic data set shall be delivered with at least two backup copies and ready for immediate accessibility and continued use by the incoming Contractor unless all data has been transferred to MODNet prior to contract start date. - Provide assistance and information to the incoming Contractor to enable the full electronic information-set to be fully installed and operational on the new Contractor’s IT suite. - The existing GFA, IT hardware and software purchased and/or utilised as part of the previous contracts will be transferred to the incoming Contractor. Ongoing Activities - The Contractor shall nominate a single point of contact within the Air SCIDA organisation, through whom the Authority will address all issues concerning tasking, management, and contractual obligations. The nominated individual shall have sufficient delegated authority from the Contractor to act on its behalf on these issues. - The Contractor shall provide audit reports, drawings, and other information as specified in requirements B.1 to B.12 or as detailed in any specific non-routine task requirements. - The Contractor shall maintain, or produce alternatives to, the contract management tools handed over (e.g. spreadsheets, databases, schedules, templates and work instructions) to ensure efficient management of all SCIDA services and delivery of the requirements detailed in this SoR. - Throughout the duration of the contract, the contractor shall gather information to facilitate future contract renewal with a subset of that information being used to provide periodical input to the QPR. - The Contractor shall provide a quarterly report 5 working days prior to the Contract QPM. Content of QPRs will be agreed at a Contract Startup Meeting to be convened by the successful contractor during the handover period however historical report format and content will give an indication of initial expectations. Information can be textual or graphical, where large amounts of information need to be included, this can be provided in annexes cross referred in the main body. Examples of data to be collected include: Scope and Changes – Total Site count, details of site additions and deletions and major changes to ICT footprint. Contract hours. Total workforce hours expended on the contract per quarter, split into functional areas e.g. Generic/Standing Tasks (Admin, Management, SCIDA General) ECRs, Audits/SLA, General Client Assistance, Air CySC Assist/Advise, CAD, OSP, Marshall, TA Service, travel, further broken down where amplification could be useful. Staff Changes and Issues – Resignations, Retirements, recruitment, diversions, long term sick etc T&S: - Hotel Nights UK (n). - Hotel Nights Overseas (n and locations). - Flights– (Number and destinations). - Total Motor Mileage Claimed (Distance – Miles). - Other (all other costs e.g. Professional Registration, Phones, Clothing…) Site SCIDA Audits completed, overdue (inc justification), due next quarter. ECR Pt 1 – 5 received/issued. SLA Version and date information. % Progress in Baselining/Incorporating Blandford, Benson & Odiham, Lyneham. % Progress in reaching CMDB (Drawing) uplift to Framework Document requirements. Namely Building Floorplans, RED/BLACK/BLUE containment routes, TEMPEST Bubbles, IPZs and new style RFLs. Uncontrolled change: Include details of amounts, types, whether increasing/decreasing and recommended solutions. Workforce hours wasted should be included to better quantify the scale of the problem. VfM Issues. e.g. Information regarding instances where MOD may be paying for services no longer used e.g. BT circuits. Briefing and presentations. Types delivered, numbers and feedback received. Social Value Achievements. Apprenticeships and other educational and training achievements towards the requirement to ‘Support educational attainment relevant to the contract, including training schemes that address skills gaps and result in recognised qualifications’. - The contractor shall convene QPM (or equivalent) meetings within 10 working days of the quarter end date or otherwise by agreement. SCIDA shall provide the secretariat and location for the Contract QPM. Minutes of meetings to be completed within 10 working days of each QPM and provided to the Contract Manager in electronic format. |  |
| A.12 | Government Furnished Assets |  |
| A.12.a | The Contractor will be furnished with the pieces of Government Furnished Assets (GFA) as detailed at Annex G to this SoR. |  |
| A.12.b | The Contractor is to report to the Designated Officer any failures of GFA at the first instance for repair or replacement, as appropriate. |  |
| A.13 | Personnel, Qualification and Training Requirements |  |
| A.13.a | Contractor should provide (via RM6264 Attachment 2 response): - A proposed Organisation Chart (Organogram) showing all post titles and primary locations required to deliver the service. The Organogram should identify those posts considered ‘Key Staff’’ (see DPS Schedule 7). - The qualifications and/or experience required or desired are detailed at Annex F. - Current Supplier. A Matrix shall be completed for everyone identified in the organogram and provided as part of the bid submission. - New Winning Supplier. Where the intent is to TUPE current staff into their organisation, this should be stated in the table mentioned below, negating the need for a matrix for those individuals. Where alternative staff are proposed, matrices will be required. - A summary of the scoring achieved using the matrix mentioned above shall be included in a table (example shown). The table shall list all posts proposed and the score of the individual currently filling, or proposed to fill the post using the matrix at Annex F. Post (as per Org Chart/Organogram); Score; Matrix/TUPE. Head Air SCIDA; N/A; TUPE from Current Supplier. Site Eng RAF Somewhere; N/A; TUPE from Current Supplier. TA #5; 88; Matrix – New Role. Site Eng RAF Elsewhere; N/A; TUPE from Current Supplier. ….. |
| A.13.b | The Contractor is responsible for the sourcing of the appropriate training for the Contractor’s Personnel to meet the basic requirements for the roles to be undertaken (see Annex F). Hours expended on said training will NOT be attributable to the contract. Where the MOD is directly delivering the training then the Contractor and Contractor’s Personnel are to quote the Contract Reference Number and relevant Commercial Officer when booking any training for verification of the validity of training need under the Contract. Any generic MOD mandated training required for day-to-day execution of the contract will be provided (e.g. DLE); hours expended on said training will be attributable to the contract. |  |
| A.13.c | The Contractor is responsible for all costs for training of the Contractor’s Personnel in order to meet their obligations under the Contract unless otherwise noted at Annex F. |  |
| A.13.d | The Contractor shall provide (via RM6264 Attachment 2 response) an explanation of how they will ensure sufficient trained and knowledgeable workforce levels are maintained to ensure the contracted SCIDA services are maintained throughout the term of the contract. |  |
| A.14 | Certification and Accreditation |  |
| A.14.a | Company ISO 9001:2015 and ISO 27001:2022 Certification is to be held throughout the duration of the contract. (include details in RM6264 Attachment 2 response) |  |
| A.15 | Travel And Subsistence (T&S) |  |
| A.15.a | Contractors should use the information provided to build in a cost for reasonably foreseeable T&S. Some metrics have been provided in Annex I to aid in this task. Bid submissions should include an overview on how the figures have been derived. |  |

SCIDA Service Requirements

| Ref | Requirement | Additional Information | Quantity | Standard of Performance |
| --- | --- | --- | --- | --- |
| B | Deliverable Requirements |  |  |  |
| Core SCIDA Tasks |  |  |  |  |
| B.1 | Establish and maintain a Configuration Management Database (CMDB) Baseline (New Sites) (SFD Process 1) | A primary requirement of the SCIDA is to understand the ICT infrastructure and installations in the appointed area. Each new Site/Building/Area/System requires to be surveyed to gain an understanding of the state of inherited installations, CMDB records and procedures. Surveys shall cover Physical and Documentary aspects of each site and level of compliance with the standards mentioned in JSP 453 and any standards or policy referenced within. Tasks related to creating and establishing a baseline can vary depending on the area to be surveyed. The initial full baseline should be a once only activity then the maintenance of the CMDB documents shall be routine, ongoing SCIDA tasks through the formal change processes detailed at B2 – B5. | Baseline Document Set established for new sites. Action Plans produced to aid resolution of all Physical and Documentary non compliances or omissions. | - Site(s) to be added to a live Master Site List (example extract at Annex D) on allocation of a site to Air SCIDA. - Baseline audit of the site to be completed within 6 months of the site being allocated to Air SCIDA. Audit and reporting process at B.5 to be followed. Relevant risk holder to be informed of non-compliances and non-conformances. - CMDB records storage area to be established and populated with all baseline information available and generated. - Any drawings required for the CMDB are to be obtained or generated within 6 months of the Baseline Audit. |
| B.1a | Activities to support full integration of RAF Benson & RAF Odiham into Air SCIDA Service | Baseline all areas not covered under the current contract (ATM) AOR as per the New Site Process detailed in Requirement B1, Timescale as per this requirement. | Engineering and CAD support | All SL1 & 2 buildings audited and CMDB complete by end Y2. |
| B.1b | Activities to support full integration of Blandford Camp and MOD Lyneham into Air SCIDA Service | Baseline all areas not covered under the current contract ATM AOR as per the New Site Process detailed in Requirement B1 however timescale as per this requirement. | Engineering and CAD support | All SL1 & 2 buildings audited and CMDB complete by end Y2. |
| B.1.c |  | As part of the Baseline activities at B.1 and periodically thereafter (B.3), a Service Level (SL) shall be allocated or confirmed for each Site/Building/Area/System and agreed with Site HoE or designated representative. SLs are to be recorded in a Service Level Agreement (SLA). All Sites and Buildings, existing and new, at all SLs, must be included in an SLA. Small sites and lodgers etc may be included in a Parent Site SLA. Another exception is Non-MOD WAM sites where an entry in the Master Sites List (or equivalent) detailing audit scheduling, address, POC and other useful information will suffice. Information on allocation of service levels is included at Annex A. | SLA available and maintained for each site and areas within. | - SLA produced within 6 months of a site being added to the MSL. - SLA reviewed following each engineering change and ‘live’ version amended where required. - SLA to be reviewed, signed by the HoE or authorised representative (B.3) and reissued following each periodic audit (frequency as in B.5). For SL3 sites, the SLA should be produced and issued and then updated and re-issued when changes are agreed with site or authority. SLAs should be issued alongside the audit report where applicable. |
| B.2 | Employ and maintain a formal change control process (SFD Process 2). | It is essential to prevent unauthorised change which undermines SCIDA control, therefore there is a need to establish and use a robust CC process where the SCIDA is notified of a proposed change at the earliest opportunity. All proposed change must be authorised by the appointed SCIDA. Any change without notifying the SCIDA is classed as an unauthorised change and a breach of MOD policy. The formal CC process mandated by CIDA Governance contains 5 main elements; the Engineering Change Request (ECR) model process is provided in JSP 453. Equivalent documentation can be used providing that as a minimum all the information detailed in the formal ECR process documents are included. Changes are to be assessed to ensure compliance with MOD requirements and are not to adversely affect the site, existing systems, or other concurrent change(s). The Additional processes and procedures within Chapter 4 are to be used where appropriate (e.g., Retrospective ECR, Design Non-conformance, New Installation Non-conformance, and Existing Installation non-conformance reporting), Beneficial Use Statement (BUS); this is a form used within Air only and is used to authorise an installation where the system needs to be set to use prior to or in preparation for full ECR Pt 5. Resources may dictate the level of SCIDA CC applied to Service Level 3 areas however in all cases, regardless of Service Level, the full ECR change process must be followed. | Assess all changes within Air Configuration Boundaries to ensure compliance with JSP 453 and all referenced or implied Statutory Instruments, Policy, and Standards (MOD, National and International). | - All formal change process documentation received or generated is to be retained and maintained and will form part of the CMDB for the area. All drawings and other record types affected by changes are to be updated as detailed in process B.3. - A record is to be maintained of every ECR 1, ECR 2, ECR 3, ECR 4, BUS and ECR 5 (or equivalent). - On receipt of ECR 1 or other valid request, fulfil drawing requests for change proposers within 10 working days. Hardcopy or PDF will be the default format provided. If required in another format recipients may be required to fund the effort required to produce suitable versions. - Proposals at ECR 2 are to be reviewed and responded to within 10 working days, this may involve a physical survey. - Once a design has been confirmed as compliant and conformant, ECR 3 issue is to be completed within 10 working days. - Within 10 working days of ECR 4 receipt, each completed change is to be assessed for compliance and conformance. This is to involve a physical inspection where required and includes an assessment of the as-fitted documentation supplied for completeness and accuracy. - If after assessing the installation and supporting documentation everything is deemed sufficiently compliant and conformant, an ECR 5 is to be issued and updates to all CMDB records are to be completed within 10 working days; in the case of drawings this is taken as meaning the update requests are to be lodged with the relevant drawing office within the same 10 working days. - During protracted installation work the SCIDA is to periodically assess the change to identify potential issues early enough for change proposer resolution prior to the change being completed. - Proposed new external underground or overhead ICT installations are to follow the formal change control process. - When unauthorised change has been identified, a retrospective change process is to be carried out and attempts made to prevent reoccurrence. The unauthorised change agent shall be identified, and the details provided to the relevant stakeholder. - Any local issues with change, installation standards or procedural refusals that cannot be resolved by SCIDA are to be raised to CIDA Governance. This includes organisations unwilling to follow the formal change process or poor installation practice. |
| B.2.1 | ITSM Tooling (ECR Progression Tracking) | ECR tracking is currently achieved through complex Microsoft Excel Spreadsheet (example in Annex L and at Excel File 20250606-ECR Register Extract). SCIDA delivery suppliers and Air CySC teams would benefit from efficiency and visibility improvements in ECR tracking processes (e.g. using e.g. Microsoft Power Apps, Power Fx, Power Bi, Dataverse etc) if suitable. Data would be a minimum of Official Sensitive (OS) requiring use of a suitably accredited company system or able to be homed on MODNet. | Solution should deliver: Tracker: Improvements to or new tools for tracking ECR progression. Dashboard: To include facility to output ECR tracking data to ‘dashboard(s)’. | - Audit Reporting Tool, Trackers and Dashboards available 24/7 to authorised users. - Initial development and annual upkeep costs to be detailed in the miscellaneous costs section of Commercial Cost Workbook. |
| B.3 | Maintain CMDB. Update drawings, associated configuration documents and other relevant information (SFD Process 3) | ‘As Fitted’, ‘As Built’ and SCIDA drawings are required in support of CM. For existing installations, they shall be current, readily available and provide a complete history of change. Air SCIDA SLAs detailing assigned facility Service Levels are to form part of the CMDB. To bolster the CM portfolio and to aid with proposed future ICT installations, the SCIDA shall engage with the relevant site FM Team and other departments to gain any relevant drawings. This could include, but not limited to, site plans, underground service plans, building floor plans etc. SCIDA drawings are to be produced and maintained as per Annex H. Contractors shall liaise with the site FM Team and others to gain drawings to complement the CMDB e.g. Building Plans, Electricity/Gas supply routes/maps. | CMDB for all new and existing Sites in AOR where SL dictates. | - Ensure all necessary CMDB information (as per Annex H) is complete, accurate and readily available. CC and CM documents are to be stored electronically in the relevant shared area. - This is an ongoing task through the course of SCIDA duties. - For all Service Levels where RED equipment/systems are located, establish, and maintain TEMPEST coupling Zone drawings. - Maintain records of external and internal ‘Approved Routes’ (OSP/CMS). - ‘Red Line’ Updates to drawings are to be completed and filed with the relevant Drawing Office within 10 working days. - The SLA is to be up to date and signed by the relevant site appointment. (B.3) - CMDB information set to be updated within 30 working days of the physical completion of each change or audit required at B.5. (60 working days where the SCIDA engineer does not have on-site drawing capability). |
| B.3.1 | Uplift to current contractor supplied CMDB & drawing specifications | Some of the requirements detailed in Annex H differ from the requirements currently delivered and require an uplift in content to align with the Framework Document. | In order of priority: - Whole Building Floor Plans. - Internal RED/BLACK/BLUE Cable Routes - IPZ identification - TEMPEST Bubbles - External Approved Routes - RFLs in Microsoft Excel. See Annex H. | Contractors should propose a phased approach to achieve full compliance over the term of this contract. Compliance should be measured and the level (%) of compliance reported in each QPR and QPM. |
| B.3.2 | As fitted Topology and System Schematic availability | These are often received and retained but buried within a series of documents related to individual ECRs. To ensure the most recent schematics are available to authorised agencies these drawings should be stored and shared appropriately to provide easy identification of, and access to, the most up to date versions. See Annex H Para 27. | Topology and System Schematic drawings/Diagrams | Provide 24/7 access to authorised users. |
| B.4 | Provide SCIDA advice and Guidance (SFD Process 4) | To underpin CM at a site, the SCIDA will provide support and advice to all stakeholders. This support will include technical advice to change proposers and change designers on matters such as TEMPEST, EMPP, EMC, connectivity, configuration control, associated H&S, installation standards, regulations, and policy. Telephone, email and other remote methods of advice and guidance to be afforded to RAF staff on detachment. This to exclude sites covered by other SCIDA agencies (e.g. JFCIS). | On request. | - A system to assess and record SCIDA Competent to Practice (CtP), or equivalent, for engineers and CAD Techs is to be in place. Competency can be assessed through knowledge of the work already undertaken as a SCIDA and for new staff, a training and/or experience plan documented for everyone. - Able to readily access the ICT provided to review installation documentation and associated standards required to deliver sound SCIDA advice. - Respond to all requests to provide technical advice and guidance within 10 working days of receipt. An adequate response is considered an answer to the query, or a holding reply to gain external advice on their behalf. - Understand the escalation/support process for queries that cannot be fulfilled from own resource. - Can facilitate MOD contractor requests for access to JSP 453. - Attend and provide input to any relevant boards, meetings, or forums. These could be project meetings, change advisory boards, site periodic infrastructure meetings, siting boards, invitation to tender etc. All relevant meeting minutes or records of decisions which may affect current, or future ICT infrastructure are to be held with the CMDB pack. - Establish and maintain relationships with pertinent key stakeholders in the assigned Area of Responsibility (AOR). This could be HoE, FM Team, Estate Team, A6 community etc. |
| B.5 | Conduct SCIDA audits relevant to assigned Service Level(s) (SFD Process 5) | To ensure continuing conformance to CIDA Governance requirements, sites, facilities, or systems must be regularly inspected by the SCIDA. The frequency of inspection is determined by the assigned Service Level (SL). This will require the creation of a SCIDA inspection program that must be communicated with the HoE or equivalent. Inspections of each area are to assess the current state/condition of the ICT infrastructure, highlight unauthorised change and any deterioration of installation standards i.e., poor practice. This information is to be included in an inspection report. Any non-compliant or non-conformant installation is to be highlighted in the report with remediation recommendations. Assess and record on each audit: - Whether JSP 453 installation standards and procedures are being maintained. - At a very small number of sites on the RAF Estate EMPP compatibility is to be considered when assessing ICT change. The site names/locations will be advised to the winning bidder. - The accuracy and content of CMDB (Whether ECR and other changes have been incorporated into the CMDB). - The availability of electrical safety certification for cabinets/racks (Conforming to MOD ICT Cabinet policy and / or the current legislative requirements). The Contract Manager, RAF Digital and the Defence CIDA shall be consulted where difficulties are encountered in arranging for responsible agencies to make good sub-standard installations. Action Plan(s): To be produced for Physical and Documentary non-compliances at each site. Are to Record the date the problem or aspect was discovered, the nature, location and recommended corrective action for aspects or problems identified. Are to include non-compliances or non-conformances that are outstanding from the previous SCIDA audits. These are to be escalated accordingly and entered on the relevant Risk Register as required. Non-conformances are to be detailed on Action Plans and referenced correctly to the relevant JSP 453: Defence ICT Installation Standard chapter and Paragraph and any associated Statutory Instrument, standard, policy etc. | As per agreed schedule. | - Provide and Maintain a Live SCIDA audit program detailing all sites and facilities, in the Air SCIDA Configuration Boundary (see Current ‘Master Site List’ extract at Annex D for details). The audit plan shall clearly articulate: The areas to be audited, the scheduled date and completion date of audits, SL allocations, SLA version and date, Information justifying delays, Site address and POC details, as a minimum. - Complete periodic audits at the following minimum frequency: SL1 Annually. SL2 Two Yearly (Target - 50% per year). SL3 When called for by the sites, by the authority or SCIDA providers discretion. - As SL3 sites are not routinely audited under this contract, in order to ensure site contact is maintained, successful contact should be attempted annually, and date details included in the Master Site List (or equivalent). Where no contact can be made, details must be included in the QPR and discussed at the QPM. - Where it was not possible to complete an audit of individual areas during the planned audit period this shall be notified to Air CySC who will assess the risk and instruct Air SCIDA accordingly. - Following completion of the audit, any non-compliances or non-conformances presenting a risk are to be reported to the relevant risk owner for inclusion on the relevant risk register and risk numbers allocated for future reference. Immediate risks are to be reported to the relevant risk owner at the time of the audit. . - Within 10 working days a comprehensive Audit Report, complete with Action Plans, to be issued to the relevant stakeholders (HoE, FM Team etc). - Within 30 working days of discovery, investigate all non-compliances from JSP 453. - When unauthorised change has been identified, a retrospective change process is to be carried out and attempts made to prevent reoccurrence. The unauthorised change agent shall be identified, and the details provided to the relevant stakeholder. |
| B.5.1 | ITSM Tooling (Audit Tracking and Live Audit Report) | Audit reports. Currently produced as standalone MS Word documents (examples in Annex L). Audit scheduling is currently achieved through complex Microsoft Excel Spreadsheet (example in Annex L and at Excel File 20250314-Master Site List Extract). SCIDA delivery suppliers and Air CySC teams would benefit from efficiency and visibility improvements in audit scheduling, reporting, non-compliance recording, storage and management (e.g. using e.g. Microsoft PowerApps, Power Bi, Dataverse etc) if suitable. Data would be a minimum of Official Sensitive (OS) requiring use of a suitably accredited company system or able to be homed on MODNet. | Solution should deliver: Audits. Observations gathered ‘live’. Report generation fully or partially automated. Reports available in a small number of formats/templates, observations to be filterable on any heading/category (e.g. Site, Building, Category (Electrical Safety, Security, Availability etc). Dashboards. To include facility to output Audit and ECR tracking data to ‘dashboard(s)’. Tracker: Improvements to or new tools for tracking Site Audits and ECRs. | Audit Reporting Tool, Trackers and Dashboards available 24/7 to authorised users. Initial development and annual upkeep costs to be detailed in the miscellaneous costs section of Commercial Cost Workbook. |
| Bespoke Air SCIDA Tasks |  |  |  |  |
| B.6 | Provide Technical Advisor (TA) services to Air CySC CIS Infra as tasked by Air CySC. | Provide a minimum of 4 x Full Time suitably qualified and experienced Engineers, to act as Technical Advisors. This shall be a resource tasked directly by the Authority. Whereas this number of TAs is sufficient to cover most projects known to the authority, other suitable Engineering resource in the workforce should be trained/prepared to provide surge assistance when required. This is currently provided by using experienced Site Engineers in a Hybrid role as required and where this can be achieved without detriment to the Air SCIDA BAU service. Individuals in these roles shall meet the qualifications and/or experience requirements detailed in Annex F. Deliver Technical Advisor services to Air CySC CIS Infra. Examples are: Produce CIS Specifications that incorporate user CIS requirements detailed in URD, IER and other inputs to ensure that CIS requirements for projects allocated to them are understood by contractors and that contractors are informed of and adhere to the standards and requirements defined in associated CIS Specs. Ensure timely submission of NSSR and other communications request processes. Act as the focal point to ensure adherence by all parties to engineering standards as set out in applicable British Standards and MOD publications such as JSP 453, JSP 440, and SDIP 29, as referenced in the CIS Specification. When required, act as a representative of Air CySC CIS Infra CIS specialists. Attend site meetings, project meetings. Liaise with Station communication staffs and project stakeholders. Ensure JSP 453 ECR process is followed for all project tasks. Throughout all stages of a project, consult closely with the SCIDA site engineer to ensure any impact on other projects or engineering and other changes outside the TA project boundary is considered. | Minimum 4 x Full Time SQEP (as indicated at Annex I). Service as per agreed Authority tasking. | - Complete tasks/Projects as prioritised and allocated by Air CySC. - Ensure Resilience and Succession Planning measures to ensure continuity of service. - Contractors must provide an explanation of how they will ensure sufficient trained and knowledgeable workforce levels are maintained to support this function. - Report on progress towards surge manpower availability at QPR/QPM. |
| B.7 | Provision of Outside Plant (OSP) support. (see also Annex H) | Primary Responsibilities: Provide an OSP Team as a resource available to, and tasked by, the Authority to undertake the following: - Maintain the SCIDA Record of Notified Cable Routes contained within the Stn OSP system to aid swift rectification of Operational faults. (Using The SCIDA Master Duct Record Template). - Maintain the Site Pit and Duct Plan Baseline Drawings. (This may require some additional survey work to identify un-labelled cables if required). - Maintain the Stn Records of any proposed, completed, and scheduled OSP maintenance and provide a schedule of recommended maintenance for the OC ICT section or equivalent to endorse, fund and implement per annum through Stn Services Sqn. - Attend all relevant Stn siting boards to act as the specialist advisor on OSP to Stn DSF/FST or ICT section. - Ensure that all Contractors who are working through an authorised ECR are aware of the site duct management controls, the JSP 453 and other required standards. - As tasked by Air CySC, and within the limits of available resource declared at the start of the contract, complete subsets of the tasks listed at Annex J to ensure RAF OSP is adequately managed and maintained. | OSP Team – Currently 2 FT staff + 4 Contractors. Service as per agreed Authority tasking. | - Complete tasks/Projects as prioritised and allocated by Air CySC. - Ensure Resilience and Succession Planning measures to ensure continuity of service. - Contractors must provide an explanation of how they will ensure sufficient trained and knowledgeable workforce levels are maintained to support this function. |
| B.8 | Uplifted support for Specific Location(s) at RAF High Wycombe (inc buildings supplying critical ICT Support services). (Areas covered by 20241023-Joint User Proposal for SCIDA Demarcation Agreement-V1.1-SUKEO are excluded) | In addition to the services delivered to standard sites: CMDB - Provide Microsoft Office compatible databases, spreadsheets etc detailing all installed cables, horizontal and vertical infrastructure, patch panel port utilisation and end point information. This information, and associated SCIDA drawings, could be classed at up to Tier 3 however, in consultation with and the agreement of RAFP, contractors can obfuscate documents to reduce the classification and so provide wider visibility/distribution to external agencies. Installation Design Service. - These tasks must be authorised by the contract manager. Requests for this service should be submitted through the contract manager who will in turn request an impact statement from Air SCIDA before deciding whether to authorise the task. Design will be limited to ICT equipment and infrastructure provision and will require consultation with SMEs in other specialisations (H&S, Fire, Security, FM…). Designs could include a requirement for Statement of Work and drawings and will meet all the requirements of MOD Policy, British Standards, International Standards and European norms. Any resulting SOW will include details of connectivity, cable routes and notional lengths, patching, and any additional equipment required. Cable identities will also be supplied. - Drawings produced as part of this service are to include details of all furniture, power, cable containment and connectivity outlets required in support of the ICT installation. UORs - Provide support as required to facilitate special tasking. Contract Manager to task SCIDA directly along with authority to suspend Business as Usual (BAU) tasks for the duration where required. Data Availability. All facility drawings, databases, and spreadsheets to be available to appropriately cleared ICT staff 24/7. | Minimum 2 staff members fully acquainted with all systems and infrastructure. | - Ensure Resilience and Succession Planning measures to ensure continuity of service. - Contractors must provide an explanation of how they will ensure sufficient trained and knowledgeable workforce levels are maintained to support these key locations. |
| B.9 | Supplementary support package to RAF High Wycombe, Sites 1, 2 and 3 inclusive | In addition to the services delivered to standard sites: Installation Design Service. - These tasks must be authorised by the contract manager. Requests for this service should be submitted through the contract manager who will in turn request an impact statement from Air SCIDA before deciding whether to authorise the task. Design will be limited to ICT equipment and infrastructure provision and may require consultation with SMEs in other specialisations (H&S, Fire, Security, FM…). Designs will meet all the requirements of MOD Policy, British Standards, International Standards and European norms. Any resulting SOW will include details of connectivity, cable routes and notional lengths, patching, and any additional equipment required. Cable identities will also be supplied. Drawings produced as part of this service are to include details of all furniture, power, cable containment and connectivity outlets required in support of the ICT installation. | Service as per agreed Authority tasking. | No failure to deliver agreed service. Failures to be reported at/in QPM/QPR (see Req A.f.10 & 11) |
| B.10 | Support to Project MARSHALL. Provide enhanced support to Project MARSHALL. | Manage the ECR 1-5 and BUS process on behalf of the Project MARSHALL DT. Liaise with regional / site SCIDA representatives to ensure a consistent approach during audits of MARSHALL sites. Auditing approach is to remain consistent with the processes detailed at Item B.5. Conduct audits and inspections on behalf of the DT on sites in the MARSHALL WAM portion of the Site List at Annex D; allowances must be made for slight changes to the list as the project progresses towards its conclusion and the final site laydown is confirmed (additions and subtractions). Provide SCIDA related guidance and advice to DT and the MARSHALL Prime Contractor (Aquila) to include guidance on regulatory changes to the JSP 453. Provide SCIDA related guidance and advice to Falkland Islands SCIDA service users. This is to be limited to telephone or basic email support only. Where it is felt that such support is impinging on the service provided to Air Sites this shall be brought to the attention of the contract manager and discussed at the next QPM. Provide two SCIDA briefings per year to the MARSHALL DT regarding the role of SCIDA and all the processes relevant to the program. | Previously 2 dedicated engineers. If supplier solution does not provide dedicated staff then an uplift in overall SCIDA Engineer numbers would be required to provide the service requested by, and agreed with, Marshall DT. | Core services in accordance with previous requirements. No failure to deliver agreed bespoke service. Failures to be reported at/in QPM/QPR (see Req A.f.10 & 11) |
| B.11 | IPZ and SCIDA Process alignment. (Costed Option). | Assist in IPZ and Air SCIDA process integration and assist with audit as directed by RAF Digital. | 2 x SQEP Engineers to undertake tasks as directed; must be DV cleared. Suggest that qualifications and experience levels required equate to resource for B.12.b or c levels below. Initial estimate is that the task could involve visits to 44 Sites over a 2-year period. All equipment required for the task will be available through client resources. | Resource to provide service(s) agreed when and if tasks added to contract |
| B.12 | CAD, TA, Engineer Resource Uplift (Call Off Option) | Call off service to cater for increases in scope (site additions, Major New Projects) which necessitate an increase the number of CAD Tech and TAs/Engineers. | Day rates to be detailed for the following: - CAD Tech - Site Engineer - Technical Advisor | Resource to provide service(s) agreed when and if tasks added to contract |

Annex A to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Air SCIDA Service Level Application

| SCIDA SERVICE LEVEL | SERVICE LEVEL ALLOCATION CRITERIA SITE/FACILITY/SYSTEM | SCIDA CHANGE CONTROL | MINIMUM MANDATORY AUDIT FREQUENCY | CM DOCUMENT REQUIREMENT | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 1. Any RED IPZ containing RED ICT. 2. Any Room/NER housing Tier 3 Equipment (see Note 1). 3. Supporting flight or maritime safety. 4. Where otherwise justified on Operational grounds. | 1. Establish a CMDB Baseline and maintain through a formal change process accordingly. 2. Full ECR process mandatory. | 12 months. | Establish and maintain a minimum CMDB data set as per Table at Annex H Para 11, inclusive of TEMPEST coupling zones. | 1. Manage the ECR process (or equivalent). 2. Implement measures to prevent unauthorised change. 3. Maintain the CMDB and associated documentation. 4. Conduct mandatory audits. |
| 1a | Structures housing C-E/ICT/ATM/ASACS equipment which are fully controlled by the system supplier. | As for SL1 Above, with variations as per note 2. |  |  |  |
| 2 | 1. Any AMBER IPZ containing RED ICT. 2. Any Room/NER housing Tier 2 or Crypto Equipment (see Note 1). 3. Any Operationally significant NER housing Tier 1 Equipment (see Note 1). 4. Where otherwise justified on Operational grounds. | 1. Establish a CMDB Baseline and maintain through a formal change process accordingly. 2. Full ECR process mandatory. | 24 months. | Establish and maintain a minimum CMDB data set as per Table at Annex H Para 11, inclusive of TEMPEST coupling zones. | 1. Manage the ECR process (or equivalent). 2. Implement measures to prevent unauthorised change. 3. Maintain the CMDB and associated documentation. 4. Conduct mandatory audits. |
| 3 | 1. Any GREEN or YELLOW IPZ. 2. All other exclusively Tier 1 business environments. | 1. Full ECR process mandatory. | On request by sites, the authority or at SCIDA providers discretion. | Establish and maintain a minimum CMDB data set as per Table at Annex H Para 11. | 1. Manage the ECR process (or equivalent). 2. Implement measures to prevent unauthorised change. 3. Maintain the CMDB and associated documentation. |
| Notes | 1. NER: For the purpose of this contract, an NER is defined as ‘A room which is a dedicated room hosting network communication devices i.e. routers, switches, firewalls, computers, servers, storage devices, database servers, routers etc’. Offices or other rooms where other activity is the primary purpose of the room may also host ICT cabinets housing floor distribution and limited Network equipment; however, these are not classed as NERs. SCIDA discretion to be applied regarding ‘Operationally Significant’ after consideration of the impact to departmental/operational output; any variation will require agreement of the site through the signature on the SLA. DD Core NERs and cabinets should be treated as operationally significant, therefore SL2. 2. SL1a: SCIDA responsibilities are limited or vary to those applicable to regular buildings and rooms. Following each ECR and Audit, Air SCIDA must ensure that the supplier’s/maintainer’s provided floor plans, wall views, rack layout drawings and all other information is accurate. Where this is not the case, requests for amendment shall be submitted to the supplier and hastened at least quarterly. Should requests for updated drawings be problematic, escalation action to be undertaken through the appropriate Role Office. All drawings and other CMDB data must be retained as part of the CMDB in a location where the most up to date information is easy to locate. Within registers, SL1a designated sites shall have comments added which detail the limitations to SCIDA service delivery and justifications for such. 3. OSP. CIDA Direction Note CDN/2024-001: ‘Service Levels are now aligned with Information Protection Zones (IPZ) and other specified criteria. Outside Plant (OSP) will likely never be assigned an IPZ however, this supporting infrastructure still requires ongoing Site Coordinating Installation Design Authority (SCIDA) governance and assurance’. On Air Sites, the dedicated OSP Team will be directed by the authority to undertake inspections and other tasks as detailed within and limited by the requirement in the contract. - 4. ECR Process: JSP 453 details the ECR process. |  |  |  |  |

Annex B to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Abbreviations & Terminology

| AAC | Army Air Corps |
| --- | --- |
| ACF | Air Cadet Force |
| ACHQ | Air Cadet HQ |
| ACIO | Army Careers Information Office |
| ACOS | Assistant Chief Of Staff |
| ACR | Air Cadet Region |
| ACT | Army Cadet Team |
| ACW | Air Cadet Wing |
| AF | Airfield |
| AFCO | Armed Forces Careers Office |
| AGS | Astra Ground School |
| AOC | Air Officer Commanding |
| AOR | Area Of Responsibility |
| AS | Above Secret (Protective Marking) |
| ASACS | Air Surveillance and Control Systems |
| ATC | Air Traffic Control |
| ATM | Air Traffic Management |
| ATO | Authorised Telecommunications Officer |
| A&SWC | Air & Space Warfare Centre |
| AWR | Air Weapons Range |
| BAU | Business As Usual |
| BEP | Building Entry Point |
| BMEWS | Ballistic Missile Early Warning System |
| BS | British Standard |
| BUS | Beneficial Use Statement |
| CAD | Computer Aided Design |
| CAM | Center for Aviation Medicine |
| CC | Configuration Control |
| CDIO | Chief Defence Information Officer |
| CE | Communication Electronics (C-E) |
| CIDA | Configuration Installation Design Authority |
| CIS | Communication & Information Systems |
| CM | Configuration Management |
| CMDB | Configuration Management Database |
| CMS | Cable Management System |
| DCAE | Defence College of Aeronautical Engineering |
| DCTT | Defence College of Technical Training |
| DE | Defence Enterprise |
| DIO | Defence Infrastructure Organisation |
| DO | Designated Officer |
| DT | Delivery Team |
| DTE | Defence Training Estate |
| DV | Developed Vetting (Security Clearance Level) |
| ECR | Engineering Change Request |
| EMC | Electromagnetic Compatibility |
| EMPP | Electromagnetic Pulse Protection |
| EOFT | Engineering Officer Foundation Training |
| ESO | Establishment Security Officer |
| FM | Facilities Management |
| GFA | Government Furnished Assets |
| H&S | Health & Safety |
| HMG | His Majesty's Government |
| HMNB | His Majesty's Naval Base |
| HMS | His Majesty's Ship |
| HOE | Head Of Establishment |
| HQ | Headquarters |
| HRDF | High Resolution Direction Finder (Navigation Aid) |
| HSW | Health & Safety at Work |
| HVAC | Heating Ventilation & Air Conditioning |
| ICT | Information and Communication Technology (also identified as CIS) |
| IDA | Installation Design Authority |
| IET | Institute of Engineering and Technology |
| IPZ | Information Protection Zone |
| IT | Information Technology |
| JHC | Joint Helicopter Command |
| JSP | Joint Service Publication |
| KPI | Key Performance Indicator |
| KR | Kings Regulations |
| LAN | Local Area Network |
| MOB | Main Operating Base |
| MOD | Ministry of Defence |
| MSL | Master Site List |
| NATO | North Atlantic Treaty Organisation |
| NATS | National Air Traffic Service |
| NER | Network Equipment Room |
| NSSR | Non-Standard Service Request (DD Process) |
| OC | Officer Commanding |
| OPS | Operations |
| OS | Official Sensitive (Protective Marking) |
| OSP | Outside Plant (ICT Pits and Ducts) |
| PM | Project Manager |
| POC | Point Of Contact |
| POF | Point Of Failure |
| PSTN | Public Service Telephone Network |
| QA | Quality Assurance |
| QPM | Quarterly Progress Meeting |
| QPR | Quarterly Progress Report |
| RAAF | Royal Auxiliary Air Force |
| RAF | Royal Air Force |
| RAFAC | Royal Air Force Air Cadets |
| RAFP | Royal Air Force Police |
| RED | Term sued to describe any document or item which is Secret or Above |
| RF | Radio Frequency |
| RLG | Relief Landing Ground |
| RMB | Royal Marines Base |
| RNAS | Royal Naval Air Station |
| RRH | Remote Radar Head |
| RRS | Remote Radio Site |
| RSP | Radio Site Protection |
| SC | Security Check (Security Clearance Level) |
| SCIDA | Site Co-ordinating Installation Design Authority |
| SDIP | NATO Document Dealing with TEMPEST requirements |
| SHEF | Station Health & Environmental Flight |
| SL | Service Level |
| SLA | Single Living Accommodation |
| SLAM | Single Living Accommodation Modular |
| SME | Subject Matter Expert |
| SOR | Statement Of Requirement (this document) |
| SOW | Statement Of Work |
| SPF | Security Policy Framework |
| SPOF | Single Point of Failure |
| SQACR | Standard Quality Assurance Contractual Requirements |
| SQEP | Suitably Qualified and Experienced Personnel |
| SSSB | Ship Shore Ship Buffer |
| Stn | Station |
| STRAP | Used to describe some areas working at AS |
| STRAPSO | STRAP Officer |
| SU | Signals Unit |
| TA | Technical Advisor |
| TAP | Terminal Access Point (connection for fixed LAN services) |
| TBA | To Be Announced |
| TBC | To Be Confirmed |
| TCA | TEMPEST Countermeasures Assessment |
| TEMPEST | Term used to describe study of unintentional Electromagnetic Emanations |
| TIER 1 | Term used to denote processing/Data/Equipment with a protective marking of Official |
| TIER 2 | Term used to denote processing/Data/Equipment with a protective marking of Secret |
| TIER 3 | Term used to denote processing/Data/Equipment with a protective marking of Above Secret |
| TL | Team Leader |
| TLB | Top Level Budget |
| TSCM | Technical Surveillance Counter Measures |
| TVI | TEMPEST Visual Inspection |
| TX | Transmitter |
| UAD | User Access Device (PC, Laptop etc) |
| UAS | Air Squadron |
| UGDP | Underground Duct & Plant (same as OSP) |
| UOR | Urgent Operational Requirement |
| UPS | Uninterruptible Power Supply |
| VGS | Voluntary Gliding School |
| WAM | Wide Area Multilateration (Navigation Aid) |
| WAP | Wireless Access Point |
| WHQ | Wing Headquarters |
| WOC | Wing Operations Center |

Annex C to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

MOD Policy references

- In addition to the references detailed in the Terms and Conditions of the Contract the following references shall also apply as well as any subsequent revisions and amendments to the references. This list does not absolve the Contractor from conforming to any other relevant publications.

- Key publications at the time of writing:

  - JSP 453 - Defence ICT Installation Standard. Publicly available Via Defence Connect (accounts to be requested through CIDA).

  - CIDA Governance - SCIDA Framework issue 2.1 (the Framework Document). This version attached; updated versions publicly available Via Defence Connect (accounts to be requested through CIDA).

Annex D to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Air SCIDA Master Site List

- The Sites to be covered by this contract are detailed below (as at 13/4/25). The site list can vary throughout the period of the contract and may change slightly during the tender process. An indicative map (20250422-Air SCIDA UK Map) is included as an attachment to the main SOR document.

- POCs for some sites may have changed, especially SL3 sites, which are not routinely contacted under current contract requirements.

| # | Station | Zone | Address | Scope Limitations |
| --- | --- | --- | --- | --- |
| Standard Sites |  |  |  |  |
| 1 | Aberporth | North | Mod Aberporth, Cardigan, Ceredigion,Wales, SA43 2BU | MOD Assets only. Inc ATM (Marshall) Equipment |
| 2 | Alconbury | Central | Alconbury, Huntington, Cambs, PE28 4DA | ATM - Only supports Bldg 564 - DIO Server Rm |
| 3 | RAF Akrotiri | South | Aquila Maintenance manager, Aquila Site Office RAF Akrotiri BFPO 57. Mil 94120 ext 5765, PSTN. +3572527 then ext no. | Limited primarily to ATM areas only |
| 4 | Aldergrove FS | North | 38 (Irish) Bde Aldergrove FS, BFPO 808 |  |
| 5 | RAF Barkston Heath | Central | RAF Barkston Heath, Grantham NG32 2DQ |  |
| 6 | Barnham | Central | RAF Barnham, Barnham, Thetford, Suffolk, IP24 2DJ |  |
| 7 | RRH Benbecula (Sth Cletraval) | North | RRH Benbecula, South Clettraval, Lochmaddy HS6 5DL |  |
| 8 | RAF Benson Airfield | South | RAF Benson, Benson, Ewelme, Wallingford OX10 6AA |  |
| 9 | MOD Boscombe Down | South | Ground Radio Maintenance Section, ATC Tower, Boscombe Down, Amesbury, Wiltshire SP4 0JF | Air SCIDA covers ATC, Nav-aids and the MOD Networks on site. Includes SUAS & Air Cadets Wing |
| 10 | RAF Boulmer | North | RAF Boulmer, Alnwick, Northumberland, NE66 3JF |  |
| 11 | Brawdy | North | Cawdor Barracks, Brawdy, Pembrokeshire, SA62 6NN |  |
| 12 | RAF Brize Norton | South | RAF Brize Norton, Carterton, Oxon OX18 1LD |  |
| 13 | RRH Brizlee Wood | North | Via RAF Boulmer, Alnwick, Northumberland, NE66 3JF (unit approx. 11 miles from RAF Boulmer) |  |
| 14 | RRH Buchan | North | Remote Radar Head Buchan, Peterhead, Aberdeenshire, AB42 0NX |  |
| 15 | Chivenor | South | RMB Chivenor, Chivenor, Braunton, Barnstaple, ECX31 4AZ | Chivenor airfield includes active Auto Triangulation and HRDF. Lobb Hill has radios and MSSR marker for Hartland Point Watchman. |
| 16 | RAF Coningsby | Central | RAF Coningsby, Coningsby, Lincolnshire, LN4 4SY |  |
| 17 | RAF Cosford | North | RAF Cosford, Albrighton, Wolverhampton, WV7 3EX | Includes Stafford Heliops |
| 18 | RAF Cranwell | Central | RAF College Cranwell Sleaford, Lincolnshire NG34 8HB |  |
| 19 | Credenhill | North | Hereford Camp, Credenhill, Herefordshire, HR4 7DD |  |
| 20 | RAF Croughton | Central | RAF Croughton, Brackley, Northants, NN17 5XP | Bldgs 62, 30 and 34 |
| 21 | RNAS Culdrose | South | RNAS Culdrose, HMS Seahawk, Helston, TR12 7RH |  |
| 22 | DTE Donna Nook | Central | RAF Donna Nook, North Somercoates, Louth, Lincs, LN11 7PB |  |
| 23 | Durham Tees Valley Airport | North | Draken Ltd, Durham Tees Valley Airport, Darlington County Durham, DL2 1NJ | MoD Assets Only |
| 24 | 603 Sqn RAAF Edinburgh (Inc AO Scotland) | North | 25 Learmonth Terrace, Edinburgh, EH4 1NZ |  |
| 25 | RAF Fairford | South | Bldg 2 RAF Fairford, Gloucestershire, GL7 4DL. | USAF - Only responsible for the MOD networks, do not cover the ATC tower |
| 26 | Fleetlands | South | MOD Fleetlands Heliport, Fareham Road, Gosport, Hampshire, PO13 0AA | Only cover the Heliport. |
| 27 | Fylingdales | North | RAF Fylingdales, Pickering, North Yorkshire, YO18 7NT |  |
| 28 | Gibraltar | Central | RAF Gibraltar, Mouchotte Bldg, Spitfire Way, MOD Gibraltar BFPO 52 |  |
| 29 | RAF Halton | HWY | DSF, Ops & Plans Wing, RAF Halton, Aylesbury Bucks HP22 5PG |  |
| 30 | Hartland Point | South | Hartland Point Radar, EX39 6AU | Watchman and MSSR site - parented by RNAS Yeovilton |
| 31 | Hebrides Range Control | North | MOD Range Hebrides, Balivanich, Isle of Benbecula HS7 5LA | Flight Safety Systems Only |
| 32 | RAF Henlow | Central | RAF Henlow, Beds, SG16 6DN |  |
| 33 | AWR Holbeach | Central | RAF Holbeach, AWR Dawsmere, Spalding, Lincs, PE12 9NJ |  |
| 34 | RAF Honington | Central | RAF Honington, Bury St Edmonds, Suffolk, IP31 1EE |  |
| 35 | Hurn Civil | South | Draken Europe, Bournemouth Intl Airport, Christchurch, Dorset, BH23 6NE. |  |
| 36 | TA Centre - Kings Park Glasgow (602 Sqn RAuxAF) | North | 155 Carmunnock Road, Glasgow, G44 5SS |  |
| 37 | Kinloss RLG | North | Kinloss Barracks, FORRES, Kinloss, IV36 3UH | MSSR remains until replaced by WAM. |
| 38 | RAF Lakenheath | Central | RAF Lakenheath, Brandon, IP 27 9PS | USAF – MOD Buildings only |
| 39 | RAF Leeming | North | 90 SIGNALS UNIT, RAF Leeming, Northallerton, North Yorkshire, DL7 9NJ |  |
| 40 | RAF Leuchars Airfield | North | Leuchars Station, St Andrews, Fife, KY16 0JX | Flight Safety systems only, Includes ESUAS, HQ Air Cadets, Air Cadets Region, Bldgs 415 and 513 |
| 41 | RNAS Lilstock | South | Lilstock ranges, TA5 1SU |  |
| 42 | Little Rissington HRDF | South | RAF Little Rissington, Great Rissington, Cheltenham GL54 2RJ | Only DF building and VGS. |
| 43 | RAF Lossiemouth | North | RAF Lossiemouth, Lossiemouth, Moray, IV31 6SD |  |
| 44 | Manston HRDF | South | See RAF Odiham, for access to site. | DF Bullding only |
| 45 | RAF Marham | Central | RAF Marham, Kings Lynn, Norfolk, PE33 9NP |  |
| 46 | RAF Menwith Hill | North | RAF Menwith Hill, Harrogate, North Yorkshire, HG3 2RF |  |
| 47 | RNAS Merryfield | South | RNAS Merryfield, Ilton, Ilminster, TA19 9HN |  |
| 48 | Middle Wallop | South | AAC Middle Wallop, Stockbridge, Hants, SO20 8DY | ATC and Nav-aids only |
| 49 | RAF Mildenhall | Central | RAF Mildenhall, Bury St Edmunds, IP28 8NF | USAF - MOD Defence Estates Bldg only |
| 50 | RAF Molesworth | Central | RAF Molesworth, Huntingdon, Cambs, PE28 0QB | USAF - UK Cabin 2, Bldg 326, 314, 400 (Rms 16 & 1) |
| 51 | RAF Mona | North | Mona Airfield, Gwalchmai, Isle of Anglesey, LL65 4RP |  |
| 52 | RRH Neatishead | Central | RRH Neatishead, Norwich, Norfolk, NR12 8YB | Includes remote Txer & Rxer Sites |
| 53 | Netheravon | South | SAFISO Netheravon, AFIS Tower, Airfield camp, Netheravon, Salisbury, Wiltshire, SP4 9SF. | ATC building only |
| 54 | Newcastle HRDF | North | Newcastle Airport, Woolsington, Newcastle-Upon-Tyne, NE13 8BZ |  |
| 55 | RAF Northolt | HWY | DSF, Bentley Priory Bldg, RAF Northolt, Middlesex HA4 6NG |  |
| 56 | RAF Odiham | South | RAF Odiham, Hook Hampshire RG29 1QT Tel 01256 367618 or 95235 7618) |  |
| 57 | Otterburn Camp | North | Range Control, Otterburn Camp, Otterburn, Northumberland, NE19 1NX |  |
| 58 | RAF Pembrey Sands | North | Admin Office; DIO Pembrey Sands; PEMBREY; Burry Port. Carmarthen. DYFED. SA16 0NR |  |
| 59 | Plymouth Military Radar | South | HMNB Devonport, Camels gate, Devonport, PL2 2BG | Includes Wembury Point (HMS Cambridge - ARIP, Watchman and MSSR Site) Fort Staddon G2A and MSSR marke |
| 60 | Portland | South | Portland radar, Grove Road, Grove, Portlamd DT5 1DL |  |
| 61 | RRH Portreath | South | RRH Portreath, Toltiken Road, Redruth, TR16 4RA |  |
| 62 | Prestwick Airport HRDF | North | Glasgow Prestwick Airport, Aviation House, Prestwick, KA9 2PL | Flight Safety Systems/areas only |
| 63 | RRH Saxa Vord | North | 31 Setters Hill Estate, Baltasound, UNST, Shetland, ZE2 9DU |  |
| 64 | RAF Shawbury | North | RAF Shawbury, Shrewsbury, Shropshire, SY4 4DZ | Includes Grinshill however no access as all visitors need to be confined space trained |
| 65 | Silloth | North | (Silloth Wigton, Cumbria, CA7 4PA) C/O RAF Spadeadam, Guilsland, Cumbria, CA8 7AT |  |
| 66 | RAF Spadeadam | North | RAF Spadeadam, Guilsland, Cumbria, CA8 7AT |  |
| 67 | St Athan HRDF | North | Bldg 419 MOD St Athan, Barry, Vale of Glamorgan, Cardiff, CF62 4WA |  |
| 68 | St Kilda | North | OS Grid Reference NF095995 | Flight Safety Systems Only |
| 69 | RAF St Mawgan | South | RAF St. Mawgan, Bldg 663, St. Mawgan, TR8 4HP |  |
| 70 | RRH Staxton Wold | North | RRH Staxton Wold, Scarborough, North Yorkshire, YO12 4TJ |  |
| 71 | Stornoway HRDF | North | Stornoway Airport, Isle of Lewis, HS2 0BN |  |
| 72 | Swanwick | South | 78 Sqn – Swanwick, NATS Swanwick, Sopwith Way, Hampshire SO31 7AY | NATs site – ASACS CRC areas only. |
| 73 | RRS Swingate | HWY | RRS Swingate, Dover, Kent CT15 5DW |  |
| 74 | RAF Syerston | Central | RAF Syerston, Newark NG23 5NN |  |
| 75 | DIO Tain | North | Tain Air Weapons Range, FENDOM, IV19 1PE |  |
| 76 | RAF Ternhill | North | Clive Barracks, Tern Hill, Market Drayton, TF9 3QE |  |
| 77 | Thorney Island | South | See RAF Odiham, for access to site. | Only responsible for the DF building on the disused Airfield. |
| 78 | Tiree HRDF | North | Tiree Airport, Crossapol, Isle of Tiree, PA77 6UW |  |
| 79 | RAF Topcliffe | North | RAF Topcliffe, Alanbrooke Barracks,Thirsk, YO7 3DZ |  |
| 80 | RRH Trimingham | Central | RRH Trimingham, Trimingham, Norfolk, NR11 8DX |  |
| 81 | RAF Valley Airfield | North | RAF Valley, Holyhead, Isle of Anglesey, LL65 3NY |  |
| 82 | RAF Waddington | Central | RAF Waddington, Lincoln LN5 9NB |  |
| 83 | Warton Airfield | North | BAE Warton, Preston, Lancashire, PR4 1AX | Secret Assets only. |
| 84 | Wattisham Airfield | Central | Wattisham Airfield, Ipswich, IP7 7RA |  |
| 85 | RAF Welford | South | Under the RAFLO at Fairford | USAF – MOD Buildings only |
| 86 | MOD West Freugh | North | Qinetiq, MoD West Freugh, Stranraer, DG9 9DN | Flight Safety Systems/areas only |
| 87 | Weston On The Green | South | RAF Weston-on-the-Green, Bicester, Oxon, OX25 3TQ |  |
| 88 | Wick NATS HRDF | North | Wick John O’Groats Airport, CAITHNESS, KW1 4QP |  |
| 89 | Windy Head NATS HRDF | North | NATS Windyhead Radio Station, New Aberdour, Aberdeenshire, AB43 6JH |  |
| 90 | RAF Wittering | Central | RAF Wittering, Peterborough, PE8 6HB |  |
| 91 | RAF Woodhall Spa | Central | LN4 4PQ - Near RAF Coningsby, Coningsby, Lincolnshire, LN4 4SY |  |
| 92 | RAF Woodvale ATC | North | RAF Woodvale, Formby, Liverpool, L37 7AD |  |
| 93 | RNAS Yeovilton | South | RNAS Yeovilton, Heathcote Road, Yeovil, BA22 8HT | Flight Safety Systems/areas only |
| 94 | RAF High Wycombe | HWY | RAF High Wcombe, Walters Ash, High Wycombe, Bucks, HP14 4UE |  |
| 95 | Blandford Camp | South | Camp Support Unit DSCIS DCTT Harrogate Building Blandford Camp Blandford Forum DT11 8RH | 22Gp and some lodger Units |
| 96 | RRC Crickhowell | North | Robson Resilience Centre Crickhowell-RRC(C), Cwrt-y-Gollen, Crickhowell, NP8 1TE |  |
| 97 | NACATC Fairbourne | North | Plas Yr Antur, Waverley Rd, Fairbourne, LL38 2PJ |  |
| 98 | RAF Feltwell | Central | RAF Feltwell, Thetford, IP26 4HL |  |
| 99 | RRGC Grantown On Spey | North | Old Drill Hall, Forest Road, Grantown-on-Spey, PH26 3JL |  |
| 100 | MOD Lyneham | South | The Prince Phillip Barracks, MOD Lyneham, Chippenham, Wilts, SN15 4XX | A and C Sites only |
| Marshall Sites |  |  |  |  |
| 101 | Asgarby (Coningsby Cluster) | WAM-CON | Asgarby, Horncastle Hill, Asgarby, Spilsby, Lincolnshire PE23 4HY |  |
| 102 | Beacon Hill MD (BZN WAM Cluster) | WAM-BZN | SP4 9JJ |  |
| 103 | Beckwith Shaw (LEE (Was Linton) WAM Cluster) | WAM-LOO | Beckwithshaw, Otley Road, Beckwithshaw, HG3 1QX |  |
| 104 | Belmont (Coningsby WAM Cluster) | WAM-CON | Belmont Arqiva Transmitting Station, Near to Belmont House Benniworth, South Willingham, Lincolnshire, LN8 6JT |  |
| 105 | Benson MD - (BZN WAM Cluster) | WAM-BZN | Priory Drive Wallingford OX10 6EW |  |
| 106 | Bilborough (Was Linton WAM Cluster) | WAM-LOO | Bilborough Yorkshire Water, Bilborough, YO23 3PF |  |
| 107 | Bilsdale (LEE (Was Linton) WAM Cluster) | WAM-LEE | Bilsdale, Chop Gate, Bilsdale, TS9 7JU |  |
| 108 | Boscombe Down MD - (BZN WAM Cluster) | WAM-BZN | DERA Amesbury SP4 7LF |  |
| 109 | Bristol Water (BZN WAM Cluster) | WAM-BZN | MAP Location , BS37 6EJ |  |
| 110 | Burnham (Marham WAM Cluster) | WAM-MAR | PE31 8DD |  |
| 111 | Castle Camps Coopers Farm (Marham WAM Cluster) | WAM-MAR | CB21 4TN |  |
| 112 | Old Catterick ATE (Leeming WAM Cluster) | WAM-LEE | Old Catterick ATE, Leeming Lane, Catterick , North Yorkshire, DL10 7JX |  |
| 113 | Christmas Common (BZN WAM Cluster) | WAM-BZN | OX49 5HW |  |
| 114 | Cirencester* (CI) (BZN WAM Cluster) | WAM-BZN | GL7 2PY |  |
| 115 | Clarborough (Coningsby WAM Cluster) | WAM-CON | Clarborough, Howbeck Lane, Retford, Nottinghamshire, DN22 9LW |  |
| 116 | Claxby (Coningsby WAM Cluster) | WAM-CON | Claxby NATS Radar Site, Claxby, Market Rasen, Lincs, LN7 6SS |  |
| 117 | Clun (Shawbury WAM Cluster) | WAM-SHY | Clun, Soudley Wood, Clun, Shropshire, SY7 0JD |  |
| 118 | Kendrew Barracks (Coningsby WAM Cluster) | WAM-CON | Kendrew Barracks Site 1, Cottesmore, Oakham, Rutland, LE15 7BL |  |
| 119 | Coningsby MD part of the Coningsby WAM cluster | WAM-CON | Coningsby MD, Baxter Close, Coningsby, Lincoln, Lincolnshire LN4 4SU |  |
| 120 | Danbury (Marham WAM Cluster) | WAM-MAR | CM3 4NS |  |
| 121 | Dawley Heath Hill (Shawbury WAM Cluster) | WAM-SHY | Shawbury East MDRAF, Shawbury, Shrewsbury, Shropshire, SY4 4EF |  |
| 122 | Dorchester Wardon Hill (Yeovilton Cluster) | WAM-YEO | Not yet confirmed |  |
| 123 | Gatley Long Coppice (Shawbury Cluster) | WAM-SHY | Gatley Long Coppice, Gatley Estate, Leinthall Earls, Leominster, Herefordshire, HR6 9TT |  |
| 124 | Grantham Newgate Lane (Coningsby WAM Cluster) | WAM-CON | Grantham, Newgate Lane, New Gate Lane, Grantham, Lincolnshire, NG31 9HD |  |
| 125 | Hannington (BZN WAM Cluster) | WAM-BZN | RG26 5UD |  |
| 126 | Harmer Hill (Shawbury WAM Cluster) | WAM-SHY | Harmer Hill Reservoir, Higher Road, Shrewsbury, Shropshire, SY4 3RA |  |
| 127 | Henley on Thames - (BZN WAM Cluster) | WAM-BZN | RG9 3HP |  |
| 128 | High Wycombe PWHQ South MD - (BZN WAM Cluster) | WAM-BZN | Hp14 4UE |  |
| 129 | Holyhead (Valley WAM Cluster) | WAM-VAL | Holyhead, South Stack Road, Holyhead, Isle of Anglesey, LL65 1YH |  |
| 130 | Honington MD (Marham Cluster) | WAM-MAR | IP31 1EG |  |
| 131 | Hurst Barn Farm (BZN WAM Cluster) | WAM-BZN | OX14 4LY |  |
| 132 | Kings Lynn (Marham WAM Cluster) | WAM-MAR | PE35 6EJ |  |
| 133 | Knockmore (Lossiemouth Cluster) | WAM-LOS | Knockmore Transmitter, Aberlour, AB38 9RL |  |
| 134 | Lavenham Hall Farm (Marham WAM Cluster) | WAM-MAR | CO10 9SJ |  |
| 135 | Leeming Water Tower (LEE (Was Linton) WAM Cluster) | WAM-LEE | Leeming Water Tower, RAF Leeming, Northallerton, DL7 9NJ |  |
| 136 | Linton MD (Leeming WAM Cluster) | WAM-LEE | Linton-On-Ouse MD, Linton-On-Ouse, York, North Yorkshire, YO30 2TB |  |
| 137 | Llandona (Valley WAM Cluster) | WAM-VAL | Llanddona, Beaumaris, Isle of Anglesey, LL58 8YE |  |
| 138 | Llanfaethlu (Valley WAM Cluster) | WAM-VAL | Llanfaethlu ATE, Llanfaethlu, Isle of Anglesey, LL65 4NP |  |
| 139 | Lopcombe Corner (BZN WAM Cluster) | WAM-BZN | SP5 1BX |  |
| 140 | Maesbury | WAM-YEO | Not yet confirmed |  |
| 141 | Manningtree MF (Marham WAM Cluster) | WAM-MAR | CO11 2NP |  |
| 142 | Marham MD (Marham WAM Cluster - RAF Beachemwell) | WAM-MAR | PE33 9NP |  |
| 143 | MARSTON MAGNA (Yeovilton Cluster) | WAM-YEO | Not yet confirmed |  |
| 144 | Meldrum (Lossiemouth Cluster) | WAM-LOS | Meldrum Mast, Oldmeldrum, Inverurie, AB51 0AE |  |
| 145 | Mendip Transmitter (Yeovilton Cluster) | WAM-YEO | Not yet confirmed |  |
| 146 | Mendlesham (Marham WAM Cluster) | WAM-MAR | IP14 5TR |  |
| 147 | Middle East Farm (Marham WAM Cluster) | WAM-MAR | PE6 0QH |  |
| 148 | Minterne Magna (Yeovilton Cluster) | WAM-YEO | Not yet confirmed |  |
| 149 | Morgans Hill (BZN WAM Cluster) | WAM-BZN | SN10 2LP |  |
| 150 | Mounteagle (Lossiemouth Cluster) | WAM-LOS | Mounteagle, Dingwall, IV8 8PQ |  |
| 151 | Nebo (Valley WAM Cluster) | WAM-VAL | Nebo (S), Nebo Radio Site, Amlwch, Isle of Anglesey, LL68 9NH |  |
| 152 | Nedging Tye (Marham WAM Cluster) | WAM-MAR | IP7 7GA |  |
| 153 | Newton Barrow - (BZN WAM Cluster) | WAM-BZN | SP3 4UG |  |
| 154 | Odiham MD - (BZN WAM Cluster) | WAM-BZN | RG29 1QG |  |
| 155 | Oxford Boars Hill - (BZN WAM Cluster) | WAM-BZN | OX1 5HL |  |
| 156 | Peterborough (Marham WAM Cluster) | WAM-MAR | PE7 3TQ |  |
| 157 | Rumster Forest (Lossiemouth WAM Custer) | WAM-LOS | Rumster Transmitting Station, Latheron KW5 6DJ |  |
| 158 | Salisbury (SA) (BZN WAM Cluster) | WAM-BZN | SP3 4UG |  |
| 159 | Sandy Heath (Marham WAM Cluster) | WAM-MAR | SG19 2NH |  |
| 160 | Shawbury East WAM ((Shawbury WAM Cluster) Non-MOD) | WAM-SHY | Shawbury East MDRAF, Shawbury, Shrewsbury, Shropshire, SY4 4EF |  |
| 161 | Spalding (Coningsby Cluster) | WAM-CON | Spalding, Spalding Sub Station, Off Spalding Drive, Spalding, Lincolnshire, PE12 3BL |  |
| 162 | Staxton Wold MD (LEE (Was Linton) WAM Cluster) | WAM-LEE | Staxton Wold MD, Raf Staxton Wold, Wold Lane, Scarborough, YO12 4TJ |  |
| 163 | Stickney (Coningsby WAM Cluster) | WAM-CON | Stickney, R Collier Haulage Yard, Main Road Stickney, Boston Lincolnshire, PE22 8BZ |  |
| 164 | Stockland Hill SC (Yeovilton Cluster) | WAM-YEO | Not yet confirmed |  |
| 165 | Stoke Holy Cross (Marham WAM Cluster) | WAM-MAR | NR14 8NR |  |
| 166 | The Shrubbery (Chapel Hill) - (Marham WAM Cluster) | WAM-MAR | PE33 9JT |  |
| 167 | Tinwell (Coningsby Cluster) | WAM-CON | Tinwell, Lodge Farm, Steadfold, Lane Stamford, Leicestershire, PE9 3UJ |  |
| 168 | Titterstone (Clee Hill) - Shawbury WAM Cluster | WAM-SHY | Clee Hill, Ludlow, SY8 3NY |  |
| 169 | Topcliffe (MD) - (LEE (Was Linton) WAM Cluster) | WAM-LEE | Topcliffe MD, Alanbrooke Barracks, Thirsk, YO7 3QE |  |
| 170 | Tor Sliasg - Lossiemouth WAM Cluster | WAM-LOS | Tor Sliasg MFR radio transmitter, Unnamed Road Buckie AB56 5ET |  |
| 171 | Waltham (Coningsby WAM Cluster) | WAM-CON | Waltham, Garthorpe Lane, Waltham-on-the-Wolds, Melton Mowbray Leicestershire LE14 4AF |  |
| 172 | Waunfawr (Valley WAM Cluster) | WAM-VAL | Waunfawr, Manweb, Waunfawr, Caernarfon, Gwenydd, LL55 4SE |  |
| 173 | Welshpool Beacon (Shawbury WAM Cluster) | WAM-SHY | Welshpool Beacon Ring, Trelystan, Leighton, Welshpool, SY21 8JA |  |
| 174 | West Runton (Marham WAM Cluster) | WAM-MAR | NR11 8QE |  |
| 175 | Winchester Sparsholt (WIC) - 2 (BZN WAM Cluster) | WAM-BZN | SO22 5QT Crabwood Farm Old Sarum Road |  |
| 176 | Wisbech (Marham WAM Cluster) | WAM-MAR | PE13 2QA |  |
| 177 | Woodbridge Debach (Marham WAM Cluster) | WAM-MAR | IP13 6BY |  |
| 178 | Wyberton (Coningsby WAM Cluster) | WAM-CON | Wyberton, Millennium Communications, Riverside Industrial Estate, Boston, Lincolnshire, PE21 7SL |  |
| 179 | Yeovilton MD (Yeovilton Cluster) | WAM-YEO | Not yet confirmed |  |
| SL3 Sites |  |  |  |  |
| 180 | Aberdeen AFCO | North | 63 Belmont St Aberdeen AB10 1JS - POC Craig Mitchell 01224 640251 |  |
| 181 | Cambridge ACIO | Central | 2 Glisson Road CB1 2HD - POC SSgt Barker 01223 358060 |  |
| 182 | Gloucester AFCO | South | Railway House, Bruton Way GL1 1DG - POC Flt Lt Paul Moss 01452 502011 |  |
| 183 | Hull AFCO | North | Wenlock Barracks, Anlaby Road, Hull HU3 6PB. POC CPO Chris Day 94786 2532 or 01482 232532 |  |
| 184 | Leeds AFCO | North | 10-14 Bond Court LS1 2JY - POC Office Manager Sgt Amanda Edward 94771 3223 |  |
| 185 | Lincoln AFCO | Central | Sibthorpe House 350-352 High Street, Lincoln LN5 7BN POC Sarah Kelly 01522 565882 |  |
| 186 | Liverpool AFCO | North | Long Lane, Aintree Barracks, L9 7AT - POC Sgt Jay Peatling 0151 5226649 |  |
| 187 | Norwich AFCO | Central | 2 Magdalen Street, Norwich, NR3 1HX - POC Sgt Shawn Masters 01603 614616 or 94613 2003 |  |
| 188 | Plymouth AFCO | South | Pilgrim House, Derry's Cross PL1 2SW - POC Cpl Ian Grimshaw 01752 604563 |  |
| 189 | Preston ACIO | North | Fishergate Shopping Centre, 54 Fishergate, PR1 8BH |  |
| 190 | Stoke AFCO | North | Liverpool Road, Newcastle under Lyme ST5 9ED - POC Anne Lucas 01782 386081 |  |
| 191 | Altcar Air Cadet Training Center | North | Altcar Training Camp, Hightown Merseyside L38 7JD |  |
| 192 | London and South East (RAF Northolt) | HWY | RAF Northolt, (Bldg 63), West End Road, Ruislip, Middlesex HA4 6NG (Commandant Gp Capt Al Lewis Tel; 0208 833 8506 or 95233 8506) |  |
| 193 | North (RAF Leeming) | North | RAF Leeming. (Commandant Gp Capt Mark Leeming Tel0167745 Ext8315) |  |
| 194 | South West, Devizes - Wiltshire ACF | South | Le Marchant Barracks, Franklyn Road, Devizes, Wilts SN10 2FE (Commandant Gp Capt Mike Remlinger Tel 01380 739990 Ext 202) |  |
| 195 | Scotland and Northern Ireland (RAF Leuchars) | North | Air Cadet Regional HQ (Scotland & Northern Ireland) Bldg 8, Leuchars Station (POC Sqn Ldr Hilda Erasmuson Assistant Regional Commandant 01334 859471 Ext 7847 or 95151 7847) |  |
| 196 | Wales and West (RAF Cosford) West Mercian Wing | North | RAF Cosford, Boyle Block (Bldg. 47), Wolverhampton, West Midlands WV7 3EX (Commandant Gp Capt Rog Simon Tel 01902 377903 or 95561 7903) |  |
| 197 | No 1 Welsh Wing (Cardiff) | North | Air Cadet Centre, Maindy Barrack, Cardiff, CF14 3YE (Wing Ex O Sqn Ldr Al Jones Tel 029 2072 6147 or 94355 8147) |  |
| 198 | No 2 Welsh Wing (Queensferry, Flintshire) | North | Army Reserve Centre, Station Road, Queensferry, Flintshire, CH5 2TE (Wing Ex O Sqn Ldr Pat Roberts Tel 01244 846380 (ext 8224) or 94555 8224) |  |
| 199 | No 3 Welsh Wing (Swansea) | North | TY Ivor Mogan, Park Road, Gorseinon Swansea SA4 4UR POC Gary Neville C2 (RAFAC-WHQ-No3Welsh-WexO). Gary.Neville100@mod.gov.uk |  |
| 200 | Beds & Cambs, Cambridge TAC | Central | Army Reserve Centre, Coldhams Lane, Cambridge CB1 3HS (Wing Ex O Sqn Ldr Mick Barton Tel 01223 240160) |  |
| 201 | Bristol & Gloucester, ACW HQ Gloucester | South | 4 Highliffe Drive Quedgley Gloucester GL2 4QN (Wing Ex O Sqn Ldr Nigel Roebuck Tel 01452 722931), |  |
| 202 | Central & East Yorks, (RAF Leeming) | North | RAF Leeming. (Commandant Gp Capt Mark Leeming Tel0167745 Ext8315) |  |
| 203 | Cumbria and Lancs (Preston) | North | Inskip Cadet Centre, Higham Side Road, Preston, PR4 0TF (Wing Ex O Sqn Ldr Mike Linehan Tel 01772 690549) |  |
| 204 | Devon & Somerset (Exeter) | South | Bldg 13A Wyvern Barracks, Barrack Road, Exeter, EX2 6AR (Wing Ex O Sqn Ldr J Gray Tel 01392 275173) |  |
| 205 | Dorset & Wilts (RAF Boscombe Down) | South | Bldg 422 RAF Boscombe Down Salisbury SP4 0JE (Wing Ex O Sqn Ldr Harriet Balshaw Tel 01980 662014) |  |
| 206 | Durham & Northumberland, Gosforth Air Cadets | North | RFCA Centre Knightsbridge, Gosforth, Newcastle-upon-Tyne NE3 2JJ (Wing Ex O Mrs Lorna McLeod, C2 Tel 0191 2131919) |  |
| 207 | Sussex Wing (Seaford) | South | 17a Broad Street, Seaford, Sussex, BN25 1LS (Wing Ex O Sqn Ldr Neil Banks Tel 01323 899900) |  |
| 208 | Thames Valley Wing (Abingdon) | South | North Lewis Block Edward Brooks Barracks, Abingdon, OX13 6HW (Wing Ex O Sqn Ldr Stephen New Tel 01235 547990 or 94256 5990) |  |
| 209 | Trent Wing (RAF Digby) | Central | Building 55 RAF Digby LN4 3LH (Wing Ex O Sqn Ldr Tim Driver Tel 01526 327580 or 95712 7580) |  |
| 210 | Essex (Chelmsford) | Central | Carver Barracks, Wimbish, Saffron Walden, CB10 2YA (Wing Ex O, Sqn Ldr Stephen Rudd Tel 01799 521447) |  |
| 211 | Greater Manchester (University Barracks) | North | University Barracks, Boundary Lane, M15 6DH (Wing Ex O, Sqn Ldr Jon Baker Tel 0161 228 Ext 0424 or 94571 3254) |  |
| 212 | Herts & Bucks (RAF Halton) | HWY | The Learning Centre RAF Halton Aylesbury Bucks HP22 5PG (Wing Ex O, Sqn Ldr Jocelyne Tack 01296 656116 or 95237 6116) |  |
| 213 | Highland Wing HQ (Inverness) | North | Bldg 411, RAF Lossiemouth Morayshire IV31 6SD (Wing Ex O, Sqn Ldr Joe McAlister Tel 01343 817555 or 95161 7555) |  |
| 214 | Kent (Maidstone) | South | Yeomanry Cottages, Boxley Road, Maidstone, ME14 2AR (Wing Ex O Sqn Ldr Andre Leverton ( Tel 01622 754188) |  |
| 215 | Merseyside (RAF Woodvale) | North | RAF Woodvale, Formby, Merseyside L37 7AD ( Wing Ex O Sqn Ldr Paul Routledge Tel 01704 872287 Ext 7247 or 95512 7247) |  |
| 216 | Middlesex (RAF Northolt) | HWY | RAF Northolt, (Bldg 63), West End Road, Ruislip, Middlesex HA4 6NG (Wing Ex O Sqn Ldr Cherry Barrons Tel 0208 842 6263 or 95233 6263)) |  |
| 217 | Northern Ireland (JRCHQ, Aldergrove) | North | JRCHQ Aldergrove BFPO 808 (Wing EX O Kerr, Janette C2 MSF (RAFAC-WHQ-NIreland-WexO) Janette.Kerr134@mod.gov.uk |  |
| 218 | Norfolk & Suffolk (Norwich) | Central | Constitution Hill, (Entrance on Charwell Road) Norwich, NR6 7RA (Wing Ex O Sqn Ldr Martin Thorne 01603 427575) |  |
| 219 | Plymouth & Cornwall (RAF St Mawgan) | South | RAF St Mawgan Newquay (Wing Ex O Sqn Ldr Paul Smith Tel Mil 95423 7638) |  |
| 220 | South & East Mids (RAF Wittering) | Central | RAF Wittering, Peterborough, PE8 6HB |  |
| 221 | South & East Scotland (RAF Leuchars) | North | Bldg 8, Leuchars Station (Wing Ex O POC Sqn Ldr Si Roberts Tel 01334 857464 or 95151 7136) |  |
| 222 | South & West Yorks (Castleford) | North | Healdfield Road, Castleford, WF10 4LQ ( Wing Ex O Sqn Ldr David Espie Tel 01977 604691) |  |
| 223 | Staffs & West Mercian Wg (RAF Cosford) | North | Boyle Block (Bldg. 47), RAF Cosford, WV7 3EX (Wing Ex O Ian Stockley-Miles Tel 01902 377476 or 95561 7476)) |  |
| 224 | Wawickshire & Birmingham (Coventry) | South | Cateswell House,Sir Henry Parkes Road, Canley, Coventry, CV5 6TA (Wing Ex O Sqn Ldr Alistair Mepham Tel 02476 854933 or 94423 8933) |  |
| 225 | West Scotland (Paisley) | North | The Cadet Centre Hawkshead Road, Paisley, PA1 3NE (Wing Ex O Sqn Ldr Iain Low Tel 0141 887 3111) |  |
| 226 | Winchester - Hampshire & IOW ACF | South | Newburgh house, Newburgh Street, Winchester Hants SO23 8UY Tel 01962 890728) Contact Karen Toze Admin Officer E1. |  |
| UAS/VGS Sites |  |  |  |  |
| 227 | 615 (UAS VGS) - AF Kenley (Nr Croydon), parented by Odiham | South | Kenley Aerodrome, Victor Beamish Avenue, Caterham, surrey CR3 5FX (OC Sqn Ldr Jon Cavalli jonathan.cavalli100@rafac.mod.gov.uk Tel 0208 6459784) |  |
| 228 | 661 (UAS VGS) - RAF Kirknewton (South West of Edinburgh), parented by Lossiemouth | North | RAF Kirknewtown, Whitemoss Road, Kirknewton, Midlothian (OC Sqn Ldr Tony Woods antony.woods100@rafac.mod.gov.ukTel 01506 880280) |  |
| 229 | NIUAS - Aldergrove (Inc 664 AGS) | North | FS Aldergrove, BFPO 808 |  |
| 230 | 622 (UAS VGS) - Upavon (USU), parented by BZN | South | Trenchard Lines, Upavon, Pewsey, Wilts SN9 6BE (OC S Goddard Tel 01980 615286 or 94344 5286) |  |
| 231 | 611 (UAS VGS) - Honington | Central | RAF Honington, Bury St Edmunds Suffolk IP31 1EE (OC Sqn Ldr Tony Woods antony.woods100@rafac.mod.gov.uk Tel 01359 237492) |  |
| 232 | 613 (UAS VGS) - Halton | HWY | RAF Halton, Aylesbury, HP22 5PG (OC Sqn Ldr D Johnson Tel 01296 656409 or 95237 6409) |  |
| 233 | 626 (UAS VGS) - Predannack | South | Predannack Airfield, The Lizard, Helston TR12 7AU (OC Sqn Ldr Garry Vitta, garry.vitta100@rafac.mod.gov.uk Tel 01326 241197) |  |
| 234 | 631 (UAS VGS) - Woodvale | North | RAF Woodvale, Formby, Merseyside L37 7AD (OC Sqn Ldr Dave Hale david.hale101@rafac.mod.gov.uk Tel 01704 872287 Ext 7256 or 95512 7256 |  |
| 235 | 632 (UAS VGS) - Tern Hill | North | RAF Tern Hill, Nr Market Drayton, Shropshire TF 9 3QE (OC Sqn Ldr Graham Delaney graham.delaney100@rafac.mod.gov.uk Tel 01630 698329 or 94462 8329) |  |
| 236 | 633 (UAS VGS) - Cosford | North | DCAE Cosford WV7 3EX (OC Sqn Ldr Colin Haynes colin.haynes100@rafac.mod.gov.uk Tel 01902 377320 or 95561 7320) |  |
| 237 | UWAS - St Athan | North | Bldg 383A, Aerospace Business Park Llantwit Road, Bro Tathan South, St Athan, Barry Vale of Glamorgan, CF62 4AN |  |
| 238 | 637 (UAS VGS) - Little Rissington | South | RAF Little Rissington GL54 2QB (OC Sqn Ldr I J Mullan Tel 01451 810078) |  |
| 239 | 644 (VGS) - RAF Syerston | Central | RAF Syerston, Newark, NG23 5NG (OC Sqn Ldr Chris Moore christopher.moore101@rafac.mod.gov.ukTel 01400 264533 or 95751 4533) |  |
| 240 | 645 & 642 (UAS VGS) - Topcliffe | North | RAF Topcliffe, Alanbrook Barracks, Thirsk YO7 3QE (645 OC Sqn Ldr Chris Fleming, chris.fleming100@rafac.mod.gov.u, Tel 01845 595345 or 94712 5345) 642 OC Sqn Ldr Mark Parry, mark.parry100@rafac.mod.gov.uk |  |
| 241 | 663 (AGS) - Lossiemouth | North | RAF Kinloss, Forres Morayshire IV36 0UH (OC Sqn Ldr Rich Lear, richard.lear100@rafac.mod.gov.uk, Tel 01309 672161 or 95131 7238) |  |
| 242 | Cambridge UAS HQ | Central | 2 Chaucer Road, Cambridge CB2 7EB |  |
| 243 | University of Glasgow and Strathclyde Air Squadron (UGSAS) | North | 12 Park Circus, Glasgow, G3 6AX (Postal address). | Flight Safety Systems/areas only |
| Adventure Training Centre |  |  |  |  |
| 244 | NACATC Windermere | North | NACATC, 36 Park Road, Windermere, Cumbria, LA23 2BJ (OC NACATC Mr G Clithero, Tel 015394 44946) |  |

Annex E to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Indicative SCIDA Personnel Site Deployment

2025 figures correct at time of compilation (23/4/25). 2026 figures are suggested levels, however, see also requirement A.1.f for further information. The figures in the table are for information only, bidders should formulate their own personnel structure having considered the information in this annex and all other factors in the SoR.

Note. DPS Order Schedule 7 details the requirements for the identification of, and measures related to, Key Staff. Posts considered Key are indicated in the table below. The proportion of Key Staff is high due to the high level of reliance on knowledge and experience of individuals delivering the service to specific sites and projects.

| Roles and Current/Proposed Locations |  |  | 2025 Numbers | 2026 Est | Comments/Uplift Justification |
| --- | --- | --- | --- | --- | --- |
| Head of SCIDA |  | Basing at any RAF Unit with suitable facilities | 1 | 1 |  |
| TA Key Staff: Qty 4 |  |  | 4 | 5 | Uplift x 1: Rationale: Consider together with RAF Lossiemouth uplift below. Second engineer at LOS could cover TA Service uplift in Scotland negating this uplift? |
| Site Engineers Key Staff: All Engineers (unless site is double manned where this can drop to one per site, this to be the most experienced engineer) | HWY | RAF High Wycombe | 5 | 5 | Support Engineer Included |
|  | South | RAF Brize Norton | 3 | 3 | South Area Manager (AM) + 2 |
|  |  | RAF St Mawgan | 1 | 1 |  |
|  |  | RAF Benson & Odiham | 1 | 1 |  |
|  |  | Swanwick (NATS) | 1 | 1 |  |
|  | Central | RAF Coningsby | 2 | 2 | Central AM + 1 . |
|  |  | RAF Marham | 2 | 2 |  |
|  |  | RAF Waddington | 2 | 2 |  |
|  |  | RAF Wittering | 1 | 1 |  |
|  | North | RAF Lossiemouth | 1 | 2 | Uplift x 1: Rationale: Reinstate 2nd Eng removed prior to start of current contract. Workload stats (see Annex I) indicate additional TA (see TA row above) and/or Site resource required due to geographical area covered as well as significant upcoming TA level projects. |
|  |  | RAF Boulmer | 1 | 1 | North AM |
|  |  | RAF Fylingdales | 1 | 1 |  |
|  |  | RAF Leeming | 1 | 1 |  |
|  |  | RAF Cosford | 1 | 1 |  |
| MARSHALL Engineers Key Staff: Qty 1 ATM Specialist. If solution does not allocate dedicated engineers, then one of the site engineers with sufficient ATM experience to be classed as key. |  | Location depends on the solution. | 2 | 2 | If not allocated to dedicated engineers, the workload for the audit and advice part of this task will require an increase to Site Engineer numbers. |
| CAD Key Staff: Team Lead |  | RAF High Wycombe | 3 | 5 | Uplift x 2: Rationale: Additional work to bring Odiham, Benson, Lyneham, Blandford up to baseline levels/standards & uplift to CMDB |
| OSP Team Key Staff: OSP Manager |  | Mobile | 2 - 4 | 2 - 4 | 2 Perm – 4 Contractor |
| Business Spt & Config Mgt Key Staff: BS/CM x 1 |  | Home Based | 2 | 2 | 1 FT, 1 PT |
| Totals: |  |  | 37 FT/PT Perm + 4 Cont | 41 FT/PT Perm + 4 Cont | Total Uplift of 4 staff |

Annex F to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Personnel Experience, Qualification and Training Requirements

The following skills, training, qualifications, experience, and security clearance are listed in hierarchical order and detail the various skills considered appropriate for optimum Air SCIDA service delivery. Current staff are deemed compliant by virtue of delivering an excellent service for many years.

Note: Engineers with RAF Trade Group 3 or 4 experience (or equivalent in other services) are well suited to the engineering roles)

When the experience is no longer available in the recruitment pool then the formal qualifications quoted, or equivalents, are required to ensure selected staff have the necessary fundamental engineering and other skills. Deviations or concessions are to be approved by the Authority.

Current Contractor:

The following matrix should be completed for each member of staff who it is anticipated will be part of the team delivering the contract at the start of 2026.

Note:  Scores available for each entry are indicated in brackets.

Winning Contractor (if different to above):

Where you intend to include staff transferring under TUPE there is no need to complete matrices. However, please complete the table shown at A.13.a.3 and a matrix for each new member of staff who could, TUPE allowing, be placed in new or changed roles in the team delivering the contract at the start of 2026.

Note:  Scores available for each entry are indicated in brackets.

| Post and Location: | e.g. Air SCIDA Site Engineer - RAF Somewhere | Date Matrix Completed: | 22/6/25 |
| --- | --- | --- | --- |

| Experience, Qualification or Training Scores available for each element are in (brackets) | Score | Relevant Posts | Responsibility for Delivery of the Qualification or Training | Responsibility for Payment of the Qualification or Training |  |
| --- | --- | --- | --- | --- | --- |
| Security Clearance |  |  |  |  |  |
| SC Minimum Security Clearance. DV required for most roles (post contract award where necessary). (In accordance with HMG Personnel Security Controls, clearances should be requested or transfer requested post contract award) | N/A | Potentially all Engineers and CAD Staff. | MOD. | Sponsoring Organisation (usually MOD). |  |
| Experience (Desirable – no minimum) (Recent = <2 years ago, Past >2 Years, FT= primary occupation 3 Days or more/Wk) |  |  |  |  |  |
| Current, or Recent FT Air SCIDA Role (No of Years) |  | All Engineers and Managers. | N/A | N/A |  |
| Current, or Recent FT SCIDA Role outside Air (No of Years). |  | All Engineers and Managers. | N/A | N/A |
| Design, Management, Maintenance of MOD CIS/ICT/ATM systems. (No of Years) |  | All Engineers and Managers. | N/A | N/A |
| Crypto Awareness. (Past – 1, Recent – 2). |  | All Engineers and Managers. | Contractor/Individual. | Contractor/Individual. |
| TEMPEST Awareness (Assessment and Countermeasures Application). (Past – 1, Recent – 2) |  | All Engineers, CAD Techs and Managers. | DLE | RAF/MOD. |
| Skills (Minimum 5) |  |  |  |  |  |
| CIDA Foundation Course - Mandatory for Engineers, Technical advisors and OSP Manager/Team Leader and recommended for CAD. (5) |  | All Engineers, Engineering and OSP Managers and CAD. | Contractor/Individual. | Contractor/Individual. |
| Producing formal documentation for superiors/clients. (Occasional – 1, Experienced – 2) |  | All Engineers and Managers. | N/A | N/A |
| Providing briefs / presentations to Senior Stakeholders. (Occasional – 1, Experienced – 2) |  | Managers. | N/A | N/A |
| Chairmanship. (Occasional – 1, Experienced – 2) |  | Head, TA, Managers. | N/A | N/A |
| Application of Quality Assurance processes. (Past – 1, Recent – 2). |  | All Engineers and Managers. | N/A | N/A |
| Produce reports in JSP 101 format. (Occasional – 1, Experienced – 2) |  | All Engineers and Managers. | Contractor/Individual. | Contractor/Individual. |
| H&S management. (Past – 1, Recent – 2). |  | All Engineers and Managers. | Contractor/Individual. | Contractor/Individual. |
| Project Management Practice. (Past – 1, Recent – 2) |  | All Engineers and Managers. | Contractor/Individual. | Contractor/Individual. |
| Strong initiative and innovation. (1) |  | All Engineers and Managers. | N/A | N/A |
| Management & Supervision Experience and Training. (Past – 1, Recent – 2) |  | Managers & Team Leaders. | N/A | N/A |
| Advanced TEMPEST Training. (Past – 1, Recent – 2) |  | Selected Engineers. | Contractor/Individual. | Contractor/Individual. |
| Produce building ICT Specifications. (Past – 1, Recent – 2) |  | TAs and Managers. | Contractor/Individual. | Contractor/Individual. |
| Understanding building ICT Cable systems. (1) |  | All Engineers and Managers. | Contractor/Individual. | Contractor/Individual. |
| AutoCAD– 2D. (Beginner – 1, Intermediate – 2, Skilled – 3) |  | CAD Tech/Managers. | Contractor/Individual. | Contractor/Individual. |
| Microsoft Office. (Beginner – 1, Intermediate – 2, Skilled – 3) |  | All Staff. | Contractor/Individual. | Contractor/Individual. |
| Knowledge & Understanding (Desirable - no minimum) |  |  |  |  |  |
| Depth of understanding of the RAF and MOD Organisations. (L – 1, M – 2, H – 3) |  | All Engineers and Managers. | N/A | N/A |
| Depth of knowledge of JSP 453: Defence ICT Installation Standard (formerly JSP 604 Lft 4800), SDIP 29, AP 600 and relevant areas of JSP 440. (L – 1, M – 2, H – 3) |  | All Engineers and Managers. | N/A | N/A |
| Value Added Skills and Training |  |  |  |  |  |
| Add courses/skills etc that add value to the SCIDA Service. Score 1 for each added (e.g. 18th Edition, CNIT etc) |  | 18th Edition, CNIT |  |  |
| Professional Registration (Desirable - no minimum) |  |  |  |  |  |
| Chartered Engineer. (5) |  | Head. | Contractor/Individual. | Contractor/Individual. |
| Incorporated Engineer (IEng) with the IET (or equivalent). (4) |  | All Engineers. | Contractor/Individual. | Contractor/Individual. |
| Engineer Technician (EngTech) or ICT Tech with the IET(or equivalent). (3) |  | All Engineers. | Contractor/Individual. | Contractor/Individual. |
| Academic Qualifications (minimum 1 unless Experience >5) |  |  |  |  |  |
| MSc in Eng or similar suitable subject. (In progress 3, Achieved 6) |  | Head. | Contractor/Individual. | Contractor/Individual. |
| BSc in Communication, Electronics, Electrical, Information Management Systems, Computer Science or equivalent. (In progress 1, Achieved 4) |  | All Engineers. | Contractor/Individual. | Contractor/Individual. |
| BTEC ONC / HNC in Communication, Electronics, Electrical, Information Management. (In progress 1, Achieved 2) |  | All Engineers and Managers. | Contractor/Individual. | Contractor/Individual. |
| ONC / OND in engineering drawing NVQ level 2 or equivalent. City & Guilds in Engineering. (In progress 1, Achieved 2) |  | CAD Techs. | Contractor/Individual. | Contractor/Individual. |
| MOD Training |  |  |  |  |  |
| All DLE Training Mandatory for contractors (post contract award where necessary) | N/A | All Staff | MOD. | MOD. |
| Total: |  |  |  |  |  |

Brief synopsis of Relevant Experience: Add up to 2 sides of A4.

Annex G to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Government Furnished Assets (GFA)

MODNet Laptops and accounts will be provided to the Contractor for the duration of the contract. Costs for Contractor specific ICT equipment such as internal Company Laptops, Desktops and networks are the responsibility of the Contractor.

Existing GFA will be transferred to the incoming Contractor at the start of the contract. The Contractor may utilise their own self-funded company LAN where security requirements permit (OS accredited where necessary).

At those sites where a requirement exists for processing information at SECRET and / or Above Secret (AS), access to UADs and accounts will be provided to those Air SCIDA personnel that hold the appropriate level of clearance.

It is accepted that locations and numbers for all items could change up or down dependant on the workforce engaged to provide the service.

RAF High Wycombe SCIDA HQ Staff (Inc Head, HWY Engineers, CAD)

| Description | Quantity |
| --- | --- |
| Office space for Head of Air SCIDA | Desk and conf table, max 2 people - Nimrod |
| Office space for 10 staff and associated storage, plotters and printers | Current office area can accommodate 12 desks – Nimrod. 3 Hot Desks in V |
| Accounts and access to Tier 2 & 3 Systems as required | As requirement emerges |
| MODNet access, headsets and accounts | HWY / OSP / TA / Head / PM / Bus Spt / Management = 20 accounts 18 laptops |
| MODNet A4 and A3 printer | Access to shared printer |
| Internet Access | DBI Wifi |
| Double cabinets | 2 |
| 4 x drawer cabinets | 4 standard and 1 secure |
| Large desks | Nimrod – 9 V - 3 |
| Normal desks | Nimrod - 1 |
| Access to meeting room | As required |
| Space for large plotter | 1 |
| Space for SCIDA LAN and printers | 1 small room in Nimrod and 1 printer |
| Space for ladder storage | Yes |
| Server room with minimum dimensions 2.5 metres x 2 metres | 1 – Depends whether AutoCAD on Laptops manages to remove need for LAN |

SCIDA TA - Per TA – WFH and Hot Desk

| Description | Quantity (each Engineer) |
| --- | --- |
| Accounts and access to Tier 2 & 3 Systems as required | 1 |
| MODNet Laptop/UADs, Headsets and account | 1 |
| MODNet A4 and A3 printer | Access to shared printer |
| Access to meeting room | As Required |

SCIDA Site Engineer

| Description | Quantity (each Engineer) |
| --- | --- |
| Office space on Engineer Home Base sites: RAF Brize Norton, RAF Coningsby, RAF Fylingdales, RAF Leeming, RAF Lossiemouth, RAF Marham, RAF Odiham, RAF St Mawgan, RAF Waddington, RAF Wittering | 1 |
| Desk | 1 |
| Accounts and access to Tier 2 & 3 Systems as required | 1 |
| MODNet UAD, headset and account | 1 |
| MODNet A4 and A3 printer | Access to shared printer |
| Filing cabinet | 1 |
| Access to meeting room | As Required |

Annex H to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Air SCIDA Configuration Management Database (CMDB) Definitions and Scope

- The Air SCIDA service is to provide drawings for all MOD Airfields and RAF sites. Where a site has tailored requirements, these are detailed accordingly.

- The Framework Document sets out the minimum CMDB drawings requirements for SCIDA. The Air requirements, based on the above, are detailed below; the contractor is to maintain the SCIDA Drawing Set in accordance with the requirements below.

Definitions

- Retain. SCIDA are required to save any drawings produced or received as part of change processes, as part of the CMDB for the site, utilising MODNet storage areas. These are to be saved in the received format (AutoCAD, Visio, PDF, MS Draw).

- Maintain. SCIDA produced and maintained drawings are to be updated to incorporate changes detailed in received drawings to ensure the SCIDA drawing set accurately represents the ICT layout of the area where the change has taken place.

- Produce. This means SCIDA are required to generate a drawing from scratch and/or received information and add it to the SCIDA drawing set and held as part of the CMDB.

General

- Air SCIDA are required to produce and maintain a SCIDA drawing set for SL1 and 2 and some SL3 areas, in accordance with the following paragraphs. Any drawings already produced over and above these requirements are to be retained in archive for audit trail purposes and to simplify the process should the service level for the area(s) change.

- As Fitted documentation provided by installers and / or the IDAs is essential to enable SCIDA to produce and maintain the mandated CMDB drawings. SCIDA are required to check the drawings, request corrections where necessary and retain all provided drawings as part of the CMDB. Where required, SCIDA produced and controlled drawings are to be amended to incorporate any changes.

- When IDAs / Installers do NOT provide as-fitted drawings despite repeated requests, SCIDA are required to formally advise RAF Digital and the site of the occurrence and seek direction. Where appropriate, authority for re-prioritisation of work to enable core hours to be expended and/or the engagement of additional drawing resource should be sought from the contract manager.

Drawing Content

- The position of all items of ICT and infrastructure are required to be drawn to scale and accurately positioned. Common items such as PCs are required to use a common “block” representing all such items. All items permanently fixed to the fabric of the building are required to be drawn to scale.

- Furniture. Due to the ease of relocation and to prevent nugatory drawing effort, only furniture items of which form a fundamental part of ICT installations are to be included. Otherwise, furniture should only be included by exception and under specific tasking approved by the contract manager.

Minimum CMDB data sets

- The minimum CMDB data sets differ between Service Levels, the following Table details the requirements for each:

|  |  | Service levels |  |  |
| --- | --- | --- | --- | --- |
| Item | Documentation | 1 | 2 | 3 |
| 1 | All formal change process documentation | M | M | M |
| 2 | Building floor plans detailing telecommunications outlet locations, TEMPEST coupling zones, all classifications (red/black/blue) of ICT cable containment routes, TX’s (inc WAP) and IPZ locations and type. | M | M | D* |
| 3 | External and Internal Approved Routes | M | M | M |
| 4 | Network Equipment Room and Data Centre layout plans | M | M | D* |
| 5 | Rack face layouts (cabinet face plans) | M | M | D* |
| 6 | Site plans detailing ICT outside plant (pits and ducts) | M | M | D* |
| 7 | Building elevation plans, wall views etc | D | D | D |
|  | *For Service Level 3, if existing records are held, these are to be held in archive for future use. |  |  |  |

All formal change process documentation.

- For all SLs, all formal change process documentation is to be retained and form part of the sites CMDB. This is to include all documentation which details the current configuration and historical information regarding ICT change, including but not limited to: ECR documentation, IDA as fitted drawings, Test results, Audit Reports (and associated action plans), Service Level Agreements. All data shall be stored on MODNet.

- As fitted and other Information received which pertains to drawings already included in the SCIDA drawing set is to be extracted and added to those existing drawings to maintain accuracy.

- IDA drawings are required to be issued to the appropriate SCIDA Site Engineer for assessment. Any errors or omissions are required to be notified to installer for correction and corrected documents stored as per above.

Building floor plans detailing telecommunications outlet locations, TEMPEST coupling zones and all classifications (red/black/blue) of ICT cable containment routes.

- Whole Building floor plans shall be produced for all buildings containing SL1 & 2 systems/rooms. These shall include:

  - All TX/RX locations (inc WAPs).

  - ICT cable containment routes of all classifications (red/black/blue).

  - All ICT outlet locations.

  - TEMPEST Coupling Zones.

  - RED and AMBER IPZs.

  - Room Number/Identifier.

- Individual room floor plans shall be produced and maintained for SL1 and 2 rooms. Plans are to include all ICT equipment, floor power sockets, wall sockets, TAPs and cable containment routes and any other items fixed in and position in the room (wall, floor etc). Cable routes in floor and ceiling voids shall be shown as dotted lines of the appropriate colour. Wall, ceiling and underfloor ICT and infrastructure shall be included in room floor plans and shall be distinguishable from floor mounted items through either colour, shading, line type, labels etc.

- TEMPEST bubbles shall be added to all rooms housing RED equipment and systems.

External & Internal Approved Routes.

- Whole Building floor plans are to include details of all internal ICT cable approved routes; this is part of the requirement satisfied by Item 1. Site Plans (Item 6) are to include details of all external routes however Air do not wish approved routes be differentiated from other routes on an Official Sensitive drawing.

NER and Data Centre Layout Plans.

- Tier 2 & 3 NERs and Data Centers shall be allocated SL 2 or 1 as appropriate. These room plans shall include all rack positions and associated isolation points in addition to the requirements detailed in the Room Floor Plan requirements above. They shall also include all wall views detailing all permanently installed items e.g., equipment, outlets, power, containment.

- For this contract, an NER is defined as ‘A room which is dedicated room hosting network communication devices i.e. routers, switches, firewalls, computers, servers, storage devices, database servers, routers etc’. Offices or other rooms where other activity is the primary purpose of the room but may also host ICT cabinets housing floor distribution and limited Network equipment, these are not classed as NERs.

Rack (cabinet) Face Layouts.

- Rack face Layouts (RFL) shall be produced and maintained for all SL1 & SL2 ICT cabinets. Cabinets housing purely SL3 (including Audio Visual, PA/Tannoy etc) are not a mandatory requirement however where SCIDA believe there is a need to maintain operations or critical training, or the environment could have H&S implications, then these shall be included.

- RFLs shall be produced using Microsoft Excel or a compatible software solution which will enable staff without AutoCAD skills or software the opportunity to maintain these layouts. An RFL, currently used across Defence, is included at Appendix 1 to Annex H as an example of potential format and content.

- Columns J to T are considered the minimum content for existing cabinets, expanding to include other information when received from installers of new cabinets or new/replacements into existing cabinets. This is a change to the current contract deliverable and shall be achieved within 3 years of contract start.

Site plans detailing ICT outside plant (pits and ducts).

- Air SCIDA are required to maintain site plans. Drawings are to include Buildings, MOD pits and Ducts, Nav-Aids, Fixed masts and towers, Antennas, the perimeters of the Inspectable space and any other relevant features that are within or may impinge on the CM boundaries of the site. These are to be provided for MOD sites only.

  - RF Radiation exclusion zones, radio protection zones and BT pits and ducts are NOT to be included on the plan as these elements are the responsibility of other agencies. The Radio Site Protection department (RSP) supply information on RF safety zones and transmitter exclusion zones.

  - Due to specialist surveying requirements (Specialised Civil Eng equipment with GPS) involved in measuring, locating, and representing buildings and other features to the required degree of accuracy, Air SCIDA are not required to produce a new site plan from scratch. Where sufficiently detailed as-fitted information is available from any other agency (e.g. DIO, RSP); these shall be adopted and converted to produce a SCIDA Site Plan.

  - Site plans may not be available for some of the smaller sites and sites where Air SCIDA are not responsible for the whole site.

Building elevation plans, wall views etc.

- Air SCIDA shall provide room wall views for all SL1 & 2 NERs.

System Schematics or Interconnect Drawings.

- SCIDA generated versions of these documents are not currently part of the basic SCIDA requirement and IDA and Contractor submitted schematics and topology drawings are merely required to be retained iaw procedures for retention of CMDB data.

  - For some systems IDAs will provide updated system schematics and/or topology drawings as part of ECR activity; new systems installations may also provide these drawings as part of the ECR process; the information contained in these documents is invaluable in pursuit of fault finding and resolution etc.

  - The amount of resource required to generate SCIDA versions of these drawings and to keep current is deemed unaffordable at this time. Additionally, it is felt that there is insufficient control over small changes to be able to guarantee to keep these up to date (e.g. break fix tasks) plus there is a risk of having several versions of the truth available through disparate sources.

- The value of these documents requires that the most recent versions of these documents are available to authorised agencies in the most efficient way possible; they should be stored and shared appropriately to provide easy identification of, and access to, the most up to date versions. See requirement B.3.2.

RAF Boulmer Service.

- In addition to the drawing services described previously, Air SCIDA are to provide the following additional services at RAF Boulmer:

  - Produce Works Requirement drawings detailing the scope of works required for installations or reconfigurations within the R3 Bunker controlled area.

  - Produce a drawing set for the R3 Bunker that is comprehensive and includes the following:

    - Plan layout.

    - Power and cable trays.

    - Fixed UPS and general power distribution.

    - Fire Alarm System.

    - Legacy LAN(S).

RAF Fylingdales Service

- In addition to the drawing services described previously, Air SCIDA are to provide the following additional drawing types at RAF Fylingdales:

  - Plan layout including dimensions.

  - Access floor layout.

  - Reflected ceiling plan.

  - Fire precautions.

  - Small power.

  - Lighting.

  - Power and cable trays.

  - Water distribution.

  - Compressed air.

  - Mechanical services.

  - Communications and leaky feeder.

  - Trunking.

  - Ladder racks and trays.

  - Air supply.

  - Electronic cooling water.

  - Chilled water.

  - HT / LT equipment. drains.

  - Telephones.

  - System block diagram.

  - Power schematics.

  - Equipment Room layout drawings.

- Master drawings to be held on site with amended drawings forwarded to the central Drawing Office for alternative storage.

RAF High Wycombe SCIDA Drawing Service

- In addition to the drawing services described previously, Air SCIDA are to provide the following additional services at RAF High Wycombe:

- Building Floor Plans. Full building floor plans for all SL1 and 2 and some SL3 buildings; floor plans are to be created as a layered set. Drawings to show all IT equipment, ICT taps, comms cable routes (above and below any false ceiling or floor) power sockets and power cable routes (above and below any false ceiling or floor). Furniture will be included where the density dictates that it provides better representation of the fitted ICT infra.

- Enhanced building Floor Plans. The drawing set for High Wycombe may be enhanced for certain facilities to include building services such as: coolers, fire system (underfloor fire heads), domestic power items (ex-lighting system). The working documentation detailing all systems terminated at the ICT TAPs (service posts, wall trunking and under-bench trunking assemblies) is to be maintained.

- Drawing Publication. OS Drawings shall be published in PDF form on a Teams SPOL site maintained by the contractor, access to these to be strictly controlled. Where drawings are required to be protectively marked above OS, suitably accredited systems will be provided to the contractor.

Drawing Availability and Distribution

- All drawings are to be made available to all agencies as part of the ECR process or any other legitimate reason. In the case of electronic drawings, they will be provided as .pdf; requests for .dwg or other formats will be processed through RAF Digital for authority.

- In the case of hardcopy drawings, these will be provided at a suitable size up to A0. Authority may be sought from the Contract Manager where requests are nonstandard. Drawings are to be sent out using the MOD mail system using recorded delivery.

- Unless requested as part of the ECR process, the Air SCIDA Help Desk should be approached in the first instance for all other requests.

Appendix 1 to

Annex H to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Example of CIDA RFL Standardised Format and Content

See separate Excel file

Annex I to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Useful Metrics and Supplementary Information

ECR Numbers (Historical)

- It should be noted that the figures below are intended to be indicative only. For example, some ECRs closed with a Part 5 in 2023 could have been raised in 2023 or previous years so there is no direct relationship between the number of Pt1s raised and the Pt 5’s closing out ECRs in 2023; the same applies to 2024.

- Table 1 is sorted on the number of ECR Pt 1 raised in 2023, Table 2 being similarly sorted for 2024. Sites with no ECR activity in those years are excluded for brevity.

| 2023 |  |  |  | 2024 |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Stations | Pt 1's | Pt 5's |  | Stations | Pt 1's | Pt 5's |
| Lossiemouth | 116 | 94 |  | Waddington | 142 | 121 |
| Waddington | 112 | 76 |  | Lossiemouth | 97 | 88 |
| Marham | 110 | 79 |  | Marham | 89 | 44 |
| Coningsby | 101 | 72 |  | Coningsby | 82 | 75 |
| High Wycombe | 72 | 55 |  | Waddington ASWC | 75 | 66 |
| Brize Norton | 70 | 33 |  | Leeming | 66 | 42 |
| Leeming | 70 | 48 |  | Wittering | 59 | 41 |
| Waddington A&SWC | 62 | 50 |  | High Wycombe | 56 | 46 |
| Wittering | 53 | 27 |  | Boulmer | 52 | 49 |
| Boulmer | 51 | 41 |  | Brize Norton | 43 | 24 |
| Cranwell | 40 | 37 |  | Fylingdales | 30 | 22 |
| Cosford | 36 | 19 |  | Cranwell | 26 | 23 |
| Shawbury | 33 | 25 |  | Northolt | 26 | 14 |
| Fylingdales | 29 | 21 |  | Shawbury | 23 | 15 |
| Honington | 23 | 24 |  | Valley | 23 | 19 |
| Halton | 22 | 15 |  | Honington | 22 | 18 |
| Valley | 21 | 17 |  | Halton | 21 | 20 |
| Northolt | 20 | 21 |  | Cosford | 19 | 20 |
| Culdrose | 19 | 5 |  | Culdrose | 19 | 6 |
| Henlow | 15 | 11 |  | Lyneham | 18 | 5 |
| Staxton Wold | 15 | 12 |  | Blandford Camp | 13 | 4 |
| Neatishead | 14 | 10 |  | Henlow | 12 | 11 |
| Plymouth | 11 | 6 |  | Boscombe Down | 11 | 2 |
| Sultan | 11 | 12 |  | Spadeadam | 9 | 6 |
| Boscombe Down | 10 | 8 |  | St Mawgan | 9 | 6 |
| St Mawgan | 10 | 12 |  | St Athan | 8 | 2 |
| Benson | 9 | 1 |  | Plymouth | 8 | 2 |
| Buchan | 9 | 2 |  | Benbecula | 7 | 3 |
| Yeovilton | 9 | 4 |  | Portreath | 7 | 4 |
| Gibraltar | 8 | 4 |  | Syerston | 7 | 8 |
| Portland | 8 | 7 |  | Saxa Vord | 7 | 12 |
| Syerston | 8 | 8 |  | Yeovilton | 7 | 4 |
| Woodvale | 8 | 6 |  | Barkston Heath | 6 | 2 |
| Akrotiri | 7 | 4 |  | Molesworth | 6 | 6 |
| Croughton | 7 | 3 |  | Aberporth | 6 | 1 |
| Lyneham | 6 | 11 |  | Portland | 5 | 1 |
| Portreath | 6 | 8 |  | Staxton Wold | 5 | 10 |
| Spadeadam | 6 | 6 |  | Sultan | 5 | 4 |
| Blandford Camp | 6 | 3 |  | 637 (UAS VGS) Little Rissington | 5 | 3 |
| Barkston Heath | 5 | 3 |  | Benson | 4 | 4 |
| Donna Nook | 5 | 1 |  | Leuchars | 4 | 1 |
| Holbeach | 5 | 3 |  | Ternhill | 4 | 2 |
| Mona | 5 | 3 |  | Woodvale | 4 | 2 |
| Saxa Vord | 5 | 6 |  | Wattisham | 4 | 3 |
| Wattisham | 5 | 2 |  | Stornoway | 4 | 0 |
| Benbecula | 4 | 7 |  | Swanwick | 4 | 2 |
| Odiham | 4 | 1 |  | Gibraltar | 3 | 2 |
| Lakenheath | 4 | 5 |  | Neatishead | 3 | 8 |
| Molesworth | 4 | 4 |  | Odiham | 3 | 5 |
| Tain | 4 | 3 |  | Croughton | 3 | 5 |
| Aberporth | 4 | 6 |  | Brawdy | 3 | 0 |
| Swanwick | 4 | 5 |  | Little Rissington | 3 | 0 |
| Middle Wallop | 3 | 0 |  | Hartland Point | 3 | 0 |
| Pembrey Sands | 3 | 3 |  | Norwich AFCO | 3 | 3 |
| Fairford | 3 | 1 |  | ACW Cumbria & Lancs | 3 | 0 |
| Hartland Point | 3 | 0 |  | Buchan | 2 | 5 |
| Swingate | 3 | 1 |  | Middle Wallop | 2 | 3 |
| Gosforth Air Cadets (Northumberland) | 3 | 3 |  | Lakenheath | 2 | 0 |
| ACR Northern Ireland (JRCHQ Aldergrove) | 3 | 2 |  | Mildenhall | 2 | 1 |
| ACR Sussex Wing | 3 | 3 |  | Prestwick | 2 | 0 |
| Chivenor | 2 | 0 |  | Brizlee Wood | 2 | 2 |
| Leuchars | 2 | 2 |  | Silloth | 2 | 0 |
| Netheravon | 2 | 5 |  | Hurn Civil | 2 | 0 |
| Ternhill | 2 | 0 |  | Newcastle Airport | 2 | 0 |
| St Athan | 2 | 0 |  | Grantown on Spey | 2 | 1 |
| Brizlee Wood | 2 | 3 |  | Akrotiri | 1 | 2 |
| Manston | 2 | 0 |  | Aldergrove | 1 | 0 |
| Weston on the Green | 2 | 2 |  | Kinloss | 1 | 1 |
| ACR West Scotland | 2 | 2 |  | Fairford | 1 | 1 |
| Aldergrove | 1 | 0 |  | Menwith Hill | 1 | 0 |
| Fleetlands | 1 | 1 |  | Tain | 1 | 4 |
| Menwith Hill | 1 | 2 |  | Topcliffe | 1 | 3 |
| Mildenhall | 1 | 4 |  | St Kilda | 1 | 3 |
| Prestwick | 1 | 0 |  | Windy Head | 1 | 0 |
| Woodhall Spa | 1 | 1 |  | Merryfield | 1 | 0 |
| Topcliffe | 1 | 2 |  | West Freugh | 1 | 1 |
| Little Rissington | 1 | 0 |  | Hebrides | 1 | 1 |
| Silloth | 1 | 0 |  | Wick | 1 | 0 |
| Stornoway | 1 | 0 |  | Tiree | 1 | 0 |
| Windy Head | 1 | 0 |  | Manston | 1 | 0 |
| Merryfield | 1 | 1 |  | Glasgow (UGSAS) | 1 | 1 |
| West Freugh | 1 | 0 |  | ACHQ London & South East (RAF Northolt) | 1 | 1 |
| Wick | 1 | 0 |  | ACR Greater Manchester | 1 | 1 |
| Tiree | 1 | 0 |  | ACR Essex | 1 | 1 |
| Newcastle Airport | 1 | 0 |  | Welford | 1 | 0 |
| ACHQ London & South East (RAF Northolt) | 1 | 0 |  | EMUAS Beeston | 1 | 1 |
| ACR Greater Manchester | 1 | 1 |  | Chivenor | 0 | 0 |
| Hurst Barn Farm | 1 | 0 |  | Donna Nook | 0 | 2 |
| TBC (site 1000, undefined in records) | 1 | 0 |  | Fleetlands | 0 | 2 |
| HMS Gannet | 1 | 0 |  | Holbeach | 0 | 1 |
| Dishforth | 1 | 0 |  | Mona |  | 5 |
| Kinloss |  | 1 |  | Rumster Forest |  | 1 |
| St Kilda |  | 1 |  | Old Catterick ATE Site | 0 | 1 |
| Hurn Civil |  | 0 |  |  |  |  |
| Teeside Civil |  | 3 |  |  |  |  |
| Hebrides |  | 3 |  |  |  |  |
| Alconbury |  | 1 |  |  |  |  |
| Grantown on Spey |  | 1 |  |  |  |  |
| Glasgow (UGSAS) |  | 1 |  |  |  |  |
| 603 Sqn RAAF Edinburgh |  | 1 |  |  |  |  |
| Knockmore |  | 1 |  |  |  |  |
| Mounteagle |  | 1 |  |  |  |  |
| Meldrum |  | 1 |  |  |  |  |
| Torr Sliassg |  | 1 |  |  |  |  |
|  | 1441 | 1071 |  |  | 1227 | 931 |

Workforce hours Consumption Data.

Technical Advisor (TA) Workforce hours Consumption Data 2024. (sites with no activity omitted for brevity)

Total figure represents 4.15 TAs, (6530.75- hours 2024 / 1575 (annual Hours per TA); a small number of the following hours will have been undertaken by Site Engineers fulfilling a Hybrid TA role for smaller projects. The figures do not include hours spent on general admin, MOD mandated training and other necessary additional work that all staff are required to undertake as part of their role.

Table 1

| 2024 Site/Project | ECR | Audit/ SLA | Project Marshall (inc WAM Audits) | General Client Assistance | AirCySC Assist/ Advise | Drawing Office | OSP | IDA (HWY) | Travel | Totals |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TA - LOSSIEMOUTH - E7 New Build | 1536.9 |  |  | 11.5 |  |  |  |  | 143.3 | 1691.70 |
| TA - WADDINGTON - Protector | 1334 |  |  | 9.5 |  |  |  |  |  | 1343.50 |
| TA - LOSSIEMOUTH - ATC (R4D) | 534.4 |  |  | 2.5 |  |  |  |  | 23.4 | 560.30 |
| TA - MARHAM - ANVIL II | 461.75 |  |  | 19.25 |  |  | 7.5 |  | 40.5 | 529.00 |
| TA - LOSSIEMOUTH - LDP | 188.7 |  |  |  |  |  |  |  | 289.3 | 478.00 |
| TA - LYNEHAM – Project CUBIT | 179 |  |  | 24.25 |  |  |  |  | 12.5 | 215.75 |
| TA - CONINGSBY - TFST (MOB1) | 204 |  |  | 7.25 |  |  |  |  |  | 211.25 |
| TA - MARHAM - New Fire Section | 149 |  |  | 17.75 |  |  | 4 |  | 32.75 | 203.50 |
| TA - MARHAM - Dog Section | 148.25 |  |  | 23.75 |  |  |  |  | 16 | 188.00 |
| TA - LEEMING - Hangar 3 (MSF) | 156 |  |  | 13 |  |  |  |  | 8 | 177.00 |
| TA - LOSSIEMOUTH - TFST (MOB2) | 145.9 |  |  | 1 |  |  |  |  | 6 | 152.90 |
| TA - WADDINGTON - 54 Sqn Bldg 561 | 114 |  |  |  |  |  |  |  |  | 114.00 |
| TA - CONINGSBY - European Common Radar System | 41.75 |  |  | 30.25 |  |  |  |  | 29.25 | 101.25 |
| TA - LOSSIEMOUTH - SLAM | 64.4 |  |  | 0.5 |  |  |  |  |  | 64.90 |
| TA - WITTERING – Move of RAFP from Henlow to Wittering | 56.5 |  |  |  |  |  |  |  |  | 56.50 |
| TA - LOSSIEMOUTH - US Navy Verticals | 52.9 |  |  |  |  |  |  |  |  | 52.90 |
| TA - LEEMING - ASP3 | 36.5 |  |  | 6 | 1.5 |  |  |  | 8.5 | 52.50 |
| TA - Assistance to Sites and Generic Tasks | 22 |  |  | 20.5 | 9 |  |  |  |  | 51.50 |
| TA - CRANWELL - CAM Move from Henlow | 35.5 |  |  |  |  |  |  |  |  | 35.50 |
| TA - MARHAM - ASMT | 31.75 |  |  | 1.75 |  |  | 0.5 |  |  | 34.00 |
| TA - HIGH WYCOMBE - ZEUSS | 30 |  |  |  |  |  |  |  |  | 30.00 |
| TA – FYLINGDALES – New Secure facility | 18 |  |  | 3.75 |  |  |  |  | 7 | 28.75 |
| TA - LOSSIEMOUTH - IX(B) Sqn Typhoon FLS | 27 |  |  |  |  |  |  |  | 0 | 27.00 |
| TA - CONINGSBY - Project Miller | 19.25 |  |  |  |  |  |  |  | 6.5 | 25.75 |
| TA - LOSSIEMOUTH - MEI Test Facility | 18.3 |  |  |  |  |  |  |  |  | 18.30 |
| TA - LEEMING - YUAS | 18.25 |  |  |  |  |  |  |  |  | 18.25 |
| TA - MARHAM - Bldg 148 Refurb | 12 |  |  | 4 |  |  |  |  |  | 16.00 |
| TA - BOULMER - ASP3 | 11.4 |  |  |  |  |  |  |  |  | 11.40 |
| TA - WADDINGTON - Shadow | 8.5 |  |  |  |  |  |  |  |  | 8.50 |
| TA - CONINGSBY - WOC | 3 |  |  | 5.5 |  |  |  |  |  | 8.50 |
| TA – BRIZE NORTON – New Freight Handling facility | 7.3 |  |  | 1 |  |  |  |  |  | 8.30 |
| TA - LOSSIEMOUTH - Fire Section | 7.8 |  |  |  |  |  |  |  |  | 7.80 |
| TA - LOSSIEMOUTH - MMA P8 | 5 |  |  |  |  |  |  |  |  | 5.00 |
| TA - HONINGTON - WOSM | 1.5 |  |  | 0.75 |  |  |  |  |  | 2.25 |
| TA - LEEMING - Aircrew Training Facility | 0 |  |  | 1 |  |  |  |  |  | 1.00 |
|  | 5680.5 | 0 | 0 | 204.75 | 10.5 | 0 | 12 | 0 | 623 | 6530.75 |
|  | No of TAs Req: |  | This number does not include any allowance for general admin, MOD mandated training and other necessary additional work. |  |  |  |  |  |  | 4.146508 |

| Top 3 Workhours Projects/Sites |  |
| --- | --- |
| RAF Lossiemouth | 3059 |
| RAF Waddington | 1466 |
| RAF Marham | 970 |

Overall Workforce hours Consumption 2023 & 2024 (sites with no activity omitted for brevity)

Note: Standing tasks include Admin, Engineering Supervision & Management, Training - MOD mandated and job related, SCIDA Task General (inc Policy & Standards).

Table 2

| 2023 | Standing Tasks | ECR | Audit/SLA | Project Marshall (inc WAM Audits) | General Client Assistance | Air CySC Assist/ Advise | Drawing Office | OSP | IDA (HWY) | Travel | Totals |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High Wycombe |  | 1403.5 | 557.5 | 6.25 | 205 | 162.5 | 871.17 | 16 | 1825 | 7.5 | 5054.42 |
| Waddington |  | 1462.25 | 250.5 | 10.5 | 421 | 12 | 246.25 | 257 | 25 | 130.5 | 2815.00 |
| Brize Norton |  | 437.75 | 266 | 20.75 | 1117 | 435 | 112.83 | 110 |  | 104.5 | 2603.83 |
| Coningsby |  | 1359 | 272 | 4.5 | 163.75 | 16.75 | 350.91 | 122.5 |  | 234.05 | 2523.46 |
| Marham |  | 809.41 | 297.75 | 32.5 | 211.75 | 20.25 | 430.91 | 345.5 |  | 191.75 | 2339.82 |
| TA - LOSSIEMOUTH - E7 New Build |  | 1485 |  |  | 1 |  |  |  |  | 49.1 | 1535.10 |
| Leeming |  | 623.25 | 84.75 | 13.5 | 193 | 56.25 | 19.41 | 366.25 |  | 137 | 1493.41 |
| Lossiemouth |  | 1115.75 | 67 | 24.5 | 148 | 2 | 3.25 | 21 |  | 72 | 1453.50 |
| TA - WADDINGTON - Protector |  | 1061.75 |  |  |  |  |  |  |  |  | 1061.75 |
| Fylingdales |  | 746.75 | 33.5 | 6 | 262.25 |  | 3.5 | 2 |  | 4.5 | 1058.50 |
| TA - LOSSIEMOUTH - LDP |  | 526.7 |  |  | 8 |  |  |  |  | 285.9 | 820.60 |
| Wittering |  | 277.5 | 82.25 | 27 | 220.25 | 4 | 124.18 | 0.5 |  | 13.25 | 748.93 |
| Project Marshall |  | 32.5 | 6.5 | 515 | 7 |  |  |  |  | 167 | 728.00 |
| Shawbury |  | 175.25 | 49.25 | 35.25 | 65.5 | 17.25 | 21.75 | 187.75 |  | 164.5 | 716.50 |
| Boulmer R3 Bunker |  | 355.75 | 38.5 | 1.75 | 253.5 | 1 | 35.17 |  |  | 25.5 | 711.17 |
| Northolt |  | 78 | 99 | 33.5 | 40 | 2 | 26.5 | 220 |  | 149 | 648.00 |
| Valley |  | 299 | 63.75 | 10.25 | 75.5 | 9 | 5.67 | 2 |  | 104 | 569.17 |
| Staxton Wold |  | 218 | 25 | 5.25 | 58.5 |  | 15.42 | 136 |  | 91.25 | 549.42 |
| Sultan |  | 124 |  |  | 88.75 | 10 | 3.5 | 136 |  | 186.5 | 548.75 |
| Cranwell |  | 217.25 | 94.75 | 12.75 | 71.75 |  | 21.34 |  |  | 54.5 | 472.34 |
| Honington |  | 143.67 | 121.5 |  | 46.5 | 1.75 | 91.92 | 2 |  | 51.25 | 458.59 |
| TA - MARHAM - ANVIL II |  | 409.75 |  |  | 7.5 |  |  |  |  | 18.75 | 436.00 |
| Cosford |  | 172 | 41.5 | 2 | 93.75 | 10.5 | 3.5 | 20 |  | 85 | 428.25 |
| TA - LOSSIEMOUTH - TFST (MOB2) |  | 365.2 |  |  | 1.5 |  |  |  |  | 35.8 | 402.50 |
| TA - CONINGSBY - TFST (MOB1) |  | 334.75 |  |  |  |  |  |  |  | 36.25 | 371.00 |
| St Mawgan |  | 70.5 | 42.25 |  | 121.75 | 5 |  | 54 |  | 47 | 340.50 |
| Project Guardian |  | 82.25 |  |  | 196.25 | 17 |  |  |  | 39 | 334.50 |
| Gibraltar |  | 108.5 | 72.5 | 16 | 31 |  | 10.75 |  |  | 60 | 298.75 |
| Halton |  | 62.5 | 1.75 |  | 35.5 | 1 |  | 125 |  | 63 | 288.75 |
| Neatishead |  | 144.09 | 34.75 | 15.25 | 4 |  | 57 | 4.25 |  | 26 | 285.34 |
| Henlow |  | 26.75 | 40 |  | 74.75 | 3.25 | 43.75 |  |  | 85 | 273.50 |
| TA - LEEMING - Aircrew Training Facility |  | 227.5 | 6 |  |  |  |  |  |  | 30.25 | 263.75 |
| Akrotiri |  | 37.25 | 54 | 26.25 | 29 | 4.25 | 13.83 |  |  | 62.5 | 227.08 |
| TA - LOSSIEMOUTH - SLAM |  | 202 |  |  | 3 |  |  |  |  | 5 | 210.00 |
| Odiham |  | 56.75 | 45.5 | 25 | 13 |  | 19.67 |  |  | 40.5 | 200.42 |
| Swanwick |  | 89 | 22.5 | 0.25 | 41.5 | 8 |  |  |  | 31.5 | 192.75 |
| Boscombe Down |  | 66 | 41.25 | 17 | 17.25 | 2 |  | 3 |  | 33.75 | 180.25 |
| TA - WADDINGTON - Shadow |  | 164 |  |  |  |  |  |  |  |  | 164.00 |
| Culdrose |  | 56.5 | 21 | 6 | 59.5 | 1 |  |  |  | 14.5 | 158.50 |
| Blandford Camp |  | 69.5 |  |  | 56 | 6 |  |  |  | 26.5 | 158.00 |
| Yeovilton |  | 52.4 | 21 | 12 | 32 | 2 |  |  |  | 22.5 | 141.90 |
| TA - LYNEHAM – Project CUBIT |  | 123 |  |  | 1.75 |  |  |  |  | 16.5 | 141.25 |
| Spadeadam |  | 50.5 | 17.5 | 7.5 | 21 |  |  |  |  | 44 | 140.50 |
| Portreath |  | 34 | 20.25 | 2 | 65 | 1 |  |  |  | 18.1 | 140.35 |
| Croughton |  | 33.5 | 18.75 |  | 25 |  | 28.17 | 0.25 |  | 33.5 | 139.17 |
| Molesworth |  | 51.5 | 11.5 |  | 33.25 |  | 21.42 |  |  | 20 | 137.67 |
| TA - MARHAM - Dog Section |  | 101.75 |  |  | 16.5 |  |  | 1 |  | 14.5 | 133.75 |
| Saxa Vord |  | 66.5 | 20.5 | 1.25 | 10.75 |  | 12.25 |  |  | 21 | 132.25 |
| Benson |  | 43.25 | 25.75 | 19.25 | 13.5 |  | 8.25 |  |  | 12 | 122.00 |
| Portland |  | 35 | 13.5 | 13.5 | 33.5 | 0.5 |  |  |  | 23.5 | 119.50 |
| TA - LEEMING - Hangar 3 (MSF) |  | 109.5 | 2 |  | 5 |  |  |  |  |  | 116.50 |
| TA - LOSSIEMOUTH - IX(B) Sqn Typhoon FLS |  | 115.6 |  |  |  |  |  |  |  |  | 115.60 |
| Aberporth |  | 58.75 | 21 | 3.75 | 9.75 |  | 1 |  |  | 20.25 | 114.50 |
| Lyneham |  | 59.25 |  |  | 27.5 | 2.5 |  |  |  | 24.5 | 113.75 |
| Benbecula |  | 40.5 | 15.75 | 0.25 | 7.25 |  | 4 |  |  | 44 | 111.75 |
| TA - LEEMING - YUAS |  | 99.5 |  |  | 2 |  |  |  |  | 8 | 109.50 |
| Plymouth |  | 34 | 12.25 | 10.5 | 33 | 0.5 |  |  |  | 18.25 | 108.50 |
| Barkston Heath |  | 37.75 | 33.75 | 1.5 | 8.25 |  | 17 |  |  | 7.5 | 105.75 |
| TA - CRANWELL - CAM Move from Henlow |  | 105.5 |  |  |  |  |  |  |  |  | 105.50 |
| Mildenhall |  | 34.25 |  |  | 16.75 |  | 16 |  |  | 33 | 100.00 |
| Topcliffe |  | 35.25 | 3.75 | 37.5 |  |  |  |  |  | 18.75 | 95.25 |
| Lakenheath |  | 21 |  |  | 40.5 |  |  |  |  | 30 | 91.50 |
| TA - LOSSIEMOUTH - Fire Section |  | 89 |  |  |  |  |  |  |  |  | 89.00 |
| TA - WITTERING – Move of RAFP from Henlow to Wittering |  | 82.5 |  |  | 5 |  |  |  |  |  | 87.50 |
| TA - LOSSIEMOUTH - ATC (R4D) |  | 83.7 |  |  | 1 |  |  |  |  |  | 84.70 |
| Holbeach |  | 19.25 | 13 | 9.25 | 7.5 |  | 11.25 |  |  | 24.25 | 84.50 |
| Woodvale |  | 41.5 | 24.25 | 2 | 2 |  | 1.5 |  |  | 12 | 83.25 |
| Middle Wallop |  | 17.25 | 21 | 6 | 17.25 | 3.5 | 3 |  |  | 7.75 | 75.75 |
| Wattisham |  | 33.25 | 13.25 | 2 |  |  |  |  |  | 22.25 | 70.75 |
| Fleetlands |  | 29 | 15 | 5 | 2 | 3 | 3.75 | 1 |  | 10.5 | 69.25 |
| Syerston |  | 24.5 | 23.75 | 1 | 6 |  | 3 |  |  | 5 | 63.25 |
| Buchan |  | 22.25 | 11.75 | 0.5 | 9 |  |  |  |  | 16.5 | 60.00 |
| TA - LOSSIEMOUTH - US Navy Verticals |  | 50.1 |  |  | 5 |  |  |  |  |  | 55.10 |
| Weston on the Green |  | 27.75 |  |  | 14.25 |  |  |  |  | 7.75 | 49.75 |
| TA - MARHAM - New Fire Section |  | 36 |  |  | 3.75 |  |  |  |  | 8 | 47.75 |
| Swingate |  | 5.5 | 8.5 | 13.75 | 4 |  |  |  |  | 14.5 | 46.25 |
| Manston |  | 18 | 9.25 | 2.75 | 2 |  |  |  |  | 13 | 45.00 |
| TA - Assistance to Sites and Generic Tasks |  | 32.5 |  |  | 10.5 | 2 |  |  |  |  | 45.00 |
| Mona |  | 20.5 | 9.25 | 2.75 | 2 |  | 2 |  |  | 4 | 40.50 |
| Scampton |  | 33 |  |  | 6 |  |  |  |  | 0.5 | 39.50 |
| Hebrides |  | 12.25 | 13.25 |  | 1.5 |  | 10.5 |  |  | 1.5 | 39.00 |
| Brizlee Wood |  | 14.75 | 5 |  | 0.5 |  | 9.42 |  |  | 4.25 | 33.92 |
| Leuchars |  | 13.5 | 7.5 |  | 11.5 | 0.5 |  |  |  |  | 33.00 |
| Netheravon |  | 12 | 8 |  | 1.5 |  |  | 1 |  | 9 | 31.50 |
| Merryfield |  | 5.5 | 13 | 4.5 | 5.5 |  |  |  |  | 2 | 30.50 |
| Linton on Ouse |  | 10.5 | 2.5 | 6.75 | 3.75 |  |  |  |  | 6 | 29.50 |
| Thorney Island |  | 3.75 | 9.25 | 1 | 7.25 |  |  |  |  | 7.5 | 28.75 |
| Donna Nook |  | 10 | 8.75 | 1.5 |  |  | 5 |  |  | 3 | 28.25 |
| Pembrey Sands |  | 7.5 | 14.75 |  | 1.5 |  |  |  |  | 4.5 | 28.25 |
| Hurn Civil |  | 1.5 | 12 |  | 1 | 2 | 5.75 |  |  | 5.5 | 27.75 |
| West Freugh |  | 3 | 5.75 |  | 0.75 |  | 4.5 |  |  | 13.25 | 27.25 |
| Project Grapevine |  | 2 |  | 21 | 4 |  |  |  |  |  | 27.00 |
| Aldergrove |  | 4 | 8 |  |  |  | 2 |  |  | 11 | 25.00 |
| TA - LOSSIEMOUTH - MMA P8 |  | 24.5 |  |  |  |  |  |  |  |  | 24.50 |
| TA - CONINGSBY - Project Miller |  | 18 |  |  |  |  |  |  |  | 6.5 | 24.50 |
| Ternhill |  | 5 | 10.5 | 3.75 |  | 0.5 |  |  |  | 4.5 | 24.25 |
| Hartland Point |  | 7.75 | 10.75 | 0.75 | 1 |  |  |  |  | 4 | 24.25 |
| Tain |  | 0.5 | 11.75 |  | 1 |  |  |  |  | 10.5 | 23.75 |
| TA – BRIZE NORTON – New Freight Handling facility |  | 23.4 |  |  |  |  |  |  |  |  | 23.40 |
| Menwith Hill |  | 4.25 | 12.5 |  | 3 |  |  |  |  | 1.75 | 21.50 |
| Tiree |  | 1.75 | 4.75 | 0.5 |  |  |  |  |  | 14.5 | 21.50 |
| Teeside Civil |  | 4.75 | 11.75 |  | 3.25 |  |  |  |  | 1.5 | 21.25 |
| TA - HIGH WYCOMBE - 11 Group New Op Centre |  | 20.8 |  |  |  |  |  |  |  |  | 20.80 |
| Warton Airfield |  |  | 11 |  | 2 | 0.5 | 2 |  |  | 5 | 20.50 |
| TA – FYLINGDALES – New Secure facility |  | 15 |  |  | 5.5 |  |  |  |  |  | 20.50 |
| Windy Head |  | 2 | 9.5 | 1 |  |  |  |  |  | 7.25 | 19.75 |
| Stornoway |  | 1.75 | 6.75 |  |  |  |  |  |  | 11 | 19.50 |
| St Kilda |  | 11 | 4 | 3 |  |  |  |  |  |  | 18.00 |
| TA - MARHAM - ASMT |  | 15 |  |  | 2.25 |  |  | 0.5 |  |  | 17.75 |
| TA - WADDINGTON - DOTC(A) |  | 17.5 |  |  |  |  |  |  |  |  | 17.50 |
| Glasgow (UGSAS) |  | 2.75 | 6 |  |  |  | 0.5 |  |  | 8 | 17.25 |
| TA - ZEUSS |  | 15.1 |  |  | 2 |  |  |  |  |  | 17.10 |
| Chivenor |  | 2.25 | 10 |  | 0.5 |  |  |  |  | 4 | 16.75 |
| 603 Sqn RAAF Edinburgh |  | 3.25 | 5.25 |  |  |  |  |  |  | 8 | 16.50 |
| Lilstock |  | 2 | 7.5 | 0.5 |  |  |  |  |  | 6 | 16.00 |
| Alconbury |  | 5.25 |  |  | 2.25 |  |  |  |  | 7.5 | 15.00 |
| Stoke AFCO |  |  | 11 |  |  |  |  |  |  | 4 | 15.00 |
| Hull AFCO |  | 0.25 | 11 |  | 1 |  |  |  |  | 2.25 | 14.50 |
| Little Rissington |  | 5 | 4.75 |  | 1.5 |  |  |  |  | 2 | 13.25 |
| ACR Sussex Wing |  | 6 |  |  | 1 |  |  |  |  | 6 | 13.00 |
| ACR West Scotland |  | 3.75 | 4 |  |  |  |  |  |  | 5 | 12.75 |
| Wick |  |  | 5 |  |  |  |  |  |  | 7.25 | 12.25 |
| TA - CONINGSBY - WOC |  | 4.5 |  |  |  |  |  |  |  | 7.75 | 12.25 |
| Belmont |  |  | 2 |  |  |  |  |  |  | 10 | 12.00 |
| 634 (UAS VGS) St Athan |  | 0.25 |  |  | 8 |  |  |  |  | 3.5 | 11.75 |
| Fairford |  | 6 |  |  | 3 |  |  |  |  | 2.5 | 11.50 |
| Kinloss |  | 2.5 |  | 8 |  |  |  |  |  | 0.5 | 11.00 |
| Brawdy |  |  | 5.25 |  | 0.75 |  |  |  |  | 5 | 11.00 |
| Welshpool |  |  | 1 | 6 |  |  |  |  |  | 4 | 11.00 |
| TA - LEEMING - SQN HQ New Build |  | 11 |  |  |  |  |  |  |  |  | 11.00 |
| Cambridge UAS HQ |  | 1 | 7.25 |  |  |  |  |  |  | 2.5 | 10.75 |
| Crickhowell |  |  | 8.75 |  |  |  |  |  |  | 1.5 | 10.25 |
| Credenhill |  |  | 6.5 |  | 2 |  |  |  |  | 1.5 | 10.00 |
| TA - LOSSIEMOUTH - ATCT |  | 10 |  |  |  |  |  |  |  |  | 10.00 |
| ACR No.3 Welsh Wing (Swansea) |  |  | 7 |  |  |  |  |  |  | 2.75 | 9.75 |
| Project Hydra |  | 0.5 |  |  | 9 |  |  |  |  |  | 9.50 |
| Prestwick |  | 0.25 | 3.5 |  | 0.5 |  |  |  |  | 5 | 9.25 |
| ACR No.1 Welsh Wing (Cardiff) |  |  | 6.5 |  |  |  |  |  |  | 2.75 | 9.25 |
| Linton MD |  |  |  | 3 | 3 | 0.5 |  |  |  | 2.5 | 9.00 |
| Newcastle Airport |  | 0.25 | 4.25 |  |  |  |  |  |  | 4 | 8.50 |
| Rumster Forest |  | 2.5 |  | 2 |  |  |  |  |  | 4 | 8.50 |
| St Athan ATC |  | 1.5 |  |  | 6.75 |  |  |  |  |  | 8.25 |
| Salisbury |  |  | 4.25 | 1 |  |  |  |  |  | 3 | 8.25 |
| Gosforth Air Cadets (Northumberland) |  | 2.5 | 2.5 |  |  |  |  |  |  | 3 | 8.00 |
| ACR Greater Manchester |  | 4 |  |  |  |  |  |  |  | 4 | 8.00 |
| Grantham Newgate Lane |  |  | 1 |  |  |  |  |  |  | 6.5 | 7.50 |
| Otterburn |  | 0.5 | 2.5 | 1 |  | 0.5 |  |  |  | 2.75 | 7.25 |
| UAS VGS RAF Kirknewton |  |  | 4.75 |  |  |  |  |  |  | 2.25 | 7.00 |
| Gatley Long Coppice |  |  |  | 1 |  |  |  |  |  | 6 | 7.00 |
| Titterstone (Clee Hill) |  |  |  | 1 |  |  |  |  |  | 6 | 7.00 |
| Mounteagle |  | 1.5 |  | 2 |  |  |  |  |  | 3 | 6.50 |
| Meldrum |  | 1.5 |  | 2 |  |  |  |  |  | 2 | 5.50 |
| Torr Sliassg |  | 1.5 |  | 3 |  |  |  |  |  | 1 | 5.50 |
| ACR Northern Ireland (JRCHQ Aldergrove) |  | 4 | 1 |  |  |  |  |  |  |  | 5.00 |
| ACR South & West Yorks |  |  | 5 |  |  |  |  |  |  |  | 5.00 |
| Dawley Heath Hill |  |  |  | 1 |  |  |  |  |  | 4 | 5.00 |
| Cottesmore |  |  | 1 |  |  |  |  |  |  | 4 | 5.00 |
| Shawbury East |  |  | 0.5 | 1 |  |  |  |  |  | 3.5 | 5.00 |
| Harmer Hill Reservoir |  |  |  | 1 |  |  |  |  |  | 3.5 | 4.50 |
| Claxby |  |  | 1 |  |  |  |  |  |  | 3.5 | 4.50 |
| Brunton Airfield |  |  |  |  | 3.25 |  |  |  |  | 1 | 4.25 |
| Trimingham |  | 3 |  |  | 0.25 |  | 0.75 |  |  |  | 4.00 |
| HMS Gannet |  |  | 3.5 |  |  |  |  |  |  |  | 3.50 |
| Knockmore |  | 1 |  | 2 |  |  |  |  |  | 0.5 | 3.50 |
| Dishforth |  |  | 2 |  |  |  |  |  |  | 1 | 3.00 |
| Beckwithshaw |  |  |  | 3 |  |  |  |  |  |  | 3.00 |
| Bilborough |  |  |  | 3 |  |  |  |  |  |  | 3.00 |
| Bilsdale |  |  |  | 3 |  |  |  |  |  |  | 3.00 |
| Clarborough |  |  | 1 |  |  |  |  |  |  | 2 | 3.00 |
| Sandy Heath |  |  |  | 3 |  |  |  |  |  |  | 3.00 |
| West Runton |  |  |  | 3 |  |  |  |  |  |  | 3.00 |
| ACW Devon & Somerset |  | 2.5 |  |  |  |  |  |  |  |  | 2.50 |
| 626 (UAS VGS) Predannack |  | 1 |  |  | 1.5 |  |  |  |  |  | 2.50 |
| 637 (UAS VGS) Little Rissington |  |  | 2 |  | 0.5 |  |  |  |  |  | 2.50 |
| Norwich AFCO |  | 0.25 | 2 |  |  |  |  |  |  |  | 2.25 |
| 611 (UAS VGS) Honington |  | 2.25 |  |  |  |  |  |  |  |  | 2.25 |
| Leeming Water Tower |  | 1 | 0.75 |  |  |  |  |  |  | 0.5 | 2.25 |
| ACW Cumbria & Lancs |  |  |  |  | 2 |  |  |  |  |  | 2.00 |
| ACR Thames Valley Wing |  |  | 2 |  |  |  |  |  |  |  | 2.00 |
| Middle East Farm |  |  |  | 2 |  |  |  |  |  |  | 2.00 |
| Hurst Barn Farm |  |  |  | 2 |  |  |  |  |  |  | 2.00 |
| Yeovilton MD |  |  | 2 |  |  |  |  |  |  |  | 2.00 |
| Llanfaethlu |  |  | 0.75 | 1 |  |  |  |  |  |  | 1.75 |
| Leeds AFCO |  | 0.25 | 1.25 |  |  |  |  |  |  |  | 1.50 |
| Manningtree MF |  |  |  | 1.5 |  |  |  |  |  |  | 1.50 |
| Danbury |  |  |  | 1.5 |  |  |  |  |  |  | 1.50 |
| Boscombe Down MD |  |  |  | 1.5 |  |  |  |  |  |  | 1.50 |
| The Shrubbery (Chapel Hill) |  |  |  | 1.5 |  |  |  |  |  |  | 1.50 |
| Honington MD |  |  |  | 1.5 |  |  |  |  |  |  | 1.50 |
| TA - LOSSIEMOUTH - In-Flight Feeder |  | 1.5 |  |  |  |  |  |  |  |  | 1.50 |
| ACR Norfolk & Suffolk |  |  | 0.75 |  | 0.5 |  |  |  |  |  | 1.25 |
| Clun |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Peterborough |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Wisbech |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Burnham |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Lavenham Hall Farm |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Castle Camps Coopers Farm |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Mendlesham |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Nedging Tye |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Kings Lynn |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Beacon Hill MD |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Morgans Hill |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Boars Hill |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Lopcombe Corner |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Christmas Common |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Cirencester |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Hannington |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Bristol Water |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Winchester Sparholt |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Topcliffe MD |  |  | 1 |  |  |  |  |  |  |  | 1.00 |
| Benson MD |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Henley on Thames |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| High Wycombe PWHQ South MD |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Newton Barrow |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Odiham MD |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Holyhead |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Waunfawr |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Nebo |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Llandona |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| Altcar ACT |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| TA - CONINGSBY - TTF (Refurb) |  | 1 |  |  |  |  |  |  |  |  | 1.00 |
| Fairbourne |  |  |  |  | 0.5 |  |  |  |  |  | 0.50 |
| Grantown on Spey |  |  |  |  | 0.5 |  |  |  |  |  | 0.50 |
| Liverpool AFCO |  |  |  | 0.5 |  |  |  |  |  |  | 0.50 |
| ACHQ Scotland & Northern Ireland (RAF Leuchars) |  |  | 0.5 |  |  |  |  |  |  |  | 0.50 |
| 633 (UAS VGS) Cosford |  | 0.5 |  |  |  |  |  |  |  |  | 0.50 |
| Welford |  |  | 0.5 |  |  |  |  |  |  |  | 0.50 |
| EMUAS Beeston |  | 0.5 |  |  |  |  |  |  |  |  | 0.50 |
|  | 18980.94 | 18126.17 | 3586.75 | 1319.75 | 5049.75 | 827.25 | 2705.19 | 2134.50 | 1868.00 | 4212.14 | 58810.44 |
|  | 32% | 31% | 6% | 2% | 9% | 1% | 5% | 4% | 3% | 7% | 100% |

Table 3

| 2024 | Standing Tasks | ECR | Audit/SLA | Project Marshall (inc WAM Audits) | General Client Assistance | Air CySC Assist/ Advise | Drawing Office | OSP | IDA (HWY) | Travel | Totals |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High Wycombe |  | 1141.5 | 364.25 | 1 | 472.75 | 158.25 | 564.07 |  | 1164.75 | 29.5 | 3896.07 |
| Brize Norton |  | 436.75 | 184 | 9.75 | 866.5 | 452 | 91.25 | 830.5 |  | 423 | 3293.75 |
| Coningsby |  | 1138.2 | 211 | 27 | 221.75 | 76.5 | 274.33 | 729.5 |  | 339.3 | 3017.58 |
| Marham |  | 622.75 | 275 | 47.75 | 375.75 | 95.25 | 167.25 | 741.75 | 48 | 319 | 2692.50 |
| Waddington |  | 1642.5 | 255.25 | 16.25 | 271 | 18.5 | 94.75 |  |  | 21 | 2319.25 |
| Cosford |  | 122.75 | 41.5 | 0.5 | 57.5 | 1.5 | 5 | 1417 |  | 586.25 | 2232.00 |
| Leeming |  | 608.75 | 25.75 | 13.75 | 167.75 | 27 | 4 | 854 |  | 361 | 2062.00 |
| Honington |  | 131.25 | 108.25 | 2.75 | 48.75 | 8 | 44.33 | 955.5 |  | 462.75 | 1761.58 |
| TA - LOSSIEMOUTH - E7 New Build |  | 1551.9 |  |  | 11.5 |  |  |  |  | 143.3 | 1706.70 |
| Lyneham |  | 50.5 |  |  | 68.5 | 4 | 7.5 | 1126 |  | 347.25 | 1603.75 |
| Cranwell |  | 125.5 | 91 | 13.75 | 58.25 |  | 39.5 | 875 |  | 323.5 | 1526.50 |
| TA - WADDINGTON - Protector |  | 1360.5 |  |  | 9.5 |  |  |  |  |  | 1370.00 |
| Lossiemouth |  | 1070 | 56.75 | 3.25 | 93 |  | 9 |  |  |  | 1232.00 |
| Fylingdales |  | 798.75 | 23.25 | 0 | 386.5 |  | 2 |  |  |  | 1210.50 |
| Wittering |  | 287.75 | 74.25 | 30.5 | 287.75 | 19.75 | 170.42 | 2.5 |  | 60.75 | 933.67 |
| Project Marshall |  | 22.75 | 5 | 743.75 | 17.5 |  |  |  |  | 55.5 | 844.50 |
| Boulmer R3 Bunker |  | 411.25 | 40.25 |  | 251.25 |  | 33.5 |  |  | 15 | 751.25 |
| TA - LOSSIEMOUTH - ATC (R4D) |  | 576.4 |  |  | 2.5 |  |  |  |  | 23.4 | 602.30 |
| St Mawgan |  | 47 | 23.5 |  | 143.5 |  | 0.5 | 271 |  | 99 | 584.50 |
| Valley |  | 368 | 44.5 | 12.75 | 50.5 |  | 3 |  |  | 97.5 | 576.25 |
| TA - MARHAM - ANVIL II |  | 464.75 |  |  | 19.25 |  |  | 7.5 |  | 40.5 | 532.00 |
| TA - LOSSIEMOUTH - LDP |  | 192.2 |  |  |  |  |  |  |  | 289.3 | 481.50 |
| Northolt |  | 57.5 | 39.5 | 21.75 | 54 |  | 5 | 170.5 |  | 122.5 | 470.75 |
| Shawbury |  | 174.75 | 40.5 | 21.75 | 121.25 | 7.5 |  | 1 |  | 39.75 | 406.50 |
| Boscombe Down |  | 139 | 39.5 | 11 | 45 | 11 | 31.5 |  |  | 57 | 334.00 |
| Project Guardian |  | 89.5 | 8 | 1 | 179 | 17 |  |  |  | 22 | 316.50 |
| Culdrose |  | 106.5 | 17.75 | 37 | 82 |  |  |  |  | 39.25 | 282.50 |
| Odiham |  | 88.5 | 34.75 | 15.25 | 59 |  | 14 | 1 |  | 67.75 | 280.25 |
| Henlow |  | 24 | 48.5 |  | 60.25 | 3 | 44.25 | 0 |  | 70.5 | 250.50 |
| Portreath |  | 52 | 14 | 8.5 | 133.5 |  |  |  |  | 23.75 | 231.75 |
| Yeovilton |  | 52 | 23.75 | 63.25 | 49 |  |  |  |  | 31 | 219.00 |
| TA - LYNEHAM – Project CUBIT |  | 180 |  |  | 24.75 |  |  |  |  | 12.5 | 217.25 |
| Neatishead |  | 92.25 | 27 |  | 5.75 |  | 70.5 |  |  | 17.25 | 212.75 |
| TA - MARHAM - New Fire Section |  | 157 |  |  | 17.75 |  |  | 4 |  | 33 | 211.75 |
| TA - CONINGSBY - TFST (MOB1) |  | 204 |  |  | 7.25 |  |  |  |  |  | 211.25 |
| Spadeadam |  | 90.5 | 13 | 7.5 | 33.75 |  |  |  |  | 63.75 | 208.50 |
| Staxton Wold |  | 118 | 18.25 | 1.5 | 40.25 |  | 7 |  |  | 20 | 205.00 |
| TA - MARHAM - Dog Section |  | 161.5 |  |  | 23.75 |  |  |  |  | 16 | 201.25 |
| Sultan |  | 102 | 2 |  | 22 |  |  | 2 |  | 71.5 | 199.50 |
| Benson |  | 54.5 | 20.75 | 20.25 | 50.25 |  | 11.5 |  |  | 29 | 186.25 |
| Gibraltar |  | 53 | 62 | 6.25 | 32.5 |  | 3.17 |  |  | 27 | 183.92 |
| Blandford Camp |  | 96.5 | 7 |  | 28 | 3.5 |  |  |  | 42.5 | 177.50 |
| TA - LEEMING - Hangar 3 (MSF) |  | 156 |  |  | 13 |  |  |  |  | 8 | 177.00 |
| Croughton |  | 45.25 | 11 |  | 37 |  | 27.25 |  |  | 38.25 | 158.75 |
| Plymouth |  | 39.5 | 17.75 | 43 | 36.5 |  |  |  |  | 21 | 157.75 |
| TA - LOSSIEMOUTH - TFST (MOB2) |  | 145.9 |  |  | 1 |  |  |  |  | 6 | 152.90 |
| Wattisham |  | 40.75 | 34.75 | 7.25 | 6.25 |  | 30.5 |  |  | 27.25 | 146.75 |
| Donna Nook |  | 37.25 | 19.5 | 35 | 18.75 |  | 8 |  |  | 27.75 | 146.25 |
| Benbecula |  | 53 | 17.75 | 2 | 9.25 |  | 34 |  |  | 24 | 140.00 |
| Halton |  | 44 | 10.25 | 0 | 44 |  |  |  |  | 37.5 | 135.75 |
| Portland |  | 37 | 12 | 19.5 | 37 |  |  |  |  | 12.5 | 118.00 |
| TA - WADDINGTON - 54 Sqn Bldg 561 |  | 118 |  |  |  |  |  |  |  | 0 | 118.00 |
| Swanwick |  | 53 | 41 |  | 18 | 1.5 |  |  |  | 4 | 117.50 |
| Akrotiri |  | 35.5 | 47 |  | 10.5 |  | 1.5 |  |  | 22 | 116.50 |
| Saxa Vord |  | 57 | 17 |  | 3.5 |  | 5.5 |  |  | 19.5 | 102.50 |
| TA - CONINGSBY - European Common Radar System |  | 41.75 |  |  | 31.25 |  |  |  |  | 29.25 | 102.25 |
| Fleetlands |  | 21.5 | 14.5 | 26 | 3 |  | 15.5 |  |  | 14.25 | 94.75 |
| Barkston Heath |  | 24.5 | 25.25 | 4 | 21 |  | 7.5 |  |  | 10.5 | 92.75 |
| Woodvale |  | 34 | 34.25 | 1.5 | 2.5 |  |  |  |  | 20 | 92.25 |
| Molesworth |  | 32.25 | 7.75 |  | 25.5 |  | 11.5 |  |  | 11.75 | 88.75 |
| Syerston |  | 15 | 34.25 |  | 26 |  | 4.5 |  |  | 5 | 84.75 |
| Aberporth |  | 28.5 | 21 | 1.75 | 4.75 | 1 | 8.75 |  |  | 18.5 | 84.25 |
| Ternhill |  | 41.5 | 7 | 7.75 | 3.25 |  |  |  |  | 18.5 | 78.00 |
| Tain |  | 24 | 10.5 | 5 | 0.5 |  |  |  |  | 37.25 | 77.25 |
| Mildenhall |  | 10 | 9.25 |  | 11.75 |  | 21.25 |  |  | 24 | 76.25 |
| Topcliffe |  | 24 | 1.5 | 24 | 2.5 |  |  |  |  | 24 | 76.00 |
| Buchan |  | 36.5 | 8.5 |  | 7 |  |  |  |  | 22.5 | 74.50 |
| Netheravon |  | 1 | 42.5 |  |  |  | 27.5 |  |  | 3 | 74.00 |
| Middle Wallop |  | 18.5 | 26.25 | 3 | 1.5 |  | 4 |  |  | 17 | 70.25 |
| TA - LOSSIEMOUTH - SLAM |  | 64.4 |  |  | 0.5 |  |  |  |  |  | 64.90 |
| Holbeach |  | 20.5 | 14.25 | 4.5 | 6.5 |  |  |  |  | 18 | 63.75 |
| Little Rissington |  | 34.25 | 4.25 | 6.5 | 5.5 |  | 2.5 |  |  | 10 | 63.00 |
| TA - Assistance to Sites and Generic Tasks |  | 22 |  |  | 32 | 9 |  |  |  |  | 63.00 |
| West Freugh |  | 30 | 7 | 2.5 |  |  | 4 |  |  | 19 | 62.50 |
| Mona |  | 38.25 | 6 | 1.75 | 2 |  | 0 |  |  | 11 | 59.00 |
| TA - WITTERING – Move of RAFP from Henlow to Wittering |  | 56.5 |  |  |  |  |  |  |  |  | 56.50 |
| TA - LEEMING - ASP3 |  | 37.5 |  |  | 9 | 1.5 |  |  |  | 8.5 | 56.50 |
| Merryfield |  | 12 | 8.25 | 21.5 | 7.75 |  |  |  |  | 6.75 | 56.25 |
| TA - LOSSIEMOUTH - US Navy Verticals |  | 52.9 |  |  |  |  |  |  |  |  | 52.90 |
| Leuchars |  | 18.5 | 11 |  | 17 |  |  |  |  |  | 46.50 |
| Menwith Hill |  | 7.5 |  |  | 27 |  |  |  |  | 6.25 | 40.75 |
| Stornoway |  | 7.25 | 5 |  | 1 |  |  |  |  | 24.5 | 37.75 |
| TA - CRANWELL - CAM Move from Henlow |  | 37.5 |  |  |  |  |  |  |  |  | 37.50 |
| St Kilda |  | 8.75 | 11.25 | 2 |  |  |  |  |  | 14 | 36.00 |
| Brizlee Wood |  | 8.25 | 4.5 |  | 7 |  | 12.5 |  |  | 3.5 | 35.75 |
| Lakenheath |  | 10 | 7.75 |  | 9 |  | 2 |  |  | 6.25 | 35.00 |
| TA - MARHAM - ASMT |  | 31.75 |  |  | 1.75 |  |  | 0.5 |  |  | 34.00 |
| TA - BOULMER - ASP3 |  | 32.6 |  |  |  |  |  |  |  |  | 32.60 |
| Norwich AFCO |  | 17.5 | 4 |  | 7.25 |  |  |  |  | 3.5 | 32.25 |
| St Athan ATC |  | 20 | 5.25 |  | 5.5 |  |  |  |  |  | 30.75 |
| TA - HIGH WYCOMBE - ZEUSS |  | 30 |  |  |  |  |  |  |  |  | 30.00 |
| TA – FYLINGDALES – New Secure facility |  | 18 |  |  | 3.75 |  |  |  |  | 7 | 28.75 |
| Hurn Civil |  | 5.5 | 7.25 |  | 7.5 |  |  |  |  | 7.5 | 27.75 |
| TA - LOSSIEMOUTH - IX(B) Sqn Typhoon FLS |  | 27 |  |  |  |  |  |  |  |  | 27.00 |
| Brawdy |  | 13.75 | 7.5 |  |  |  |  |  |  | 5 | 26.25 |
| TA - CONINGSBY - Project Miller |  | 19.25 |  |  |  |  |  |  |  | 6.5 | 25.75 |
| Tiree |  | 4.75 | 6 |  |  |  |  |  |  | 14 | 24.75 |
| Warton Airfield |  |  | 10.5 |  | 7.25 |  | 2 |  |  | 5 | 24.75 |
| Hebrides |  | 6.5 | 11 |  |  |  | 6.17 |  |  | 1 | 24.67 |
| Aldergrove |  | 0.5 | 6 |  | 1 |  | 5 |  |  | 12 | 24.50 |
| Wick |  | 6.75 | 5.5 |  | 1.5 |  |  |  |  | 7 | 20.75 |
| Thorney Island |  |  | 11 | 0.5 | 0.25 |  |  |  |  | 7.5 | 19.25 |
| Hartland Point |  | 4.5 | 6.75 | 1.5 | 4.5 |  |  |  |  | 2 | 19.25 |
| Pembrey Sands |  |  | 11.75 |  | 2.5 | 1 |  |  |  | 3.5 | 18.75 |
| Fairford |  | 7.75 |  |  | 6 |  |  |  |  | 5 | 18.75 |
| Manston |  | 9.75 | 2.5 | 0.5 | 0.5 |  |  |  |  | 5.5 | 18.75 |
| 637 (UAS VGS) Little Rissington |  | 15 |  |  | 1 | 0.5 |  |  |  | 2 | 18.50 |
| TA - LOSSIEMOUTH - MEI Test Facility |  | 18.3 |  |  |  |  |  |  |  |  | 18.30 |
| TA - LEEMING - YUAS |  | 18.25 |  |  |  |  |  |  |  |  | 18.25 |
| Prestwick |  | 4.75 | 6.5 |  | 0.75 |  |  |  |  | 5 | 17.00 |
| TA - MARHAM - Bldg 148 Refurb |  | 12 |  |  | 4 |  |  |  |  |  | 16.00 |
| Kings Park |  |  | 4.75 |  | 5.75 |  |  |  |  | 4 | 14.50 |
| 634 (UAS VGS) St Athan |  | 10.75 | 2 |  | 1.5 |  |  |  |  |  | 14.25 |
| Windy Head |  | 4 | 4.75 |  | 1 |  |  |  |  | 4 | 13.75 |
| Newcastle Airport |  | 3.75 | 4.25 |  |  |  | 1.5 |  |  | 3.5 | 13.00 |
| Lilstock |  | 1 | 7.25 |  |  |  |  |  |  | 3.5 | 11.75 |
| Catterick Camp |  | 3 |  |  |  |  |  |  |  | 8.5 | 11.50 |
| Credenhill |  | 0.5 | 4 |  | 4.5 |  |  |  |  | 2 | 11.00 |
| Alconbury |  | 1.75 |  |  | 2.75 |  |  |  |  | 5.5 | 10.00 |
| Staxton Wold MD |  |  |  | 2 |  |  |  |  |  | 8 | 10.00 |
| ACR Greater Manchester |  | 4 |  |  |  |  |  |  |  | 5 | 9.00 |
| Linton MD |  | 7 |  |  |  |  |  |  |  | 1.5 | 8.50 |
| TA - WADDINGTON - Shadow |  | 8.5 |  |  |  |  |  |  |  |  | 8.50 |
| TA - CONINGSBY - WOC |  | 3 |  |  | 5.5 |  |  |  |  |  | 8.50 |
| TA – BRIZE NORTON – New Freight Handling facility |  | 7.3 |  |  | 1 |  |  |  |  |  | 8.30 |
| Glasgow (UGSAS) |  | 0.5 | 2.75 |  |  |  | 1 |  |  | 4 | 8.25 |
| Silloth |  | 8 |  |  |  |  |  |  |  |  | 8.00 |
| TA - LOSSIEMOUTH - Fire Section |  | 7.8 |  |  |  |  |  |  |  |  | 7.80 |
| ACR Essex |  | 7 |  |  | 0.5 |  |  |  |  |  | 7.50 |
| Danbury |  |  |  | 1.5 |  |  |  |  |  | 6 | 7.50 |
| Chivenor |  |  | 5.25 |  |  |  |  |  |  | 2 | 7.25 |
| Titterstone (Clee Hill) |  |  | 0.5 | 0.75 |  |  |  |  |  | 5.5 | 6.75 |
| Dawley Heath Hill |  |  |  | 1.5 |  |  |  |  |  | 5 | 6.50 |
| Welshpool |  |  |  | 1 |  |  |  |  |  | 5 | 6.00 |
| Kinloss |  | 1.5 |  | 1 | 3 |  |  |  |  |  | 5.50 |
| ACW Cumbria & Lancs |  | 3.5 |  |  |  |  |  |  |  | 2 | 5.50 |
| Peterborough |  |  |  | 1 |  |  |  |  |  | 4.5 | 5.50 |
| Wisbech |  |  |  | 1 |  |  |  |  |  | 4.5 | 5.50 |
| Clun |  |  | 1 | 1 |  |  |  |  |  | 3 | 5.00 |
| Harmer Hill Reservoir |  |  |  | 1.5 |  |  |  |  |  | 3.5 | 5.00 |
| Otterburn |  |  | 2.5 |  |  |  |  |  |  | 2.5 | 5.00 |
| TA - LOSSIEMOUTH - MMA P8 |  | 5 |  |  |  |  |  |  |  |  | 5.00 |
| Claxby |  |  |  | 0.5 |  |  |  |  |  | 4 | 4.50 |
| Teeside Civil |  |  | 2.25 |  |  |  |  |  |  | 1.75 | 4.00 |
| Gatley Long Coppice |  |  | 1 |  |  |  |  |  |  | 3 | 4.00 |
| Hurst Barn Farm |  | 1 |  | 2.75 |  |  |  |  |  | 0.25 | 4.00 |
| Topcliffe MD |  |  |  | 2 |  |  |  |  |  | 2 | 4.00 |
| Waunfawr |  |  | 0.5 | 1.5 |  |  |  |  |  | 2 | 4.00 |
| Project Hydra |  |  |  |  | 3.75 |  |  |  |  |  | 3.75 |
| Newton Barrow |  | 1 |  | 2 |  |  |  |  |  | 0.5 | 3.50 |
| Coningsby MD |  |  |  | 1 | 1.5 |  |  |  |  | 1 | 3.50 |
| Manningtree MF |  |  |  | 2 |  |  |  |  |  | 1.25 | 3.25 |
| Cirencester |  |  |  | 1 |  |  |  |  |  | 2.25 | 3.25 |
| Swingate |  | 0.5 |  | 1.5 | 1 |  |  |  |  |  | 3.00 |
| Grantown on Spey |  | 3 |  |  |  |  |  |  |  |  | 3.00 |
| Weston on the Green |  | 2 |  |  | 1 |  |  |  |  |  | 3.00 |
| Castle Camps Coopers Farm |  |  |  | 1 |  |  |  |  |  | 2 | 3.00 |
| Middle East Farm |  |  |  | 1 |  |  |  |  |  | 2 | 3.00 |
| Kings Lynn |  |  |  | 1 |  |  |  |  |  | 2 | 3.00 |
| The Shrubbery (Chapel Hill) |  |  |  | 1 |  |  |  |  |  | 2 | 3.00 |
| Belmont |  |  |  | 1 |  |  |  |  |  | 2 | 3.00 |
| Llanfaethlu |  |  |  | 1.5 |  |  |  |  |  | 1.5 | 3.00 |
| Holyhead |  |  |  | 1.5 |  |  |  |  |  | 1.5 | 3.00 |
| Nebo |  |  |  | 1.5 |  |  |  |  |  | 1.5 | 3.00 |
| Clarborough |  |  |  | 1 |  |  |  |  |  | 1.75 | 2.75 |
| Shawbury East |  |  | 1.25 | 1 |  |  |  |  |  | 0.5 | 2.75 |
| Stoke Holy Cross |  |  |  | 1.5 |  |  |  |  |  | 1 | 2.50 |
| Mendlesham |  |  |  | 2 |  |  |  |  |  | 0.5 | 2.50 |
| Woodbridge Debach |  |  |  | 1.75 |  |  |  |  |  | 0.75 | 2.50 |
| Salisbury |  |  |  | 1 |  |  |  |  |  | 1.5 | 2.50 |
| Winchester Sparholt |  |  |  | 1 |  |  |  |  |  | 1.5 | 2.50 |
| Henley on Thames |  |  |  | 1 |  |  |  |  |  | 1.5 | 2.50 |
| Leeming Water Tower |  |  | 0.5 | 1.5 |  |  |  |  |  | 0.5 | 2.50 |
| Morgans Hill |  |  |  | 1 |  |  |  |  |  | 1.25 | 2.25 |
| TA - HONINGTON - WOSM |  | 1.5 |  |  | 0.75 |  |  |  |  |  | 2.25 |
| Wyberton |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Stickney |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Waltham CON |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Grantham Newgate Lane |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Sandy Heath |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Burnham |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Asgarby |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Tinwell |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Beacon Hill MD |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Bristol Water |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| Boscombe Down MD |  |  |  | 0.5 |  |  |  |  |  | 1.5 | 2.00 |
| Oxford Boars Hill |  |  |  | 1 |  |  |  |  |  | 1 | 2.00 |
| EMUAS Beeston |  | 1 |  | 0 | 1 |  |  |  |  |  | 2.00 |
| Lavenham Hall Farm |  |  |  | 0.75 |  |  |  |  |  | 1 | 1.75 |
| Christmas Common |  |  |  | 1 |  |  |  |  |  | 0.75 | 1.75 |
| Nedging Tye |  |  |  | 1 |  |  |  |  |  | 0.5 | 1.50 |
| Hannington |  |  |  | 1 |  |  |  |  |  | 0.5 | 1.50 |
| Lopcombe Corner |  |  |  | 1 |  |  |  |  |  | 0.25 | 1.25 |
| Welford |  | 1 |  |  |  |  |  |  |  |  | 1.00 |
| Marham MD |  |  |  | 1 |  |  |  |  |  |  | 1.00 |
| TA - LEEMING - Aircrew Training Facility |  |  |  |  | 1 |  |  |  |  |  | 1.00 |
| Leeds AFCO |  | 0.5 |  |  | 0.25 |  |  |  |  |  | 0.75 |
| Hull AFCO |  | 0.75 |  |  |  |  |  |  |  |  | 0.75 |
| ACR Merseyside (RAF Woodvale) |  |  | 0.5 |  |  |  |  |  |  |  | 0.50 |
| ACR Trent Wing (RAF Digby) |  |  |  |  | 0.5 |  |  |  |  |  | 0.50 |
| Benson MD |  |  |  | 0.5 |  |  |  |  |  |  | 0.50 |
| Odiham MD |  |  |  | 0.5 |  |  |  |  |  |  | 0.50 |
| Barnham |  |  |  |  | 0.25 |  |  |  |  |  | 0.25 |
| 611 (UAS VGS) Honington |  |  |  |  | 0.25 |  |  |  |  |  | 0.25 |
|  | 14710.00 | 17370.15 | 2936.00 | 1425.75 | 5541.50 | 917.25 | 1941.24 | 7989.25 | 1212.75 | 5724.55 | 59768.44 |
|  | 25% | 29% | 5% | 2% | 9% | 2% | 3% | 13% | 2% | 10% | 100% |

Site Laydowns: A site map (20250422-Air SCIDA UK Map), Marshall WAM site spreadsheet (20250422-WAM Locations).

Organisation chart: Showing current workforce (20250429-Air SCIDA Org Chart), a chart is included as separate documents in ITT pack.

Annex J to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Outside Plant Task Examples

- Request ICT section assistance as required to access pits (Key control, work permits, authority, escorting – SCIDA not present on each site) iaw local site instructions. ICT section shall be provided 14 days’ notice of any assistance requirements.

- Make random checks during works on Contractors engaged for tasks on the pit and duct system to ensure that work is compliant and being conducted in accordance with instructions.

- Authorise any proposed cable and duct routes for new installations and projects iaw the Air SCIDA ECR procedures. (Issue ECR Part 3).

- Investigate unauthorised use of, or construction of new ducts to determine the authority for any such activity. Ensure new ducts are added to existing records / audit programmes and the Stn underground duct plant supervisor is informed.

- Report any identified damage to pits, pit covers and bores to OC ICT section for Stn remedial non-routine maintenance action.

- Attend all handovers and technical transfers for projects which in any way involve the use or build of RAF ducts. Ensure ‘As fitted’ records supplied by the Contractor or duct user are complete and of a sufficient standard to enable to the site records to be properly maintained. As fitted information must be provided together with the associated Air SCIDA ECR Part 4.

- Ensure a percentage of Stn pits and ducts are inspected at least annually and any defects or required remedial works are reported to OC DSF on Stn.

- Establish a OSP Compliance Manager and team to oversee all OSP work and conduct pit and duct surveys and minor maintenance tasks.

- Pit and duct tasks to include:

- Removal of redundant cabling. (Routine activity as well). Renewal of pit lid markings. (Routine activity as well). Provision of site drawings.

- Rod and re-rope service. (Replacement ropes can be installed by the SCIDA pit and duct team if no responsible agent can be identified).

- Duct blockage or damage investigation.

- Minor repairs for pit furniture.

- Provision of skips for waste cable (additional charge). Undertake A and B end investigation as requested to potentially trace and record specific priority operational circuits.

- Install cables if required for UOR or operational imperative (cable to be provided).

- Request for investigation into unusable duct links into buildings (last pit into BEP).

- Establish a rolling programme of routine maintenance visits across the in-scope estate.

- Undertake and maintain records of the following routine maintenance and inspection activities on ducts / bores during scheduled site visits:

- Inspect for bell mouth present and damage to lips.

- Rodding to prove ducts (if suspected broken/damaged pipes).

- Identification for pits that are classed as confined space.

- Recording any noticeable ground subsidence on routes.

- Undertake and maintain records of the following routine.

- maintenance and inspection activities on pits during scheduled site visits:

- Low density vegetation, root and debris removal from pit and immediate surrounds.

- Resolve uneven lids – H&S.

- Minor repairs to damaged lids.

- Minor repairs to pit furniture.

- Minor repairs to hasp (no welding).

- New lock fitting (locks provided by MOD).

- Water pumping to facilitate inspections.

- Re-labelling of pit lids – check existing or obtain new.

- GPS tagging of pit locations.

- Confirmation of pits within 5m of BEP.

- Confirm and report Approved Circuit pit and duct runs are secured.

- Correct type of pit lids fitted; changed since install.

- Undertake and maintain records of the following routine maintenance and inspection activities on cables during scheduled site visits:

- Inspections for damage.

- Compliance checks.

- Inspections of existing labelling.

- Removal of redundant cables – identified and clarified by site.

- Undertake and maintain records of the following routine maintenance and inspection activities on BEPs during scheduled site visits.

- BEP investigations (cut / damaged cables, JSP 453 / BT LN 550, capping spec).

- Compliance checks.

- Inspecting duct capping and undertake minor repairs. Inspections for evidence of flooding/water ingress.

- Gas seal inspections – conformant and serviceable. Undertake and maintain records of routine maintenance and inspection activities on Linking Containment Systems during scheduled site visits.

- Inspection of Approved Circuit main arterial routes from BEP, removal of RED banding if not required.

- Confirming if the containment linking from BEP is continuous. Removal of redundant cabling from BEP and / or splice boxes to equipment rack.

- Confirmation and visual inspection of bonding and earthing. Make good any inadvertent accidental damage caused as a direct result of maintenance work. This shall not include components which would have failed despite the maintenance works.

- Maintain comprehensive records of all inspections. Records shall include the following as a minimum:

- Pit / duct ID.

- Date of inspection.

- Security status.

- Physical status.

- Duct run length between pits.

- Numbers of ducts between pits.

- Details of recommended maintenance / in progress / planned.

- Hold any in-force duct sharing agreements for each site.

- Attend start-up meetings to ensure Contractors understand which pits, ducts and routes are to be utilised and that the requirements of JSP 453 on cable labelling are understood.

- The SCIDA pit and duct team shall maintain a tasking request list for all specific pit and duct tasks which will be prioritised in association with RAF DIGITAL; these ‘call-off’ tasks shall be undertaken by interleaving with the routine tasks.

Annex K to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Key Performance Indicator - Criteria (Cabinet Office Reportable) - TBC prior to contract start.

Note: KPI failure due to dependencies on individuals, agencies or groups outside the control of the supplier should not be included in calculations.

| Key Performance Indicator | Measure | Measured by | Inadequate | Requires Improvement | Approaching Target | Good |
| --- | --- | --- | --- | --- | --- | --- |
| KPI 1 - Contract Requirement B.5 Standard 5. | Audit reports issued on time. | Supplier but overseen by authority. | Audit reports are issued more than 51 days after audit completion. | Audit reports are issued within 36-50 days of audit completion. | Audit reports are issued within 31-35 days of audit completion. | Audit reports are issued within 30 days of audit completion. |
| KPI 2 - Contract Requirement B.5 Standard 2. | Audits completed within required frequency. | Supplier but overseen by authority. | Any overdue audits not brought to the attention of the authority. or Audits overdue by 6 months as a result of supplier delays. | Any overdue audits have been brought to the attention of the authority and rescheduled for within 6 months of required audit due date. | Any overdue audits have been brought to the attention of the authority and rescheduled for within 3 months of required audit due date. | Initial audit of sites added to scope list to be carried out within 1 year of being added. All SL1 and 1a sites audited within 1 year of previous audit. All SL2 sites audited within 2 years of previous audit, with 50% completed each year. |
| KPI 3 - Contract Requirement B.2 – Standards 1 – 7. | ECR Action Requests | Supplier but overseen by authority. | Assessment and response are 21 working days or more. | Assessment and response are within 16 – 20 working days. | Assessment and response are within 11 – 15 working days. | ECR Parts 1, 2 and 4 responded to within 10 working days of receipt. |
| KPI 4 - Contract Requirement B.3 Standard 7. CMDB Updates completed in the required timeframes… | Configuration Control Sets Updates | Supplier but overseen by authority. | Configuration Control information set update completion exceeds 70 working days of the issue of an ECR Part 5. | Configuration Control information set update is completed within 70 working days of the issue of an ECR Part 5. | Configuration Control information set update is completed within 65 working days of the issue of an ECR Part 5. | Configuration Control information set update is completed within 60 working days of the issue of an ECR Part 5. |
| KPI 5 - Contract Requirement B.7. | Outside Plant Inspections – Timing. | Supplier but overseen by authority. | < 20% of inspections for that period have not been completed. | <15% of inspections for that period have not been completed. | <10% of inspections for that period have not been completed. | All inspections due in this reporting period have been completed. |
| KPI 6 - Social Value - Policy Outcome: Create new businesses, new jobs and new skills. | Model Award Criteria (MAC) 2.3: Support educational attainment relevant to the contract, including training schemes that address skills gaps and result in recognised qualifications | To Be Confirmed at Contract Award |  |  |  |  |

Annex L to

Air SCIDA 2026 Statement of Requirement

Final Version 1.0 - 2 Jun 25

Master Site List Extract (see also Excel File 20250314-Mater Site List Extract)

ECR Register Extract (see also Excel File 20250606-ECR Register Extract)

RAF Somewhere SCIDA Audit - new observations

| Item | Location | Issue | Type/Risk | Action required | Reference | Stn Record of Action |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Building 7 MPGS Crew room | Redundant TV Antenna has been installed through the wall & window frame | FIRE | Remove the aerial lead and back fill with fire stopping material. Annex C Fig 1. | JSP 453 ICT Standards. Ch 5 Para 05.02 |  |
| 3 | Building 7 RAF Police JNCO OIC | Redundant Audio Visio cable in data outlet Brush. | FIRE | Building custodian to raise a Digit’s Ticket for the cabling to be removed. Annex C Fig 2. | JSP 453 ICT Standards. Ch 5 Para 05.02. |  |
| 4 | Building 12 Former Kitchen Area | OOD ITEE (Inspection & Testing Electrical Equipment) 3 x Way Power Lead. | Elec Safety L/S= 3/2 | Building custodian to liaise with VIVO for the power lead to be tested. Annex C Fig 3. | AP 8000 Vol 2 Part 6 Leaflet 8557. SI 1998 PUWE Reg 5 & 6. |  |

RAF Somewhere SCIDA Audit - outstanding actions

Table 1 – outstanding actions (further action required)

| Original Report Ref |  | Location | Issue | Type & Risk | Action required | Reference | Stn Record of Action |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Date | Item |  |  |  |  |  |  |
| Feb 24 | 1 | Bldg. 7 MPGS Outer Office | Active equipment has now been removed; the cabinet is now redundant. | Elec Safety L/S=3/4 | Building custodian to raise a digit’s ticket for the cabinet and associated cabling to be removed. |  |  |
| Feb 24 | 2 | Bldg. 97 | Rack B The UPS is powered off and or in bypass | Elec Safety L/S=4/2 | FST to raise a digit’s Ticket for the UPS to be removed. |  | AST Digit’s ticket CHG1000030326. ECR Ref Air24/0318 closed 27/08/24. |
| Feb 24 | 3 | Bldg. 97 & 99 | Wall mounted Honeywell data cabinet powered with active equipment installed within, has not been included in any electrical Inspection and Testing regime. | H&S L/S-4/2 | The Building Custodian to raise a work service for the data cabinet to be included in the I&T regime. | SI 1998 No 2306 PUWE Reg 5 & 6. |  |

CO-ORDINATING INSTALLATION DESIGN AUTHORITY

GOVERNANCE

SCIDA FRAMEWORK

Issue 2.1 dated 6 Jan 25

PLEASE DO NOT ALTER THIS COPY – DOWNLOAD

INSERT SITE NAME

Defence Digital Ops HQ - Assuring missions, enabling Multi-Domain Integration and delivering Information Advantage.

CIDA Governance - Delivering assurance of the physical and environmental aspects of MOD ICT through expert direction, support and oversight - A critical enabler of the SCIDA Enterprise.

SCIDA FRAMEWORK

Contents

| Document References |  |
| --- | --- |
| Detail | Page |
| Table of amendments | i |
| Contents | ii |
| Glossary of Terms | iii-iv |
| Contacts - CIDA Governance and Appointed SCIDA | v |

| Table of Amendments |  |  |
| --- | --- | --- |
| Date | Version | Detail |
| Pre 2018 | v1.0 | Legacy version from archive, now a retired document |
| Jul 2021 | v1.3 | No amendments, used for CIDA Governance audit trials |
| Nov 2021 | v1.4 | New document structure and layout of processes |
| Oct 2022 | v1.5 | - Existing sub-requirements moved into different processes. - Process sub-requirements added: - 3.4. - 4.1. - 4.2. - 4.4. - 4.5. |
| Nov 2023 | v1.6 | Changes to CIDA Governance hierarchy and included new CIDA Defnet Page link |
| Feb 2024 | v2.0 | To reflect the Feb 2024 changes to JSP 604 Leaflet 4800 Ch 2, updates to the new Service Levels (Table 1) and the minimum dataset (Table 2). |
| Jan 2025 | v2.1 | To remove references to JSP 604 following publication of JSP453 |

| SCIDA Framework Document Content |  |  |
| --- | --- | --- |
| Detail | Paragraph | Page |
| Introduction | 1-2 | 1 |
| CIDA Governance and SCIDA | 3-4 | 1 |
| Service Levels - Explanation of assignments | 5-6 | 1-2 |
| Service Levels and SCIDA support activity | 6a | 3 |
| Minimum CMDB datasets | 7 | 4 |
| CIDA Governance Audits | 8-9 | 4 |
| - Process 1 - Maintain a Configuration Management Baseline | 9a | 4-5 |
| - Process 2 - Employ and maintain a formal change control process | 9c | 5 |
| - Process 3 - Update drawings, associated configuration documents and other relevant information | 9d | 6 |
| - Process 4 - Provide SCIDA advice | 9e | 6 |
| - Process 5 - Periodic SCIDA inspections relevant to assigned Service Level | 9f | 7 |
| SCIDA AOR - Service Level Assignments | 10-10a | 7-8 |
| HoE (or representative) and SCIDA signatures | 10b | 9 |

Glossary of terms

| Term | Explanation |
| --- | --- |
| Baseline Activity | Confirmation and validation of the current fixed ICT infrastructure laydown within the SCIDA assigned areas. Baseline activity includes elements such as surveys and updating existing CMDB drawings and documentation. This activity should be completed no later than 24 months after SCIDA appointment, beyond this period future changes to these records are to be captured through the formal change process. |
| Change | An alteration, addition or removal affecting ICT hardware or supporting infrastructure regarding physical location, environment, or Radio Site Restriction Zones. A change in this context does not include software modification of individual equipment. Such changes may, however, affect the wider Configuration Management duties. |
| Change Control | Management of a physical change to the fixed ICT infrastructure through a formalised process. |
| CIDA Governance Audit | An independent audit conducted by CIDA Governance to review the processes, systems and structures employed by the appointed SCIDA by evaluating the current SCIDA support in line with the assigned Service Level and against this Framework. |
| CIDA Governance | Coordinating Installation Design Authority Governance. Responsible for the optimisation of the maintenance of operational capability and engineering best practice of all ICT, Communications Electronics (CE) engineering and other electronic systems and their associated infrastructures and environment during their lifespan. |
| Configuration Management | JSP 945 is the MOD policy for Configuration Management. CIDA Governance adapt this policy into their change and configuration processes. This ensures the appropriate Configuration Control (CC) and Configuration Management (CM) of relevant systems, the co-ordination of engineering change and the regulation of installation standards. |
| Configuration Management Database | Electronic ICT configuration records held in a shared access repository. |
| Defence Enterprise SCIDA | DE SCIDA apply the polices directed by CIDA Governance and appoint SCIDA to manage CC and CM of ICT infrastructure across an assigned area of the MOD Estate. DE SCIDA also maintain configuration management drawings and documentation via an organic Drawing Office. |
| FM Team | Contracted by DIO, The Facilities Management Team is the Principal Contractor responsible for the physical maintenance of MOD site infrastructure. Site dependant, the FM Team may adopt a different title, however the function is the same. |
| HoE | The Head of Establishment is appointed to manage MOD infrastructure resource within a specific boundary. In some sites this responsibility falls to a military role in a senior appointment. Smaller sites may have an empowered representative with a different role title – Infrastructure Manager, Building Custodian etc. |
| ICT | Information Communication Technologies used in place of Communication Information Systems (CIS). |
| SCIDA Audit | A periodic on-site validation of ICT installations carried out by an appointed SCIDA to ensure continuing conformance to CIDA Governance, relevant standards, and wider MOD policy. |
| SCIDA | Site Co-ordinating Installation Design Authority, appointed to undertake specific SCIDA duties with respect to a single site or group of sites. |
| Survey | A detailed, pre-planned examination of existing ICT infrastructure to gain an understanding of the current condition of installations, records and procedures. A survey task is normally associated during baseline activities. |
| TEMPEST | The name given to the phenomenon of unintentional emanations of compromising signals from electronic equipment or systems. |

CIDA Governance Team Contacts

Address:

CIDA Governance

Blumlein Building

Blandford Camp

Dorset DT11 8RH

Contacts:

| Appointment | Name | Details |
| --- | --- | --- |
| CIDA Governance TL | Mr Andrew Goss | S4B: 0300 157 6996 Email: Andrew.Goss455@mod.gov.uk |
| CIDA Governance 1 | Mr Gregory Ramsden | S4B: 0300 152 8206 Email: Gregory.ramsden101@mod.gov.uk |
| CIDA Governance 2 | Mr David Richardson | S4B: 0300 165 4160 Email: David.Richardson505@mod.gov.uk |
| CIDA Governance 3 | Mr Gareth Lock | S4B: 03001614065 Email: Gareth.Lock106@mod.gov.uk |
| CIDA Governance 4 | Mr David Butler | S4B: 0300 154 5956 Email: David.Butler131@mod.gov.uk |

CIDA Governance Group Mailbox: UKStratComDD-OPS-CS-DS-CIDAGrp@mod.gov.uk

Appointed SCIDA contact (to be completed by the SCIDA)

Address:

Telephone contacts:

Email contacts:

Introduction

- In compliance with legal requirements the HMG Security Policy Framework and the Cabinet Office Information Assurance Governance Framework, CDIO, through D CBM J6 Executive Group, established the MOD CIS Resilience Policy and Recovery Strategy and the DSO published JSP 440. These MOD policy documents mandate Information and Communications Technology (ICT) security, resilience, Configuration Management (CM), Change Control (CC), installation design control and accreditation processes, thus directly delivering the Cabinet Office governance requirement for compliance with BS ISO/IEC 27002, the provision of an accreditation process and the use of ITIL best practice.

- Responsibility for the implementation of security policy and standards is formally delegated to TLB Holders by the Permanent Undersecretary. In turn, TLBs appoint Principal Security Advisors with responsibility for the systems that the TLB is the information owner of.

CIDA Governance and SCIDA

- To ensure the correct physical and environmental aspects of all MOD ICT fixed infrastructure are installed in a safe and secure manner, the lead authority is Coordinating Installation Design Authority (CIDA) Governance who are a sub-department of the Defence Digital Operations Pillar within Complex Delivery. CIDA Governance provide direction to all SCIDA capabilities to ensure that all ICT installations in use for Defence purposes are compliant with JSP 453 Part 4 Operations Defence ICT Installation Standards and other associated standards.

- Each site is appointed a SCIDA from SCIDA resource, a periodically updated list of appointed SCIDA is available on the CIDA Governance DefNet page. JSP 453 Part 4 Operations Defence ICT Installation Standards Ch 1 details the roles and responsibilities of a SCIDA and Ch 4 defines the CC procedures that they implement. The appointed SCIDA will provide support aligned to the assigned Service Level of that area.

Service Levels

- In rare situations, an entire site could be assigned a specific Service Level or more commonly a site is divided into different Service Levels allocated to facilities, rooms or even to isolated ICT systems within a facility. The Service Levels are assigned to ensure that the appropriate degree of SCIDA provision is afforded to all facilities. Areas with specific business critical requirements and are exposed to more frequent ICT change activity are given the maximum level of support. This approach gives the greatest benefit to operational capability, safety, and security.

- Three Service Levels have been devised to reflect the degree of SCIDA support activity required to comply with the requirements. Service Levels are assigned to areas through consultation between the Head of Establishment (HoE) or designated representative and the appointed SCIDA. Depending on various factors, a Service Level is subject to change by agreement of all relevant parties. Additional to managing ICT infrastructure change through a formalised process, SCIDAs will maintain Configuration Management Database (CMDB) documentation where required, deliver a planned program of configuration management tasks and conduct periodic facility audits that correlate to the assigned Service Levels. SCIDA audit forecasts and resultant reports will be communicated with site HoE or representative directly. In the absence of a HoE or appointed representative, the SCIDA will inform a nominated equivalent.

- Table 1 details the three Service Levels, allocation criteria and SCIDA activity associated to each level. The SCIDA activities associated to the assigned Service Level are minimum requirements and any relaxation of these requirements must be risk managed accordingly and agreed between the appointed SCIDA and relevant parties beforehand:

  - Table 1.

| SCIDA SERVICE LEVEL | SERVICE LEVEL ALLOCATION CRITERIA SITE/FACILITY/SYSTEM | SCIDA CHANGE CONTROL | MINIMUM MANDATORY AUDIT FREQUENCY | CM DOCUMENT REQUIREMENT | SCIDA SUPPORT ACTIVITY |
| --- | --- | --- | --- | --- | --- |
| 1 | 1. Any RED IPZ 2. Any NER housing Tier 3 Equipment. 3. Supporting flight or maritime safety. | 1. Establish a CMDB Baseline and maintain through a formal change process accordingly. 2. Full ECR process mandatory. JSP 453 Part 4 Defence ICT Installation Standards Ch 4 details the ECR process. | 12 months. | Establish and maintain a minimum CMDB data set specific to the level of protective marking inclusive of TEMPEST coupling zones. | 1. Manage the ECR process (or equivalent). 2. Implement measures to prevent unauthorised change. 3. Maintain the CMDB and associated documentation. 4. Conduct mandatory audits. |
| 2 | 1. Any AMBER IPZ 2. Any NER housing Tier 1 or Tier 2 Equipment. | 1. Establish a CMDB Baseline and maintain through a formal change process accordingly. 2. Full ECR process mandatory. JSP 453 Part 4 Defence ICT Installation Standards Ch 4 details the ECR process. | 24 months. | Establish and maintain a minimum CMDB data set specific to the level of protective marking inclusive of TEMPEST coupling zones. | 1. Manage the ECR process (or equivalent). 2. Implement measures to prevent unauthorised change. 3. Maintain the CMDB and associated documentation. 4. Conduct mandatory audits. |
| 3 | 1. Any GREEN or YELLOW IPZ. 2. All exclusively Tier 1 business environments. | Full ECR process mandatory. JSP 453 Part 4 Defence ICT Installation Standards Ch 4 details the ECR process. | Sample audits on an opportunity basis. | Establish and maintain a minimum CMDB data set specific to the level of protective marking inclusive of TEMPEST coupling zones. | 1. Manage the ECR process (or equivalent). 2. Implement measures to prevent unauthorised change. 3. Maintain the CMDB and associated documentation. |

Minimum CMDB data sets

- The minimum CMDB data sets differ between Service Levels, Table 2 details the requirements for each:

  - Table 2:

|  | Service levels |  |  |
| --- | --- | --- | --- |
| Documentation | 1 | 2 | 3 |
| All formal change process documentation | M | M | M |
| Building floor plans detailing telecommunications outlet locations, TEMPEST coupling zones and all classifications (red/black/blue) of ICT cable containment routes | M | M | D* |
| External and Internal Approved Routes | M | M | M |
| Network Equipment Room and Data Centre layout plans | M | M | D* |
| Rack face layouts (cabinet face plans) | M | M | D* |
| Site plans detailing ICT outside plant (pits and ducts) | M | M | D* |
| Building elevation plans, wall views etc | D | D | D |
| *For Service Level 3, if existing records are held, these are to be maintained |  |  |  |

M = Mandated

D = Desirable

CIDA Governance audits

- To evaluate if the correct level of SCIDA support to the assigned Service Level is maintained, CIDA Governance audit against five core SCIDA processes:

  - Process 1 - Establish and maintain a CMDB baseline.

  - Process 2 - Employ and maintain a formal ICT change control process.

  - Process 3 - Update drawings, associated configuration documents and other relevant information.

  - Process 4 - Provide SCIDA advice and guidance.

  - Process 5 - Conduct SCIDA audits relevant to assigned Service Level(s).

- To assist in the standardisation of the CIDA Governance SCIDA audits, these processes are broken down into sub-requirements which are expanded in the tables below:

  - Table 3:

| Process 1 – Establish and maintain a Configuration Management Database baseline |  |  |
| --- | --- | --- |
| Requirement | Item | Sub-Requirement |
| A primary requirement of the SCIDA is to understand the ICT infrastructure and installations in the appointed area. Each facility or system requires to be surveyed to gain an understanding of the state of inherited installations, CMDB records and procedures. This baseline activity is to be undertaken during routine SCIDA audits and so carried out incrementally with full completion not exceeding 24 months of area appointment. Any identified non-compliances or non-conformances are to be reported to the relevant risk owner for inclusion on the relevant risk register and risk numbers allocated for future reference. | 1.1 | Carry out baseline activities during routine SCIDA audits. |
|  | 1.2 | Update baseline documents with the relevant Drawing Office. |
|  | 1.3 | Non-compliances and non-conformances identified during the baseline surveys are recorded and reported to the relevant risk holder as required. |

  - Tasks related to creating and establishing a baseline can vary depending on the area to be surveyed. The initial full baseline should be a once only activity then the maintenance of the CMDB documents are routine, ongoing SCIDA tasks through the formal change process.

  - Table 4:

| Process 2 - Employ and maintain a formal change control process |  |  |
| --- | --- | --- |
| Requirement | Item | Sub-Requirement |
| It is essential to prevent unauthorised change which undermines SCIDA control therefore there is a need to establish and use a robust CC process where the SCIDA is notified of a proposed change at the earliest opportunity. All proposed change must be authorised by the appointed SCIDA. Any change without notifying the SCIDA is classed as an unauthorised change and a breach of MOD policy. The formal CC process maintained by CIDA Governance contains 5 elements; the Engineering Change Request (ECR) model process is provided in JSP 453 Part 4 Defence ICT Installation Standards Ch 4. Equivalent documentation can be used providing that as a minimum all the information detailed in the formal ECR process documents are included. Changes are to be assessed to ensure compliance with MOD requirements and are not to adversely affect the site, existing systems or other concurrent change(s). Resources may dictate the level of SCIDA CC applied to Service Level 3 areas however in all cases, regardless of Service Level, the change process must be followed. | 2.1 | A record is to be maintained of every ECR 1, ECR 2, ECR 3, ECR 4 and ECR 5 (or equivalent). |
|  | 2.2 | On receipt of ECR 1, fulfil drawing requests to change proposers within 10 working days. |
|  | 2.3 | Proposals at ECR 2 are reviewed and responded to within 10 working days, this may involve a physical survey. |
|  | 2.4 | Once a design has been confirmed as compliant and conformant, ECR 3 issue is completed within 10 working days |
|  | 2.5 | Within 10 working days of ECR 4 receipt, assess each completed change for compliance and conformance. This involves a physical inspection and includes an assessment of the as-fitted documentation supplied for completeness and accuracy. |
|  | 2.6 | Once an installation is deemed compliant and conformant, issue of ECR 5 and updates to all CM records are completed 10 working days. This timeframe includes lodging CMDB updates with the relevant drawing office. |
|  | 2.7 | During protracted installation work the SCIDA is to periodically assess the change to identify potential issues early enough for change proposer resolution prior to the change being completed. |
|  | 2.8 | Proposed new external underground or overhead ICT installations are to follow the formal change control process. |
|  | 2.9 | If unauthorised change has been identified, a retrospective change process is carried out and attempts be made to prevent reoccurrence. The unauthorised change agent should be identified, and the details provided to the relevant stakeholder. |
|  | 2.10 | Any local issues with change, installation standards or procedural refusals that cannot be resolved by SCIDA are to be raised to CIDA Governance. This includes organisations unwilling to follow the formal change process or bad installation practice. |

  - Table 5:

| Process 3 – Update drawings, associated configuration documents and other relevant information |  |  |
| --- | --- | --- |
| Requirement | Item | Sub-Requirement |
| ‘As Fitted’ or ‘As Built’ drawings are required in support of CM. For existing installations, they should be current, readily available and provide a complete history of change. The SCIDA Framework Document detailing assigned facility Service Levels form part of the CMDB. To bolster the CM portfolio and to aid with proposed future ICT installations, the SCIDA should engage with the relevant site FM Team to gain any relevant drawings. This could include, but not limited to, site plans, underground service plans, building floor plans etc. | 3.1 | Ensure all necessary CM information is complete, accurate and readily available. CC and CM documents are to be stored electronically in the relevant shared area. All CM drawings are to be filed with the relevant Drawing Office. |
|  | 3.2 | Update CM drawings, databases and any other relevant CM documentation as required. This is an ongoing task through the course of SCIDA duties. Updates are to be completed and filed with the relevant Drawing Office within 10 working days. |
|  | 3.3 | For Service Level 1 and Service Level 2 facilities, establish and maintain TEMPEST coupling Zone drawings and a record of external and internal ‘Approved Routes’ (OSP/CMS) that can be referenced for future inspections and proposed new installations. |
|  | 3.4 | The SCIDA Framework Document is up to date and signed by the relevant site appointment. |
|  | 3.5 | Liaise with the site FM Team or equivalent to gain drawings to complement the CMDB. |

  - Table 6:

| Process 4 – Provide SCIDA advice and Guidance |  |  |
| --- | --- | --- |
| Requirement | Item | Sub-Requirement |
| To underpin CM at a site, the SCIDA will provide support and advice to all stakeholders. This support will include technical advice to change proposers and change designers on matters of installation standards and associated standards, regulations, and policy. | 4.1 | The SCIDA Competent To Practice (CTP) is current. |
|  | 4.2 | Suitable proficiency in accessing the ICT installation documentation and other associated standards required to deliver sound SCIDA advice. |
|  | 4.3 | Respond adequately to all requests to provide technical advice and guidance within 10 working days of receipt. An adequate response is considered an answer to the query, or a holding reply to gain external advice on their behalf. |
|  | 4.4 | Understand the escalation/support process for queries that cannot be fulfilled from own resource. |
|  | 4.5 | Can facilitate MOD contractor requests for access to JSP 453 Part 4 Defence ICT Installation Standards, |
|  | 4.6 | Attend and provide input to any relevant boards, meetings, or forums. These could be project meetings, change advisory boards, site periodic infrastructure meetings, siting boards, invitation to tender etc. All relevant meeting minutes or records of decisions which may affect current or future ICT infrastructure are to be held with the CC pack. |
|  | 4.7 | Establish and maintain relationships with pertinent key stakeholders in the assigned Area of Responsibility (AOR). This could be HoE, FM Team, Estate Team, G6 community etc. |

  - Table 7:

| Process 5 - Conduct SCIDA audits relevant to assigned Service Level(s) |  |  |
| --- | --- | --- |
| Requirement | Item | Sub-Requirement |
| To ensure continuing conformance to CIDA Governance requirements, sites, facilities, or systems must be regularly inspected by the SCIDA. The frequency of inspection is determined by the assigned Service Level. This will require the creation of a SCIDA inspection program that must be communicated with the HoE or equivalent. Inspections of each area are to assess the current state/condition of the ICT infrastructure, highlight unauthorised change and any deterioration of installation standards i.e. bad practice. This information is to be included in an inspection report. Any non-compliant or non-conformant installation is to be highlighted in the report with remediation recommendations. | 5.1 | Maintain a SCIDA audit program incorporating all sites, facilities, and/or systems in the SCIDA Configuration Boundary. This should be a live document and the program should clearly articulate the areas to be audited and the frequency of inspection. |
|  | 5.2 | Carry out SCIDA inspections in accordance with the audit program. |
|  | 5.3 | For issues with external enabling provisions for ICT Infrastructure, an effective reporting and resolution process is employed. This could include exhausted ICT cabinet/NER power provisions, failing cooling provisions (Air Conditioning (A/C) or Heating Ventilation Air Conditioning (HVAC)). |
|  | 5.4 | On completion of a planned inspection, within 10 working days submit a comprehensive report to the relevant stakeholders (HoE, FM Team etc). |
|  | 5.5 | ICT installation non-compliances or non-conformances are detailed on SCIDA audit reports and referenced correctly. |
|  | 5.6 | Non-compliances or non-conformances that are outstanding from the previous SCIDA audit are escalated accordingly and entered on the relevant Risk Register as required. |

The Configuration Boundary and Assigned Service Levels

- The SCIDA Configuration Boundary covers all aspects of fixed ICT infrastructure within the appointed AOR. Table 8 details the area of SCIDA provision with the assigned Service Level which is to be completed by the SCIDA and agreed with the HoE or appointed representative. Once agreed this document is to be signed by these parties and held on electronic record in the relevant repository. A signature block is provided in Table 9. A copy of this document is to accompany the Defence Digital site agreement and is to be reviewed and resigned annually. All previous versions are to be archived in the relevant repository for future reference.

  - Table 8 – SCIDA Configuration Boundary and Assigned Service Levels (SCIDA to add/delete rows as required):

| Insert site name |  |  |
| --- | --- | --- |
| Ser | Facility/Floor/Room/System | Assigned Service Level |

  - Table 9:

| The signatures below acknowledge that: 1. The Service Level(s) detailed in Table 8 have been agreed with the HoE (or representative) and the appointed SCIDA. This document will be reviewed and reissued annually by the appointed SCIDA. 2. The HoE (or representative) has received a signed copy of this document. |  |  |  |
| --- | --- | --- | --- |
| HoE or appointed representative |  | Appointed SCIDA |  |
| Name |  | Name |  |
| Rank/Grade |  | Rank/Grade |  |
| Appt |  | Appt |  |
| Date |  | Date |  |
| Signature |  | Signature |  |
| Contact e-mail |  | Contact e-mail |  |

Notes provided by the SCIDA

- This para is a free text area for the appointed SCIDA to add any pertinent points they wish to make the HOE or representative aware of. Such points may be:

  - Access to certain key areas.

  - Site support required to carry out SCIDA duties.

HMG Security Policy Framework (www.)

JSP 440 - The Defence Manual of Security