## Sheet1
Scottish Hydro Electric Power Distribution (SHEPD)
Subsea cable Supply
Request for Information
ED2 Delivery Strategy |  |  |  | 2022-01-01
Nr | Question |  |  | Suppliers Response
General
1 | Company Name
2 | Applicant makeup (e.g. Sole Applicant, Joint Venture etc.)
3 | Single point of contact details for IPQQ
4 | Tel / mobile contact number for PQQ Contact
5 | Email address for PQQ and ITT
6 | Company registered address
7 | Is the Applicant interested in submitting a PQQ for the proposed Contract. If NO please do not complete this RFI request.
Technical
8 | SHEPD will be looking to procure Subsea cable per the following specification, confirm ability to manufacture subsea cable to this specification and provide technical data sheet :
Cable Specification
3 core copper conductor (Class 2, stranded copper and comply with the requirements of BS EN 60228)
XLPE insulation (to IEC 60502-2 or equivalent and shall include additives to provide water tree retardancy)
Copper tape or copper foil laminate screen
Double wired armour (two layers of bitumen coated, hot dipped 6 mm galvanised steel wire) - torsionally balanced
1 x internal 48 fibre optic cable (ITU-T G652D)
No factory joints will be acceptable
9 | Confirm when order is required in order to secure delivery dates as per lengths / times below:
| Delivery Date | Cable Length (KM) | Conductor Size
| 2023-04-01 | 40 | 400
| April 2024 (Flexible) | 15 | 300
| 2025-04-01 | 15 | 185
| 2025-04-01 | 40 | 500 or 630
| 2026-04-01 | 46 (can be supplied as 6 and 40 lengths) | 400 or 500
| 2027-04-01 | 35 | 500 or 630
10 | Confirm estimated manufacture period for each cable length / type
11 | SHEPD have a storage facility at Nigg Energy Centre, Cromarty Firth. Confirm if cable manufacturer can deliver and the delivery duration.
12 | Confirm if lengths above can be manufactured with no factory joints and if not define the minimal length that can be manufactured without factory joints
13 | Confirm if manufacturer has ability or any installation agreements with vessel providers and subsea cable installation contractors to provide a Engineer - Procure - Construct (EPC) turnkey method of delivery, and if so, is there a minimum route length or contract value to consider to provide such an approach?
14 | If the manufacturer is interested in providing a EPC solution, please provide details of projects delivered and proposed delivery partners