## Schedule of Work
Appendix A
MCA - SCHEDULE OF WORKS
Site Address: |  | Daedalus Technical Training Centre
PO13 9FL
Project Type: |  | Installation of Air Conditioning Equipment
Tenderers for the above contract should complete the tables below, indicating what they would charge for each required element. Prices must: • Be stated in Pounds Sterling; • Include all other charges and overheads associated with the element being priced.
|  | General Works, Site Conditions and Prelims: | Tender: £ | Tenderer Comments
Notes
** | Existing main power supply and distribution boards to be reviewed. Any improvements must be advised at tender stage and detailed to the MCA. |  | 0
** | Works are to be undertaken outside normal working hours and all areas are to be returned to full use and cleared of all risings for the core training hours of 08:00hrs to 17:30hrs Monday to Friday. |  | 0
** | All works are to comply with current legislative regulations and best practice guidance.
1 | Health, Safety & Environment
1.01 | Allow for the provision of all pre-construction safety file documentation including risk assessments, method statements, COSHH assessments & F10 submissions on behalf of the client (if appropriate). |  | 0
1.02 | Allow for all new staff and operatives to undertake a site safety induction prior to starting work on the site. This is envisaged to last approximatly 20 minutes per person. |  | 0
1.03 | Allow for all safety related equipment including such items as barriers, working at height access and lifting equipment to enable the works to be carried out with minimal risk to operative and building users |  | 0
1.04 | Allow for all new penetrations through the building fabric to be sealed using appropriate fire and smoke stopping materials |  | 0
1.05 | Allow for all approriate waste transportation licences and ensure all arrisings are removed from site and disposed of in an environmentally approved manner. Extreme care should be taken to ensure that no waste arisings are allowed to be insecurely left outside the building at any time due to the high risk of wind blown Foriegn Object Debris (FOD) causing hazards to the adjacent airport operations. |  | 0
2 | Design Works
2.01 | Allow for all investigations of the existing equipment to enable the new system to function as required on completion of the project. |  | 0
2.02 | Allow for all design works and calculations to ensure the new refrigeration system is sized appropriate to the building construction and 100% of the foreseen outside air temperatures espected appropriate to the geographic area over the next 10 to 15 years. |  | 0
2.03 | Allow for all electrical design work and calculations for additional supplies to support the new heat pump system |  | 0
3 | Statement of Requirement
3.01 | Allow for the provision of a DX refrigeration heat pump with multiply room indoor units to provide heating and cooling to the training office, 3 in number training classrooms and the I&T Comms Room. Room layout plans can be found at Appendix A |  | 0
3.02 | Allow for all electrical installation works and cabling / pipework support works to facilitate the above installation |  | 0
3.03 | Optimum room temperature to be 22 degrees Celsius with minimal fluctuation around the set point during operation. The room temperature is to be adjustable for variations in occupancy and individual user preference by use of a wall mounted or remote controller in each room, heat and cooling is to be achievable in adjacent rooms simultaneously.
3.04 | Separate out of working hours set points are to be avialable together with frost protection to protect the rooms and maintain the controlled spaces at a reasonable temperature when not in use.
3.05 | Indoor units are to be either flush ceiling mounted or wall mounted units as best approriate to the room considerations, they should be silent running appropriate to a teaching enviornment and be located to minimse uncomfortable draughts to occupants of the controlled space.
3.06 | The chosen system is to be energy effiecent and use environmentally approved refrgerant with a foreseen lifespan greater than 10 to 12 years
3.07 | Allow for the monitoring of the new heat pump system by the existing Trend 963 Building Management System (BMS). Information required to be recorded is running status & room temperatures by numeric lists and graphs providing historic data. |  | 0
3.08 | Allow for the modification of the existing underfloor heating via the Trend 963 Building Management System to prevent the underfloor heating adversly reacting with the new heat pump system in these particular rooms while maintaining operation of the remainder of the building. The option should be made available to return the underfloor heating to use for a period should the heat pump fail and require a extended repair at some time in the future. |  | 0
4 | Completion
4.01 | Allow for the provision of 2 x electronic copies and one printed hard copy of all commsionning certification, test sheets, manufacturers installation, user operation and engineers service and maintenance guides, suppliers contact information, disposal information, ammended BMS strategy and logic modifications etc. together with full layout and schematic drawings of the complete install in DWG. & PDF. This information is to be presented in a post-construction health and safety file format. |  | 0
4.03 | On completion the Contractor to undertake deep clean of working areas and leave the premises clean and tidy, free from dirt, dust and any builders waste and plant. |  | 0
5 | Preliminaries & Overheads
5.01 | Prelims |  | 0
5.02 | Overheads & Profit |  | 0
| TENDER TOTAL |  | 0
| VAT |  | 0
| TOTAL INCLUSIVE OF VAT |  | 0
The nominated Procurement Manager is:
Kathy Monk
Finance & Contracts
Bay 3/19 – Spring Place
105 Commercial Road
Southampton
SO15 1EG
Tel:- 020 381 72328
Email: - Contracts@mcga.gov.uk
| Signed: | Name (Block Capitals):
in the capacity of:
duly authorised to sign tenders for and on behalf of (in BLOCK CAPITALS):
Postal Address:
| Telephone No: | Email:
Date:

## App A - Floor Plan
Appendix B