CIVIL WORKS CONTRACT

DIO OS DTE (B)

BATSUB

BOOKLET 3 PERFORMANCE SPECIFICATION FIRM PRICE CONTRACT FOR BEL/GE/1902 HV CABLE LEG 4 BATSUB, PRICE BARRACKS, BELIZE, BFPO 12

INTENTIONALLY BLANK

Drawings

# The drawings attached to this document, are to be read in conjunction with this Performance Specification (PS) for the proposed Service Trench construction.  It should be noted that the Authority’s drawings are ‘Concept Only’ and the Contractor is to produce a full set of design documentation and confirm quantities and distances in line with the Concept and Authority’s Drawings.

# Design Responsibilities

# The Contractor shall ensure all Works are carried out in accordance with, and includes the applicable requirements of, all relevant British Standards and DIO documentation along with all other design documents specified within this PS.  NOTE that these references are provided as guidance and minimum requirement only; the responsibility remains with the Contractor to ensure that all design and construction Works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the Works, geography, climate, environment and Theatre of operations.  Where there are conflicts between the Contractor’s design drawings and the Specification (Booklet 3), the PS will take precedence in all cases.  Any queries should always be addressed to the Authority in the first instance.  The references and specified British Standards (BS) and Euro Norms (EN), within this PS are to be used (or similar Authority approved standards) as a minimum standard, throughout the Works.

# UK Building Regulations.  All Works shall comply with the latest UK Building Regulations.  Should any variation be required, approval from the Authority shall be obtained in writing prior to the commencement of any Works.

# Health and Safety (H&S).  All Works shall be carried out in accordance with the Health and Safety at Work Act 1974 (HASAWA 74).  The Contractor shall submit a Construction Phase Plan (CPP) to the Authority for approval, including all risk assessments, method statements, hazardous material procedures, etc. to comply fully with CDM 2015.

# Construction Drawings.  All Works shall be constructed in accordance with the approved construction drawings (or written proposal). No works shall commence prior to obtaining written approval of the final construction drawings and proposals from the Authority.

# Design Life.  The proposed refurbishment design life to first major overhaul, repair or replacement shall be a minimum of 10 years.  The Contractor shall install all components, elements, systems and structures to satisfy this requirement, and if requested provide documentary evidence to support this.

# Existing Services.  The Contractor is responsible for ensuring all services on or adjacent to the site that will be affected by the Works are identified, located and appropriate action taken to prevent damage before work commences.  The Contractor shall ensure that any existing services and concrete slabs are reinstated to a condition at least similar to existing, with the minimum of disruption to existing facilities and services during construction.  All Works that could possibly influence existing services may only commence with written approval.  The Authority must be informed immediately if any unknown services are discovered that will have an impact on the Works or safety.

# The Contractor shall ensure that any existing services and affecting Works are of an acceptable standard to ensure the required performance over the life of the facility.  Should it be found that one or more of the services is not considered acceptable to the requirements, the Contractor shall inform the Authority and obtain written approval / instruction prior to taking any actions to rectify or make good the pertinent unacceptable situation.

# Construction Preliminaries

# Location Plan.  The location of the proposed Works within Price Barracks is shown at Dwg No. DIOB/PB/BEL_GE_1902/G/001.

# Obstructions.  As the proposed Works are to be carried out around existing infrastructure and surrounding areas, there are obstructions in the form of fences, trees and buildings etc, the Contractor is to review the site before commencing Works.

# H&S Restrictions, Precautions and Monitoring.  The Contractor shall implement the requirements described in the HASAWA 74 to protect members of the public and persons visiting the site from risks arising from the use of equipment, materials or substances defined therein.

# Control of Noise and Vibration.  The Contractor shall comply with the recommendations for practical measures to reduce noise set out in BS 5228: Parts 1, 2 and 3.

# Resource yard.  It is expected that the Contractor will not require a forward resources area other than the site. Should one be required a location within Price Barracks shall be made available, as agreed by DIO (B).  The Contractor shall be solely responsible for storage and movement of all equipment to site.  The Contractor shall remain at all times responsible for the security of equipment including prevention of theft.

# Scope of the Overall Works

- General.  This PS outlines the requirements and scope for the excavation, bedding, laying of cable and backfilling of a 185m service trench for the new HV cable that will connect 2No. sub-stations (Laundry Lines sub-station to 25 Flt sub-station) located within the BATSUB Estate.

- The Authority.  The only persons authorised to give instructions are the Superintending Officer (SO) and the Works Contract Officer (WCO).

- Existing Assets.  The Works are situated within BATSUB, Price Barracks.  The Works location and route will be within the proximity of many live and occupied assets within Price Barracks.  This information can be found on Dwg No. DIOB/PB/BEL_GE_1902/G/001.

- Restrictions to the Works.  The Works are to be undertaken without interfering with every day running of the Authority’s operations.  The demarcation of the Site boundary is to be obvious and clearly marked to restrict access to the Site whilst the Works are being undertaken.

- Proposed Works.  The location where the Works are required are shown on Dwg No. DIOB/PB/BEL_GE_1902/G/001.  It is the Contractor’s responsibility to attend site and confirm quantities and descriptions detailed below.  A site visit will be conducted during the ITT meeting and Contractors are also free to arrange access at a later date.  The Scope of Works (SoW) for the contract is as follows:

  - Groundworks.  The SoW for the Groundworks are as follows:

    - Site set up.  Fence off and secure the relevant sections (progressive lengths of the excavation) where excavation Works will be carried out.

    - Statement of known Services.  The Authority will provide a Statement of known Services to the Contractor upon Contract Award.

    - Works for the Service Trench.  The Contractor is required to excavate, lay materials, lay cable and backfill to ground level a Service Trench that is 185m (Long) x 350 mm (Wide) x 1m (Deep), from the Laundry Lines sub-station to the 25 Flt sub-station. The Construction and formation of the Service Trench can be seen on Dwg No. DIOB/PB/BEL_GE_1902/C/001.

# General Specification

- Construction.  The specification for construction Works are as follows:

  - Site set up.  Fence off and secure the relevant sections (progressive lengths of the excavation) where excavation Works will be carried out.  The Contractor is to ensure all relevant safety signage is easily viewable to members of the public, Host Nation Forces, BATSUB personnel and all others that will possibly traffic areas of where the Works will be conducted at all times.  The working area is to be secure and fenced off at all times to prevent general access to the working site areas.

  - Statement of known Services.  The Authority will provide a Statement of known Services to the Contractor upon Contract Award; however the Contractor is to ensure the following:

    - The Contractor (along with an Authority Representative) will confirm the area of Works to be excavated is clear of and / or identify the areas where there are buried services along their proposed demarcation for that day.

    - The Contractor is in possession of an Authority signed and dated Permit to Dig / Permit to Work before proceeding with any excavation Works and Groundworks.

    - Upon completion of the programmed section of excavation the Contractor will inform the Authority before commencing with the following section of excavation.  This will then follow the same process as per para 19.b.(1) and para 19.b.(2).

  - Service Trench Works.  The Construction and formation of the Service Trench can be seen on Dwg No. DIOB/PB/BEL_GE_1902/C/001.  The Service Trench for the cable shall be excavated, constructed and finished using the following in method:

    - Excavation.  The Contractor is required to safely excavate a service trench 185m (Long) x 350 mm (Wide) x 1m (Deep), from the Laundry Lines sub-station to the 25 Flt sub-station.  The excavation will be through varying terrain, materials and ground conditions.  The formation level of the excavation is to be well compacted.  The Service Trench is to be excavated safely in manageable sections.

    - Bedding.  The Contractor is to lay a 100mm thk (top to bottom) bedding layer of fine sand, to the bottom of the excavation.  The sand is to be laid and well compacted in 50mm layers.

    - Cable.  The Contractor is to lay the (Authority provided) 3 Core 35mm2 XLPE/CTS,SWA/PVC cable, centrally in the trench on top of the sand bedding layer.  The Contractor (along with an Authority Representative) is to ensure there is sufficient cable protruding at either side of the service trench to connect into each sub-station ie. Laundry Lines sub-station point and 25 Flt sub-station point.

    - Protective layer.  The Contractor is to lay a 150mm thk (from top of cable) protective layer of fine sand.  The sand is to be laid and well compacted in 50mm layers.

    - Backfill stage 1.  The Contractor is to replace a 150mm layer of the previously excavated soil into the excavation on top of the protective layer of sand.  The soil should be clear of all rocks, stone, debris, etc and well compacted in 75mm layers.

    - Warning tape.  The Contractor is to lay Electrical Warning tape centrally within the excavation, directly on top of the compacted backfill (300mm above the top of the cable).

    - Backfill stage 2.  The Contractor is to replace the remaining excavated soil into the excavation, up to finished ground level. The soil should be clear of all rocks, stone, debris, etc and well compacted in 75mm layers.

- Testing and Commissioning.  The Testing and Commissioning is the sole responsibility of the Authority along with connecting the cable into each sub-station.

Management of the Works

- Liaison with the Authority.  The Contractor shall designate one person from within his organisation who will be responsible for liaising with the Authority or his representative (SO) on a day to day basis and as the need arises.  The Liaison Officer must have the capability of reading, writing, speaking and receiving instructions in the English Language, including being able to understand and interpret technical drawings and specifications.  The Liaison Officer must be able to explain the work operations to persons performing the work in a language that those performing the work are capable of understanding.  The person so designated shall be responsible for communicating with the Authority regarding notification of intended work and explaining the effect that the Works will or may have on the operation or systems within the site.  The Liaison Officer will be responsible for responding to the Authority's enquiries and dealing with any issues or complaints.  It is a requirement that the Contractor's Liaison Officer makes daily contact with the Authority such that an active rather than a responsive attitude to liaison is maintained.  The Contractor's Liaison Officer is a key person in achieving the successful execution of this Contract.

- Supervision.  The Contractor shall accept responsibility for co-ordination, supervision and administration of the Works, including all sub-contracts.  They shall arrange and monitor a Programme with each Sub-Contractor, local Employer and any statutory undertaker, and obtain and supply information as necessary for co-ordination of the work.  In addition to constant management and supervision of the Works provided by the Liaison Officer, all significant types of work must be under the close control of competent trade supervisors to ensure maintenance of satisfactory progress and quality.

- Co-ordination of Engineering Services.  The site organisation staff must include one or more persons with appropriate knowledge and experience of Groundworks and Civil engineering in relation to the Works generally.

- Approvals.  Where products or work are specified to be approved or the Authority instructs or requires that they are to be approved, the same must be supplied and executed to comply with all requirements.

- Notice of Completion.  The Contractor is to provide the Authority at least 7 days notice of the anticipated dates of Practical Completion of the whole or parts of the Works.

- Quality Standards / Control.  The Contractor will ensure quality standards and controls.

  - Proprietary Materials.  All materials shall conform to the following:

    - Handle, store, prepare and use each material in accordance with its specification and type.  Inform PM if there is any other specified requirement. Submit copies to PM when requested.

  - Checking Quantity and Condition of Products and Materials.  The Contractor shall check all material, labels, identification marks and where appropriate the products themselves to ensure that all products comply with the Contract Documents.  In particular, check that the products comply with the following sub-paragraphs.

    - Sizes are correct.  Where tolerances are critical, measure a sufficient quantity to ensure compliance.

    - The quantities are correct, to ensure that shortages do not cause delays in the Works.

    - The products and materials are clean, undamaged and otherwise in good condition.

  - Protection of Products and Materials.  All materials and products shall be protected to ensure that they remain in the condition they are required to be in.  In particular, the Contractor is to ensure that materials and products are to be kept clean, protected from the elements and kept in original wrappings until required for the Works.

- Setting Out.  The Contractor is responsible for all setting out and shall check out the dimensions of the site against those detailed by the Authority, and record the results.  The Contractor shall inform the Authority when overall setting out is complete and before commencing Groundworks.

- Timing of Inspections.  The Contractor is to agree dates and times of inspections with the PM four days in advance, to enable the PM and other affected parties to be present.  On the previous working day to each such inspection the Contractor is to confirm to the PM that the work in question will be ready or, if not ready, agree a new date and time.

- Proposals for Rectification of Defective Work.  As soon as possible after any part(s) of the Works are known to be not in accordance with the Contract, or appear that they may not be in accordance, the Contractor is to submit proposals to the PM for inspection, making good, or removal and re-execution.  Such proposals may be unacceptable to the PM and he may issue contrary instructions.

- Quality Control.  The Authority will carry out regular inspections to control the quality of the Works being delivered.  Where defects are identified, these will be remediated in accordance with paragraph 19.  The Contractor is to establish and maintain procedures to ensure that the Works comply with the specified requirements within this PS.

- Work at or after completion.  The Contractor is required to undertake the following Works prior to handover.

  - Make good all damage consequent upon the Works, including levelling of ground.

  - Remove all temporary markings, coverings and protective wrappings unless otherwise instructed.

- Making Good Defects.  The Contractor is to make arrangements with the PM and give reasonable notice of the precise dates for access to the various parts of the Works for purposes of making good defects.  The PM is to be informed by the Contractor when remedial Works to the various parts of the Works are completed and ready for approval.

Documents to be provided by Contractors

- Work Based Information.  For the purposes of the proposed Contract, the Contractor shall provide as a minimum a written scheme detailing the proposed method of works for each element of the proposed Works.  Due to the simple nature of the proposed Works, design drawings will not be required, though pictorial representation of proposals included within the written scheme will be acceptable.

- Site Diary.  The Contractor shall keep an up to date, daily, site diary.  This document is to be used to record all decisions made on the site both verbal and written.  The document is also to be used to record visits to site and note anything, which has a direct effect on the Contract in terms of cost and extensions to time, or any other occurrence that affects the Works Programme.  All changes must have been agreed and authorised by the Authority.  The site diary shall list in writing all issued Variation Orders (VO) and site instructions, including amended drawings, and verbal decisions made on site.  All verbal decisions must be recorded in writing no less than 24hrs after they have been made and entered in the site diary.  The Contractor shall on request make the site diary available for the Authority to inspect.  This document will be used as the audit trail in light of any disputes, concerning the Contract.

General Conditions

- Permits to Work (PTW) and Authorisation.  The Contractor shall comply with the Client’s PTW system and the JSP 375, Volume 3, (details of which are obtainable from the Authority SO), including the provision of method statements, risk assessments, Permit to Dig, etc.

- The responsibility remains with the Contractor to obtain all necessary authorisations including but not limited to a Permit to Dig, security and access to the camp and site, fencing / screens to isolate other existing facilities from the Works, etc. required to commence and complete the Works.

- The Contractor shall at all times ensure that full coordination, cooperation and liaising with the SO is achieved and maintained.

Drawings

DIOB/PB/BEL_GE_1902/G/001	-	HV Cable Leg 4 Route

DIOB/PB/BEL_GE_1902/C/001	-	HV Cable Trench Detail

The Health & Safety at Work Act 1974.

Construction (Design & Management) Regulations 2015 (CDM 2015).

BS 5228 Control of Noise on Construction sites, Part 1, 2 & 3.

JSP 375 Management of Health and Safety in Defence.