## Site A - NG16 3RZ
Site A
Unit 11
Site Description | Building Size | Title | Description of works required | Cost
Industrial Estate with several units, no. of units requiring works 6 |  | CODE 2
|  | Meter Tail Cintainment | Redress meter tails and provide appropriate containment as necessary
|  | Fire Alarm | Supply and install new dedicted circuit c/w localised isolator, circuit to be wired in FP cable, test circuit on completion of works
|  | DB1 | Isolate and remove existing consumer unit and isolators, supply and install new 12way three phase distribution board c/w appropriate mcb's, rcbo's and upgrade main earth conductor, supply and install earth rings for armoured cables, on completion of works carry out inspection and test of circuit and issue BS7671 test certificate
|  | Defective Sockets | Isolate and remove 5no defective metal clad RCD sockets with new metal clad sockets, subject to DB being replaced.
|  | Existing Cables | isolate and remove cut off cable in MCB's, remove redundant MCB's and install appropriate blanks.
|  | Circuit RYB 1 | isolate and remove existing fuse wire and replace with appropriate rating to provide suitable overload protection.
|  | Lighting Circuits | Isolate and remvoe existing fuse wire for 3no lighting circuits and replace with appropriate rating to provide suitable overload protection.
|  | Meter Tails | Redress meter tails and install appropriate fixings
|  | Upgrade of Earthing | Earth conductors to main incoming water service, structural steel and supplementary bonding as necessary.
|  | DB2 | isolate and remove 1no existing consumer unit and supply and install 1no 5 way front end RCD consumer unit c/w mcb's, main eart conductor and meter tails.
TOTAL
Extra over cost for the code 2 items
|  | Out of Hours Work | Tenant has indicated some of the works may need to be carried out at weekends i.e. replacement of dist boards to minimise disturbance to his business, pc sum for out of hours works
CODE 3 ITEMS (to be carried out during normal working hourse)
|  | Roller Shutter Isolator | Supply and install 1no 32amp DP isolator c/w enclosure for roller shutter, carry out minor alterations to wiring and test operation on completion of works.
|  | Kitchen Isolator | Isolate and remove existing defective isolator and replace with new.
|  | Containment | Replace missing section of containment and fixings, repair and install plates/grommets in containment as necessary
|  | Grommets | Isolate and remove accessories and install grommets, replace accessories on completion of works, install grommet strip to main switch
|  | Phone System Socket | Isolate and remove existing cable, carry out alterations to containment, install gland and reinstate cable
|  | Workshop Socket | Supply and install bling grommet to socket outler near workshop sink
|  | Label Devises | Label sockets to demote circuits
|  | Fuses | Ref only, resoled if DB replaced
|  | Dist Board Schedules | Supply and install 2no dist board schedules
|  | 3p Isolator | Isolate and remove obsolete isolator and replace with new 3 pn&e 16 amp interlock socket, carry out minor alterations to wiring as necessary
|  | Ladies WC | Isolate and remoe defective light fitting skirt and replace with new
TOTAL
Unit 12
|  | Board Schedules | Trace and identify circuits, supply and install dist board schedules and labels to both dist boards.
|  | RCD Protection | Isolate and remove 5no existing MCB's and supply and install 5no RCBO's to provide RCD protection to appropriate circuits isolate and remove redundant MCB's and install blanks, on completion of works carry out inspection and test of installation and issue BS7671 test certificate.
|  | Workshop Socket | Isolate and remove defective wiring, supply and install new twin switched socket c/w associated wiring and containment of works carry out inspection and test of circuit and amend test certificate.
|  | Water Heater | Redress cable and supply and install appropriate fixings and support for flex.
|  | Router | Existing installation does not comply with BS7671, installation installed by tenant, works to be carried out by others
|  | Compressor | Existing installation does not comply with BS7671, installation installed by tenant, works to be carried out by others
TOTAL
Unit 14
CODE 2
|  | DB Cover | Repair and rescue dist board
|  | RCD Protection | Carry out alterations to wiring, supply and install enclosure and RCD protection to 2no 3 phase circuits and 5no single phase circuits on cmpletion of works carry out inspection and test of circuit and issue BS7671 test certificate.
|  | Mezanne Area Containment | Pc sum to address issues with cables laid around, no form of mechanical protection, carry out installation of containment, provide quotation for any major works
|  | Circuits 3/L2 & 6L2 | Isolate and remove additional circuits, supply and install 2no additional MCB's and reconnect circuits, test on comnpletion of works, amend and issue BS7671 test ciertificate
|  | External Lights | Carry out alterations to wiring and supply and isntall 1no RCD fused spur for external light, test operation on completion of works.
|  | Circuit 5/L1, 2, 3 | Isolate and remove existing MCB abd replace with new to provide appropriate overload protection, on cmpletion of works test circuit and amend test certificate.
|  | Work Bench Lights | Carry out minor alterations to wiring, supply and install localised isolator c/w appropriate overload protection
|  | Circuit 2/L3 | Isolate and remove additional circuits, supply and install 2no additional MCB's and reconnect circuits, test on completion of works, amend and issue BS7671 test certificate.
|  | Phase Isolator | Supply and install 1no 60amp 4 pole isolator c/w enclosure, carry out minor alterations to wiring and test operation on completion of works.
|  | Meter Tail Containment | Redress meter tails and provide appropriate containment as necessary
|  | DB Blanks | Supply and install appropriate dist board blanks
TOTAL
CODE 3
|  | Labels/Dis Board Schedules | Supply and install labels and dist board schedules
|  | Stairs Area Socket | Isolate and remove existing defective socket and back box and replace with new
|  | Containment | Redress cables and supply and install containment for cables around stairs area dn dist board. Replace missing section of containment and fixings, repair and install plates/grommets in containment as necessary.
|  | Earthing Arrangements | Supply and install earth tags for existing eart connections to structural steel and water services
|  | Water Heater | Redress existing cable to water heater and resecure
|  | Sleeving | Isolate and remvoe light fittings and switches and provide sleeving to identify live conductors
|  | SWA Glands | Isolate and remove existing cable, replace SWA glans to both ends, supply and install earth rings for armoured cables, on completion of works carry out inspection and test circuit and issue BS7671 test certificate.
|  | Neutral Conductors | Isolate neutral conductors within dist board, trace and identify associated circuit and reterminate to provide sequential sequence with live and earth condutors.
|  | WC and Passage Light Switches | Isolate and remove light switch, correctly terminate earth conducotrs within back box and reinstate plate.
|  | Workshop Light | Redress cable and supply and install appropriate fixings, reterminate at light point.
TOTAL
Unit 15
CODE 2
|  | Meter Tail Containment | Redress metera tails and provide appropriate containment as necessary
|  | DB Blanks | Supply and install appropriate dist board blanks
|  | Live Conductors | Trace and identify cables, reterminate cables and rest associated circuits
|  | Workshop Socket | Isolate and remove existing defective RCD socket and back box and replace with new
|  | Circuit B | Isolate and remove existing MCB and replace with new to provide appropriate overload protection, on completion of works test circuit and amend test certificate
|  | Toielt Water Heters | Carry out alterations to wiring and supply and install 2no RCD fused Spru for water heaters, test operation on cmpletion of works
|  | TRCD Protection | Carry out alterations to wiring, supply and install RCBO's to provide RCD protection to 3no single phase circuits, on completion of works carry out inspection and test of circuit and issue BS7671 test certificate.
TOTAL
CODE 3
|  | DB Cover | Rpair and resecure dist board cover
|  | SWA | Redress cables and resecure
|  | Main Isolator | Supply and install 1no 100 amp 4 pole isolator c/w enslocure, carry out minor alterations to wiring and test operation on completion of works.
|  | Circuit R1 | Isolate and remove existing MCB and replace with new to provide appropriate overload protection, on completion of works test circuit and amend test certificate.
|  | Labels/Dist Board Schedules | Supply and install labels and dist board schedules
|  | Grommets | Isolate and remove accessories and install grommets, replace accessories on completion of works, install grommet strip to main switch.
|  | Fire Alarm | Redress cables and provide appropriate fixings
|  | Neutral Conductors | No access to neutral conductors, ref only
|  | Label Devices | Label sockets and isolators to denote circuits
|  | Sleeving | Isolate and remove light fittings and switches and provide sleeving to identify live conductors
|  | Containment | Replace missing section of lighting trunking lidding and install fixings for workshop containment
|  | Office Socket | Isolate and remove existing defective RCD socket and back box and replace with new
TOTAL
Unit 16
CODE 2
|  | RCD Protection | Carry out alterations to wiring, supply and install enclosure and RCD protection to 6no single phase circuits, on completion of works carry out inspection and test of circuit and issue BS7671 test certificate
|  | Upgrade of Earthing | Earth conductors to main incoming water service, structural steel and supplementary bonding as necessary
TOTAL
Code 3
|  | Kitchen Sockets | Redress cables and resecure
|  | Labels/Dist Board Schedules | Supply and install labels and dist board/schedules
|  | Water Heater | Isolate and remove water heater accessories and install grommets and connect earth cable to face plate replace accessories on completion of works
|  | RRHS WC Light | Isolate and remove existing batten holder and repalce with new
TOTAL
Unit 18
Code 2
|  | Upgrade of Earthing | Earth conductors to main incoming water service, structural steel and supplementary bonding as necessary.
|  | DB1, 2, 3 | Exisiting Distribution boards require replacing
|  | Fire Alarm | Supply and install new dedicated circuit c/w localised isolator, circuit to be wired in FP cable, test circuit on completion of works
Code 3
|  | Water Heater | Isolate and remove water heater accessories and install grommets and connect earth cable to face plate accessories on completion of works
TOTAL

## Site B - DE5 3QL
-
Unit 1
Site Description | Building Size | Title | Description of works required | Cost
Industrial Estate with several units, no. of units requiring works 8 |  | Entrance Light | Isolate and remove 1no existing light fitting, carry out minor alterations to wiring, supply and install appropriate joint box and new light fitting c/w lamp, test operation on completion of works.
|  | Upstairs Office Socket | Isolate and remove existing defective socket outlet and back box and replace with new, test operation on completion of works
|  | External Light | Pc sum to trace and rectify fault with external light, carry out minor repairs
|  | Earth Conductors | Isolate earth conductors within dist board, trace and identify associated circuit and reterminate to provide sequential sequence with live and neutral conductors.
TOTAL
Unit 2
|  | RCD Protection | Isolate and remove 4no existing MCB's and supply and install 4no RCBO's to provide RCD protection to appropriate circuits, on completion of works carry out inspection and test of installation and issue BS7671 test certificate
|  | Steel Structure | Supply and install earth tag to main conductor to steel structure
|  | DB1 Circuit 2 | Pc sum to trace and rectify fault with ring main, carry out minor repairs
|  | Earth Conductors | Isolate earth conductors within dist board, trace and identify associated circuit and reterminate to proide sequential sequence with live and neutral conductors.
|  | Water Service | Isolate and remove existing earth clamp, carry out alterations to wiring and install new earth clamp in corection position, test continuity on completion of works
TOTAL
Unit 3
|  | Steel Structure | Supply and install main earth conductor to steel structure c/w containment, test continuity on completion of works
|  | Board Schedules | Trace and identify circuits, supply and install dist board schedules and label to both dist boards
|  | Circuit 2 | Isolate and remove cables, supply and install additional MCB and connect new circuit, test on completion of works and amend test certificate.
|  | Sleeving | Isolate and remove light switches and provide sleeving to identify live conductors
|  | Extract Fan | Isolate and remove existing extract fan and replace with new, supply to be derived from existing supply, replace external grill.
|  | Wc Extractor Fan Isolator | Supply and install localised isolator for extract fan, carry out alterations to wiring and containment and carry out inspection and test on completion of works and issue BS7671 test certificate.
|  | Neutral Conductors | Isolate neutral conductors within dist board, trace and identify associated circuit and reterminate to provide sequential sequence with live conductors.
|  | Main Isolator | Supply and install 100 amp triple pole isolator, carry out alteration to meter tails and test operation.
|  | Dist Board | Trace and identify circuits and label outgoing fuse ways as appropriate.
TOTAL
Unit 4
Code 2
|  | Consumer Unit | Isolate and remove existing consumer unit and supply and install 1no surface mounted metal clad 15 way dual RCD consumer unit c/w mcb's, supply to be derived from existing incoming service, on completion of works carry out inspection and test of whole of electrical installation and issue BS7671 test certificate.
|  | Circuits 6 & 9 | Pc sum to trace and rectify fault with cross over on circuit, carry out minor remedial works
|  | Neutral Conductors | Isolate neutral conductors within dist board, trace and identify associated circuit and reterminate to provide sequential sequence with live conductors.
|  | Steel Structure | Supply and install main earth conductor to steel structure c/w containment, test continuity on completion of works.
|  | Damaged Cable | isolate and make safe existing cable, carry out repairs to cable in workshop office, extend and replace as necessary.
|  | Circuit 5 | Pc sum to trace and rectify fault with continuity readings, carry out minor remedial works
|  | SWA Cable | isolate and remove existing SWA cable, supply and install earth tag, lugh and earth cable,, test continuity and reterminate cable.
Code 3
|  | Containment | Resecure containment above Dis Board, install saddles near roller shutter door, replace missing fixings as necessary.
|  | Sleeving | Isolate and remove light switches and provide sleeving to identify live conductors
|  | Label Isolator | Supply and install label to identify operation
|  | Fused Spur | Resecure fused spur, replace missing fixings as necessary
|  | Immersion Heater | Resecure immersion heater flex
|  | Board Schedules | Trace and identify circuits, supply and install dist board schedules and label to dist boards
|  | Extract Fan | Isolate and remove existing extract fan and replace with new, supply to be derived from existing supply, replace external grill
|  | WC Extract Fan Isolator | Supply and install localised isolator for extract fan, carry out alterationns to wiring and containment and carry out inspection and test on completion of works and issue BS7671 test certificate
|  | Water Service | Isolate and remove existing earth clamp, crry out alterations to wiring and nstall new earth clamp in correction position, test continuity on completion of works
TOTAL
Unit 5
|  | DB1 | Isolate and remove existing consumer unit and isolators, supply and install new 8 way three phase distribution board c/w appropriate mcb's, rcbo's and upgrade main earth conductor
|  | Board Schedules | Trace and identify circuits supply and install dist board schedules and labels to both dist boards.
|  | Water Service | Supply and install label to identify locate on earth board.
|  | WC Extract Fan Isolator | Supply and install localised isolator for extract fan, carry out alterations to wiring and containment and carry out isnpection and test on completion of works and issue BS7671 test certificate
|  | Containment | Resecure containment and install appropriate fixings to secure inspection lids and replace missing end cap to dado trunking.
TOTAL
Unit 6
|  | Sleeving | Isolate and remove light switches and provide sleeving to identify live conductors.
|  | Board Schedules | Trace and identify circuits supply and install dist board schedules and label to both dist boards.
|  | Steel Structure | Supply and install main earth conductor to steel structure c/w contianment, test continuity on completion of works
|  | Water Heater | Redress cable and supply and install appropriate fixings and support for flex
|  | Office Socket | Isolate and remove existing defectie socket outlet and replace with new, test operation on completion of works.
TOTAL
Unit 7
|  | Upgrade Earthing | Supply and intall eart conductors to various section of cable tray, test continuity on completion of works
|  | 2, 4 SWA Cables | Pc sum to address issues with 4no existing SWA cables, isolate and remove existing cables, reterminate glands and conductors, retest circuit and amend test certificate.
|  | RCD Protection | Supply and install RCD protection for socket outlet on wall opposite DB, carry out alterations to wiring and supply and install RCD twin switched socket c/w back box , on completion of works carry out inspection and test of circuit and issue BS7671 test certificate
|  | Containment | Replace defective containment and associated fixings about walk in freezer, for workshop fan and above DB.
|  | WC Water Heater | Pc sum to replace/repair toilet water heater
|  | Entrance Light | pc sum to rectify fault with existing light fitting, test installation, trace and identified fault, carry out repairs/replace defective light
TOTAL
Unit 8
|  | RCD Protection | Isolate and revove 2no existing MBs and supply and install 2no RCBO's to provide RCD protection to appropriate circuits, isolate and remove redundant MCB's and install blanks on completion of works carry out inspection and test of installation and issue BS7671 test certificate.
|  | Wc Extact Fan | Isolate and remvoe defective extract fan and replace with new, test operation on completion of works
|  | Warehouse Twin Spot Emergency Light | Isolate and remove existing defective twin spot emergency light and replace with new, test operation on completion of works
|  | Stairs Twin Post Emergency Light | Isolate and remove existing defective twin spot emergency light and replace with new, test operation on completion of works
|  | Kitchenette Area EM Light | Isolate and remove existing light fitting and replace with new LED maintained emergency light, test operation on completion of works.
TOTAL

## Site C - DE75 7HA
Site C
Site C
Site Description | Building Size | Item | Description of works required | Cost
Depot used for storing of vehicles and canteen for operational staff and includes, small office, canteen, ladies toilet/shower room, gents toilets/shower room, clenaing cupbaord, 8 out buildings for storing of materials/tools etc. |  | Rest Room EM Light | Isolate and remove existing defective Emergency Light fitting, carry out minor alterations to wiring, replace with new LED light fitting and test operation of works.
|  | RCD Protection | Isolate and remove 10no existing MCB's, carry out minor alterations to wiring and containment, supply and install encloser c/w RCBO's test circuits and amend BS7671 test certificate.
|  | DB4 Circuit B5 | Pc sum to test existing installation, trace and identify faults
|  | Redundant Smoke Detectors | Isolate and remove redundant smoke detectors and disconnect supplies from consumer units.
|  | Rest Room | Redress existing cable and resecure under window area
|  | Circuit 11 | Isolate and remove 6no SWA cables, regland cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works
|  | DB1 | Isolate and remove existing consumer unit and isolators, supply and install new 16 way three phase distribution board c/w appropriate mcb's, rcbo's and upgrade main earth conductor, on completion of works carry out inspection and test of circuit and issue BS7671 test certificate.
|  | DB1 Circuit 7 | Pc sum to test existing installation, trace and identify faults
|  | DB1 Circuit 6, 10, 11 | Pc sum to trace and identify circuits
|  | DB1 Area EM Light | Isolate and remove existing defective EM light fitting, carry out minor alterations to wiring, replace light with new LED light fitting and test poeration on completion.
|  | DB1, Circuit 14 | Isolate and remvoe existing defective RCD and replace with new, test circuit and amend test certificate.
|  | Camera Column | Isolate and remvoe existing metal clad isolator and replace with new IP rayed unit, reterminate cables and test operation.
|  | Workshop Socket | Isolate and remove existing defective socket outlet and replace with new, reterminate cables and test operation
|  | Workshop Consumer Unit | Isolate and remove existing consumer unit and supply and install 1no 6 way consumer unit c/w RCBO's, test installation on completion of works and issue BS7671 test certificate.
|  | Workshop Containment | Carry out repairs to containment and replace missing section of liding.
|  | Workshop Office Socket | Supply and install blank within back box.
|  | Workshop DB Circuit 1 | Pc sum to test existing installation, trace and identify faults
|  | Corridor Socket | Isolate and remove existing defective socket outlet and replace with new, reterminate cables and text operation
|  | Office Consumer Unit | Isolate and remove existing consumer unit and supply and install 1no 10 way consumer unit c/w RCBO's, test installation on completion of works and issue BS7671 test certificate
|  | Office DB, Circuit 8 | Pc sum to trace and identify circuit, test and amend test certificate
|  | External Lighting | Carry out repairs to external lighting contactor and resecure
|  | Contactor | Carry out minor repairs alterations to wiring and reterminate
|  | External Lighting DB | Supply and install blank within dist board.
|  | External Lighting DB | Isolate and remove SWA cables, regland cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works
|  | External Light Consumer Unit | Isolate and remove existing consumer unit and supply and install 1no 6 way consumer unit c/w RCBO's, test installation on completion of works and issue BS7671 test certificate.
|  | DB2, Old Boiler House | Supply and install blank within dist board.
|  | DB3 Earth Tags | Isolate and remove SWA cables, regland cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works.
|  | DB3 Blanks | Supply and install blanks with dist board
|  | DB3 MCB's | Isolate and remove existing redundant MCB's and supply and install blanks within dist board
|  | Garage Flood Light | Isolate and remove existing defective flood light fitting, carry out minor alterations to wiring, replace light with new LED light fitting and test operation of works.
|  | Boiler House Socket | Isolate and remvoe existing defective socket outlet and replace with new IP rated unit, reterminate cables and test operation.
|  | Boiler House Switch | Isolate and remvoe existing defective switch and replace with new IP rated unit reterminate cables and test operation
|  | Lighting columns Earth Tags | Isolate and remove SWA cables, regland cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works.
|  | Garage Consumer Unit | isolate and remove consumer unit and supply and install 1no 5 way IP rated consumer unit c/w RCD main switch and MCB's test installation on completion of works and issue BS7671 test certificate.
|  | Garage Socket | Isolate and remvoe existing defective socket outlet and replace with new IP rated unit, reterminate cables and test operation.
|  | Garage Containment | isolate and remvoe existing lighting circuit, rewire circuit c/w associated wiring and containment, reconnect existing light switches and fitting, test circuit on completion of works and amend BS7671 test cert.
|  | Container Light Switch | Isolate and remvoe existing defective switch and replace with new IP rated unit, reterminate cables and test operation
|  | DB11 Circuit 1 | Pc sum to test existing installation, trace and identify faults
|  | DB11 | Isoalte and remove existing consumer unit and supply and install 1no 10 way dual RCD consumer unit c/w MCB's test installation on completion of works and issue BS7671 test certificate.
|  | Redundant Cables | Isolate and remove redundant cables.
|  | DB11 Circuit 4 | Carry out alterations to wiring and partial rewire circuit.
|  | Office Heater Spur | Isolate and remove existing defective switched fused spur and replace with new, reterminate cables and test operation, works carried out at time of test.
|  | Mains Room Socket Containment | Supply and install containment for office socket cables located in main cupboard
|  | Dist Board Schedules | Supply and install 15no dist board schedules
|  | Diesel Tank Supply | Pc sum to carry out alterations to supply to diesel tank, disconnect earth conductor and alter earting arrangments, install earth rod and pit
|  | DB9 Container Supplies | Isolate and remove SY cables, regalnd cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works.
|  | Container External Socket | Isolate and remvoe existing defective socket outlet and replace with new IP rated unit, reterminate cables and test operation.
|  | Container External Light | Ioslate and remove exisitng defective external floor light and replace with new LED unit, reterminate cables and test operation.
|  | Contianer Earth Tags | Isolate and remvoe SWA cables, regalnd cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works.
|  | Container Socket | Carry out alterations to wiring and rewire circuit
|  | Label DB | Supply and install labels to consumer units in containers
|  | Container Supplies | Pc sum to carry out alterations to supplies to containers, discnnect earth conductor and alter earthing arrangements, install eart rod and pit
TOTAL

## Site D - DE75 7DU
Site D
Site Description | Building Size | Item | Description of works required | Cost
Public conveniences consisting of, ladies, gents & disabled toilet facilities. Also consists of market stall holders services area. |  | Code 2 Items
|  | Time Clock | Replace cover for Sanfgamo time clock
|  | DB1 Circuit 11 | Pc sum to investigate issue with low insulation resistance readings to 4no lighting circuits
|  | Lamp Posts | Pc sum to reterminate and install enclosure for 11no lamp posts carry out minor alterations to wiring
|  | Dist Board | Isolate and remove existing consumer unit internal components, supply and install din rail and connectors, extend existing cables, manufacture steel plate to cover existing consumer unit, supply nd install new consumer unit c/w appropriate RCBO's MCB's and blanks, test installation on completion of works and issue BS7671 test certificate on completion of works.
|  | Contractor Enclosure | Supply and install grommets and blanks as necessary
|  | DB2 MCBS | Isolate and remove 2no existing MCB's and replace with new to provide appropriate overload protection, reconnect circuits, test on completion of works, amend and issue BS7671 test certificate.
|  | RCD Protection | Carry out alterations to wiring, supply and install enclosure and RCD protection to 2no single phase circuits, on completion of works carry out inspection and test of circuit and issue BS7671 test certificate.
|  | Gents Toilet Light | Isolate and remove existing defective light fitting and replace with new
|  | Market Stores Light | Remove existing light fitting, resecure and reterminate, test operation on completion of works, investigate issue with 2nd light, trace and identify fault, carry out repairs to wiring and replace with new
|  | Market Stores Valve | Pc sum to rectify fault with valve and replace cover
|  | Market Stores/External Lights | Pc sum to trace and rectify fault with external lights
|  | Upgrade of Earthing | Earth conductors to main incoming water service and supplementary bonding as necessary
|  | Market Stores DB | Pc sum to investigate issue with water ingress, install grommets and blanks
|  | Market Store Extract Fan | Pc sum to repair/replace extract fan
|  | Circuit 2 | Isolate and remove existing MCB and replace with new and reconnect circuit, test on completion of works, amend and issue BS7671 test certificate
|  | Lighting Circuit 6 | Pc sum to investigate issue with low insulation resistance readings to lighting circuit
TOTAL Code 2 Items
Code 3 Items
|  | Service Cut Out | Ref only, service cut out eart cover is missing, require replacing, works to be carrie dout by Western Pwer - Western Power to rectify (no charge)
|  | 110v Transformer | Isolate and remvoe defective section of wiring, rewire and supply and install appropriate IP rated connection point
|  | Neutral Conductors | Isolate neutral conductors within dist board, trace and identify associated circuit and reterminate to provide sequential sequence with live conductors
|  | DB1 MCB | isolate and remove existing MCB and replace with new to provide appropriate overload protection, reconnect circuits, test on completion or works, amend and issue BS7671 test certificate
|  | Board Schedules | Trace and ifentify circuits, supply and install dist board schedules and labels to dist board
|  | Ticket Machine Circuit | Isolate cables from MCB, label and install blank
|  | DB2 Cable | Redress exisitng cable and provide appropriate fixings to support cable
|  | DB2 Labels/Dist Board Schedules | Supply and install labels to sockets isolators and dist board schedules
|  | SWA Cable | Redress SWA cable at low level adjacent pillar and provide support/fixings as necessary
|  | Toilet Socket Enclosure | Supply and install cover to existing 32 amp socket outlet
|  | Toilet DB Labels/Dist Board Shcedules | Supply and install labels to isolators and dist board schedules
|  | Toilet DB Blanks/Grommets | Supply and install appropriate dist board blanks and grommets
|  | Roof Void Smoke Detector | Supply and install 1no mains voltage interlinked smoke detector c/w 10 year lithium cell and associated wiring, supply to be derived from localised detector
|  | Market DB Labels/Schedules | Supply and install labels to socket isolators and dist board schedules
|  | Circuit 6 | Isolate and remove additional circuits, supply and install 2no additional MCB's and reconnect dircuits, test on completion or works, amend and issue BS7671 test certificate
|  | Sleeving | Isolate and remove cover to dist board and provide sleeving to identify earth conductor for incoming SWA cable.
|  | Dis WC Wall Heater | Pc sum to investigate and rectify fault with wall heater
|  | Disabled Alarm PSU | Resecure power supply unit and replace cover screws as necessary
|  | Disabled Fan Spur | Resecure fan spur, replace cover screws as necessary
TOTAL Code 3 Items

## Site E - DE55 4EY
Site E
Site Description | Building Size | Item | Description of works required | Cost
Public park changing rooms for use of footballers |  | Lighting Circuit | Disconnect existing lighting circuits, carry out alterations to wiring and containment and supply and install 2no RCD modules c/w localised isolators enclosures, supply to be derived from existing distribution boards, on completion of works test associated dircuits and amend BS7671 test certificates.
|  | Dist Board Schedules | Supply and install 2no dist board schedules
|  | Bathroom Extract Fan | Isolate and remove 1no extract fan and replace with new, carry out minor alterations to wiring as necessary, supply to be derived from existing localised isolator.
|  | External Lighting Contactor | Carry out repairs to external contactor and enclosure
|  | Circuit 2 | Carry out minor alterations to wiring wihin consumer unit, supply and install new MCB, split circuits, terminate cables, test circuit and amend test certificate
|  | Dist Board | Supply and install new bus bar shield, carry out minor repairs to enclosure
|  | Label Dist Board | Supply and install labels to dist board
|  | External Lighting | Pc sum to trace and identify fault with external lights
|  | Changing Room EM Light | Isolate and remove existing defective EM light, carry out alterations to wiring to ensure light operates with correct circuit under fault conditions, replace light with new LED unit and test operation on completion of works.
|  | Disabled Alarm | Pc sum to trace and identify fault with alarm system
|  | Shower Pull Switch | Isolate and remove existing shower pull switch and replace with new, test operation on completion of works
|  | Dist Board | Isolate and remove cables within distribution board and reterminate cables to ensure sequential connections of neutral and CPC's
|  | External Lighting Circuit | Isolate and remove existing MCB and replace with appropriate RCBO, carry out minor alterations to wiring, test associated circuit and amend BS7671 test certificate
|  | Changing Room Fan | Carry out minor alterations to wiring and supply and install localised isolator for extract fan, test operation on completion of works.
TOTAL

## Site F - DE5 3EF
Site F
Site Description | Building size | Item | Description of works required | Cost
Small public park with a Mess Room for park operative, garage for storage of equipment and Bandstand |  | Garage Light | Isolate and remove existing NCF light fitting and replace with new, test associated circuit on completion of works
|  | Mess Room Power | Carry out minor alterations to wiring and containment and supply and install 2no additional twin switched sockets, on completion of works test circuit and amend test certificate.
|  | Garage Consumer Unit | Isolate and remove existing consumer unit, carry out minor alterations to existing containment and wiring, supply and install new off stand mounting frame and 1no surface mounted IP reated 7 way fronted RCD consumer unit c/w MCBs, on completion of works carry out inspection and test of whole of electrical installation and issue BS7671 test certificate.
|  | Mess Room Heater | Redress cable and supply and install fixings
|  | Main Incoming Service Hut | Ingress of water through roof, works to be addressed by others, no costs included
|  | Bandstand contianment | Resecure existing containment, supply and install saddles as necessary
|  | Main Earth Conductor | Upgrade main earth conductor
|  | Bandstand Submain | Isolate and remove existing incoming sub main cable, supply and isntall earth tags and earth conductor within consumer unit, test continuity.
|  | Main Dist Board | Isolate and remove existing Dist board, carry out minor alterations to existing containment and wiring, supply and install new offstand mounting frame and 1no surface mounted IP rated 7 way frontend RCD consumer unit c/w mcbs, uprgade meter tails and main earth conductor, on completion works carry out inspection and test of whole of electrical isntallation and issue BS7671 test certificate
|  | Incoming Services | Existing meter requires addressing, new mounting foard required, works to be carried out by other, Western Power/Service Provider, no costs included
|  | Bandstand Sockets | Isolate and remove 4no existing socket outlets and replace with 4no IP rated sockets terminate existing cables and test on completion of works
|  | Bandstand Consumer Unit | Isolate and remove existing consumer unit, carry out minor alterations to existing containment and wiring, supply and install 1no surface mounted IP rated 5way frontend RCD consumer unit c/w mcbs, on completion of works carry out inspection and test of whole of electrical installation and issue BS7671 test certificate.
|  | Water Service | Upgrade earth conductor to main incoming water service
TOTAL

## Site G - DE5 3BT
Site G
Site Description | Building Size | Item | Description of works required | Cost
Unoccupied 1st floor office building |  | Label Switch Banks | Supply and install labels to 6no switch banks
|  | Dist Board Schedules | Supply and install dist board schedules
|  | Male WC Spur | Isolate and remove defective switched fused spur with neon and replace with new
|  | Interview Room containment | Resecure containment and assocaited boxes
|  | DB1A Circuits 5 & 6 | Isolate and remove 2no existing MCBs and replace with appropriate RCBO's, carry out minor alterations to wiring, test associated circuits and amend BS7671 test certificate.
|  | DB1A Circuit 5, 9 & 10 | Pc sum to trace and identify circuits, test and amend test certificate
|  | Small Office Light | Isolate and remove existing defective LED panel light fitting, carry out minor alterations to wiring, replace light with new LED light fittings and test operation on cmpletion of works
|  | Main Room Light Switch | isolate and remvoe defective wiring, redress and reroute, carry out alterations, resecure cables and reterminate, test operation on completion of works.
|  | First Floor, Floor Socket | Pc sum to repair/replacefloor socket lid
|  | Print Room Socket | Isolate and remove existing defective socket outlet and replace with new, reterminate cables and test operation
|  | Print Room Socket | Isolate and remove existing defective socket outlet and replace with new, reterminate cables and test operation
|  | Print Room Socket | Isolate and remvoe existing socket outlet, carry out repairs to back box, rethread and replace, reterminate cables and test operation
|  | Meeting Room, Floor Socket | Pc sum to repair/replacefloor socket lid
|  | RCD Protection | Isolate and remove 10no existing MCB's, carry out minor alteration to wiring and containment, supply and install enclosure c/w RCBO's, test associated circuits and amend BS7671 test certificate
|  | Cupbaord Socket | Isolate and remvoe existing socket outlet and replace with new RCD socket, reterminate cables and test operation.
|  | Water Heater Isolators | Isolate and remove 2no existing switched fused spurs and replace with new RCD spurs, reterminate cables and test operation.
|  | Floor Socket | Isolate and remove existing defective socket outlet and replace with new reterminate cables and test operation.
|  | External Lighting RCD | Ioslate and remove 1no existing switched fused spur and replace with new RCD spur, reterminate cables and test operation.
|  | DB1A Circuit 19 | Pc sum to trace and identify faults with circuit
|  | Interview Room, Floor Socket | Pc sum to rectify faults with floor socket
|  | SWA Earth Tags | Isolate and remove SWA cables, regalnd cables, supply and install earth tags and cable to incoming earth terminal, test continuity on completion of works.
|  | DB1A Ring Main Readings | Pc sum to trace and identify faults with ring main circuits
|  | Tea Room Water Heater | Isolate and remvoe existing outlet point and replace with new IP rated unit, reterminate cables and test operation.
|  | RCD Protection | Ioslate and remove 12no existing MCB's and replace with appropriate RCBO's, carry out minor alterations to wiring, test associated circuits and amend BS7671 test certificate
|  | Circuit 2 | Isolate and remove 1no existing MCB and replace with appropriate RCBO, carry out minor alterations to wiring, test associated circuit and amend BS7671 test certificate
|  | Circuit 4 | Isolate and remove defective plug in ceiling rose and replace with new
|  | Circuit 9 | Isolate and remove 1no existing MCB and replace with appropriate RCBO, carry out minor alterations to wiring, test associated circuit and amend BS7671 test certificate
|  | DB1A Circuits 13 & 15 | Pc sum to trace and identify faults
|  | Groundwork Office | Isolate and remove defective plug in ceiling rose and replace with new
|  | Cupbaord Socket | Isolate and remove existing socket outlet and replace with new RCD socket, reterminate cables and test operation
|  | Redundant MCB's | Isolate and remvoe redundant MCB's and supply and install blanks within dist board.
|  | Arena Floor Sockets | Isolate and remove 3no socket outlets within floor boxes, reinstate to allow sockets to be used, test operation on completion of works
|  | Floor Socket | Pc sum to carry out repairs to 30-40 floor sockets, replace/repair earth lugs and test continuity.
TOTAL