## List of FD sitewide
Drawing No. | Area | Damper No. | Detailed Location | AHU-RED if CL3 | CL2 / CL3 / CL4 / No CL | System | Vertical / Horizontal Damper Fitting | Correct Fitting - Airflow Direction? | Level of Fouling at Damper | Ductwork cleaning recommended | Standard/ Exception | Cleaned | Reason | Recommendations
P14-016-04-2 | North Labs-Plantroom | FD 01 | North Labs Plantroom | 1/N/24 | 6002-6003-5124-5127 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 02 | North Labs Plantroom | 1/N/24/1 | 6002-6003-5124-5127 | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 03 | North Labs Plantroom | 1/N/24 | 6002-6003-5124-5127 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 04 | North Labs Plantroom | 1/N/24/1 | 6002-6003-5124-5127- Lockers | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 05 | North Labs Plantroom | 1/N/25 | 6007 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 06 | North Labs Plantroom | 1/N/25 | 6007 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 07 | North Labs Plantroom | 1/N/24/1 | 6002-6003-5124-5127 | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 08 | North Labs Plantroom | 1/N/24 | 6002-6003-5124-5127 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 09 | North Labs Plantroom -bottom of Stairs EX/1/N/24/1 | EX/1/N/24/1 | 6002-6003-5124-5127- Lockers | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 10 | North Plantroom Entrance bottom of Stairs 1/N/24 | 1/N/24 | 6002-6003-5124-5127- Lockers | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 11 | North Plantroom Entrance bottom of Stairs | 1/8/N/24/1 | 6002-6003-5124-5127- Lockers | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 12 | North Plantroom Entrance bottom of Stairs | 1/N/24 | 6002-6003-5124-5127- Lockers | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 13 | North Labs Plantroom | 1/N/20 | 5072-5073-6057-6058 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 14 | North Labs Plantroom | 1/N/20/1 | 5072-5073-6057-6058 | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 15 | North Labs Ground Floor, Cleaner's Cupboard between toilets - 1/N/20 | 1/N/20 | 5072-5073-6057-6058 | Supply |  |  | - | - | Exception | No | Access to fire damper restricted by wall
P14-016-04-2 | North Labs-Plantroom | FD 16 | North Labs Ground Floor, Cleaner's Cupboard between toilets - EX/1/N/20/1 | EX/1/N/20/1 | 5072-5073-6057-6058 | Extract |  |  | - | - | Exception | No
P14-016-04-2 | North Labs-Plantroom | FD 17 | North Labs Plantroom | 1/N/9/1 | 6008-6014-6016 | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 18 | North Labs Plantroom | 1/N/10 | 5120-5121 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 19 | North Labs Plantroom | 1/N/10 | 5120-5121 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 20 | North Labs Plantroom | 1/N/10 | 5120-5121 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 21 | North Labs Plantroom - Entrance bottom of Stairs - AHU 1/N/10 | 1/N/10 | 5120-5121 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 22 | North Labs Plantroom - Entrance bottom of Stairs - AHU 1/N/10 | 1/N/10 | 5120-5121 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 23 | North Labs Plantroom - Entrance bottom of Stairs - AHU 1/N/10 | 1/N/10 | 5120-5121 | Supply |  |  | Light | N0 | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 24 | North Labs Plantroom - Entrance bottom of Stairs - AHU 1/N/10 | 1/N/10 | 5120-5121 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 25 | North Labs Plantroom | 1/N/1 | 5101-5102-5106 | Supply |  |  | - | - | Exception | No | No access door fitted
P14-016-04-2 | North Labs-Plantroom | FD 26 | North Labs Plantroom | 1/N/1 | 5101-5102-5106 | Supply |  |  | - | - | Exception | No | Unable to access fire damper due to pipework in the way | Pipework blocking access to be removed or ductwork altered to provide new access section.
P14-016-04-2 | North Labs-Plantroom | FD 27 | North Labs Plantroom | 1/N/1 | 5101-5102-5106 | Supply |  |  | - | - | Exception | Yes | No access door fitted | New access section to be installed.
P14-016-04-2 | North Labs-Plantroom | FD 28 | North Labs Lower Corridor Riser Cupboard N11 - 1/N/1 | 1/N/1 | 5101-5102-5106 | Supply |  |  | - | - | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 29 | North Labs Lower Corridor Riser Cupboard N10 - 1/N/1 | 1/N/1 | 5101-5102-5106 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 30 | North Labs Plantroom | 1/N/2 | 6020-6027-6028-6034 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 31 | North Labs Plantroom | 1/N/2 | 6020-6027-6028-6034 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 32 | North Labs Plantroom | 1/N/2 | 6020-6027-6028-6034 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 33 | North Labs Plantroom | 1/N/2 | 6020-6027-6028-6034 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 34 | North Labs Plantroom | 1/N/2 | 6020-6027-6028-6034 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 35 | North Labs Plantroom | 1/N/2/1 | 6020-6027-6028-6034 | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 36 | North Labs Plantroom | 1/N/2/1 | 6020-6027-6028-6034 | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 37 | North Labs Plantroom | 1/N/4 | 5088 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-04-2 | North Labs-Plantroom | FD 38 | North Labs Plantroom | 1/N/4 | 5088 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-04-2 | North Labs-Plantroom | FD 39 | North Labs Plantroom | 1/N/4 | 5088 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 40 | North Labs Plantroom | 1/N/6 | 6050-6053 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 41 | North Labs Plantroom | 1/N/6 | 6050-6053 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 42 | North Labs Plantroom | 1/N/6 | 6050-6053 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 43 | North Labs Plantroom | 1/N/6 | 6050-6053 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 44 | North Labs Plantroom | 1/N/4 | 5088 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 45 | North Labs Plantroom |  | Riser Cupboard N17 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 46 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 47 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 48 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 49 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 50 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 51 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 52 | North Labs Plantroom | 1/N/9 | 6008-6014-6016 | Supply |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 53 | North Labs Plantroom | EX/1/9/1 | 6008-6014-6016 | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-04-2 | North Labs-Plantroom | FD 54 | North Labs Plantroom | 1/N/21 | 6052-6061 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 55 | North Labs Plantroom | 1/N/21 | 6052-6061 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 56 | North Labs Plantroom | 1/N/21/1 | 6052-6061 | Extract |  |  | Light | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 57 | North Labs Plantroom | 1N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 58 | North Labs Plantroom | 1/N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 58A | North Labs Plantroom | 1/N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 59 | North Labs Plantroom | 1/N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 60 | North Labs Plantroom | 1/N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 61 | North Labs Plantroom | 1/N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 62 | North Labs Plantroom | 1/N/5 | 6062-6054-6064 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 63 | North Labs Plantroom | 1/N/8/1 | 5078-5082 | Extract
P14-016-04-2 | North Labs-Plantroom | FD 64 | North Labs Plantroom | 1/N/8 | 5078-5082 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 65 | North Labs Plantroom | 1/N/23. No No: | 5080 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 66 | North Labs Plantroom | 1/N/18 | 5074-5075-5076 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 66A | North Labs Plantroom | N/A | Capped off. Needs hatch and number. 5074-5075-5076 | Extract
P14-016-04-2 | North Labs-Plantroom | FD 67 | North Labs Plantroom | 1/N/26 | 5074-5075 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 68 | North Labs Plantroom | 1/N/18/1 | 5074-5075-5076 | Extract
P14-016-04-2 | North Labs-Plantroom | FD 69 | North Labs Plantroom | 1/N/7 | 6053 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 70 | North Labs Plantroom | 1/N/7 | 6053 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 71 | North Labs Plantroom | N/A | Lift shaft. No no: or system | Supply | [7 empty] | Duct In lift cage but NO damper fitted
P14-016-04-2 | North Labs-Plantroom | FD 72 | North Labs Plantroom | 1/N/28 | Prion CL3, 6046, 6047 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 73 | North Labs Plantroom | 1/N/28 | Prion CL3, 6046, 6047 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 74 | North Labs Plantroom | 1/N/28 | Prion CL3, 6046, 6047 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 75 | North Labs Plantroom | 1/N/3 | 6139-6141-6142 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 76 | North Labs Plantroom | 1/N/3 | 6139-6141-6142 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 77 | North Labs Plantroom | 1/N/15/1 | 5098-5110-5103-6012-6013 | Extract
P14-016-04-2 | North Labs-Plantroom | FD 78 | North Labs Plantroom - AHU 1/N/14 | 1/N/14 | 6030-6031-6033-6035 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 79 | North Labs Plantroom - AHU 1/N/14 | 1/N/14 | 6030-6031-6033-6035 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 80 | North Labs Plantroom - AHU 1/N/14 | 1/N/14 | 6030-6031-6033-6035 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 81 | North Labs Plantroom - AHU 1/N/14 | 1/N/14 | 6030-6031-6033-6035 | Supply |  |  | Clean | No | Standard | Yes
P14-016-04-2 | North Labs-Plantroom | FD 82 | North Labs Plantroom | 1/N/16 | 5100-5104-5108 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 83 | North Labs Plantroom | 1/N/16/1 | 5100-5104-5108 | Extract
P14-016-04-2 | North Labs-Plantroom | FD 84 | North Labs Plantroom | 1/N/15 | 5103 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 85 | North Labs Plantroom |  | Not found
P14-016-04-2 | North Labs-Plantroom | FD 86 | North Labs Plantroom | 1/N/7 | 6139-6141-6142 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 87 | North Labs Plantroom | 1/N/7 | 6139-6141-6142 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 88 | North Labs Plantroom | 1/N/16 | 5100-5104-5108 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 89 | North Labs Plantroom | 1/N/15 | 6012-6013 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 90 | North Labs Plantroom | 1/N/14 | 6030-6031-6033-6035 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-04-2 | North Labs-Plantroom | FD 91 | North Labs Plantroom | 1/N/14 | 6030-6031-6033-6035 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-04-2 | North Labs-Plantroom | FD 92 | North Labs Plantroom | 1/N/27 | 6022 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 93 | North Labs Plantroom | 1/N/27 | 6022 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 94 | North Labs Plantroom - ex from room to box on the wall | N/A | ex from room to box on the wall
P14-016-04-2 | North Labs-Plantroom | FD 95 | North Labs Plantroom | 1/N/14 | 6030-6031-6033-6035 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 96 | North Labs Plantroom | 1/N/15/2 | 6012-6013 | Extract
P14-016-04-2 | North Labs-Plantroom | FD 97 | North Labs Plantroom | 1/N/15 | 5098-5110-5103-6012-6013 | Supply
P14-016-04-2 | North Labs-Plantroom | FD 98 | North Labs Plantroom | 1/N/25 | 6007 | Supply |  |  | Clean | No | Exception | No | Access panel too small to maintain fire damper | Fire damper is small in size therefore a removable duct section to be provided to permit fire damper access & maintenance
P14-016-04-2 | North Labs-Plantroom | FD 99 | North Labs Plantroom | N/A | Fresh air inlet only to lift shaft | Supply
P14-016-04-3 | North Labs-Plantroom | FD 100 | North Labs Plantroom | 1/N/15/2 | 6012-6013 | Extract
P14-016-05 | South Labs-Plantroom | FD 01 | South Labs Plantroom, 1/S/13 | 1/S/13 | 5020-5022 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 02 | South Labs Plantroom, 1/S/13 | 1/S/13 | 5020-5022 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 03 | South Labs Plantroom, 1/S/25 | 1/N/25 | 5021-5022-5023-5030 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 04 | South Labs Plantroom, 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 05 | South Labs Plantroom. 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 06 | South Labs Plantroom, 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 07 | South Labs Plantroom 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | Clean | No | Exception | No | Fire damper faulty and will not fully close | Fire damper to be replaced
P14-016-05 | South Labs-Plantroom | FD 08 | South Labs Plantroom 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 09 | South Labs Plantroom 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 10 | South Labs Plantroom 1/S/25 | 1/S/25 | 5021-5022-5023-5030 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 11 | South Labs Plantroom 1/S/25 | 1/S/25/1 | 5021-5022-5023-5030 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 12 | South Labs Plantroom EX/1/S/25/1 | 1/S/25/1 | 5021-5022-5023-5030 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 13 | South Labs Plantroom EX/1/S/25/1 | 1/S/25/1 | 5021-5022-5023-5030 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 14 | South Labs Plantroom EX/1/S/25/1 | 1/S/25/1 | 5021-5022-5023-5030 | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 15 | South Labs Plantroom EX/1/S/25/1 | 1/S/25/1 | 5021-5022-5023-5030 | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 16 | South Labs Plantroom 1/S/9 | 1/S/9 | 5041-5044 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 17 | South Labs Plantroom EX/1/S/9/1 | EX/1/S/9/1 | 5041-5044 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 18 | South Labs Plantroom 1/S/34 | 1/S/34 | 5041 | Supply |  |  | Clean | No | Standard | Yes
P14-016-06 | South Labs-Plantroom | FD 18A | South Labs Plantroom Not capped off | N/A | Not capped off but has damper | N/A
P14-016-05 | South Labs-Plantroom | FD 19 | South Labs Plantroom EX/1/S/25/1 | EX/1/S/25/1 | 5021-5022-5023-5030 | Extract |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 20 | South Labs Plantroom EX/1/S/34 | 1/S/34 | 5041 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 21 | South Labs Plantroom 1/S/5 | 1/S/5 | 3110 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 22 | South Labs Ground Floor, Riser Cupboard 1/S/18 | 1/S/18 | 3120 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 23 | South Labs Plantroom 1/S/30 | 1/S/30/2 | 5061-5062-5063-5064-5065 | Extract |  |  | - | - | Exception | No | No routine access to fire damper | Ductwork to be modified to allow new access door to be fitted
P14-016-05 | South Labs-Plantroom | FD 24 | South Labs Plantroom EX/1/S/30/1 | 1/S/30/1 | 5061-5062-5063-5064-5065 | Extract |  |  | - | - | Exception | No | No routine access to fire damper | Ductwork to be modified to allow new access door to be fitted
P14-016-05 | South Labs-Plantroom | FD 25 | South Labs Plantroom 1/S/31 | 1/S/31 | 5061-5062-5063-5064-5065 | Supply |  |  | - | - | Exception | No | Access door too small to maintain fire damper. | Existing access door to be removed and new access door to be fitted.
P14-016-05 | South Labs-Plantroom | FD 26 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2020 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 27 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2021 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 28 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2022 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 29 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2023 | Supply |  |  | Light | No | Exception | No
P14-016-05 | South Labs-Plantroom | FD 30 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2024 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 31 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2025 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 32 | South Labs Plantroom 1/S/6 | 1/S/6 | 5040-5035. System not in use 13/01/2026 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 33 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 34 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Heavy | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 35 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 36 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 37 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 38 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 39 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 40 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 41 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 42 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 43 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 44 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 45 | South Labs Plantroom 1/S/14 | 1/S/14 | 3080-3081-5013-5014 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 46 | South Labs Plantroom (near) EX/1/S/27/1 | EX/1/S/27/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 47 | South Labs Plantroom (near) EX/1/S/27/1 | EX/1/S/27/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 48 | South Labs Plantroom (near) EX/1/S/27/1 | EX/1/S/27/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 49 | South Labs Plantroom (near) EX/1/S/27/1 | EX/1/S/27/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 50 | South Labs Plantroom (near) EX/1/S/27/1 | EX/1/S/27/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 51 | South Labs Plantroom (near) EX/1/S/27 | EX/1/S/27 | 5010-5016-3077-3076-3075-3083 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 52 | South Labs by Stairway leading to Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 53 | South Labs Stairway leading to Plantroom EX/1/S/27/1 | EX/1/S/27/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 54 | South Labs Stairway leading to Plantroom EX/1/S/14/1 | EX/1/S/14/1 | 5010-5016-3077-3076-3075-3083 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 55 | South Labs Stairway leading to Plantroom EX/1/S/14 | EX/1/S/14 | 3080-3081-5013-5014 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 56 | In Plantroom opposite Main South Plantroom Entrance |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 57 | In Plantroom 5015 opposite Main South Plantroom Entrance |  |  | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 58 | South Labs Plantroom AHU 1/S/1 | 1/S/1 | 3133 | Supply |  |  | Very Heavy | Yes | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 58A | South Labs, Ground Floor Riser Cupboard |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 59 | South Labs Plantroom AHU 1/S/15 | AHU 1/S/15 | 3131 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 60 | South Labs Plantroom AHU 1/S/2 | 1/S/2 | 3118-3122-3127-3134-5052-5059 | Supply |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 61 | South Labs Plantroom EX/1/S/2/1 | EX/1/S/2/1 | 3118-3122-3127-3134-5052-5059 | Extract |  |  | Light | No | Standard | Yes | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 62 | South Labs Plantroom EX/1/S/2/1 | EX/1/S/2/1 | 3118-3122-3127-3134-5052-5059 | Extract |  |  | - | - | Exception | No
P14-016-05 | South Labs-Plantroom | FD 63 | South Labs Plantroom AHU | 1/S/36 | 3124 | Supply
P14-016-05 | South Labs-Plantroom | FD 64 | South Labs Plantroom AHU | 1/S/18 | 3120 | Supply
P14-016-05 | South Labs-Plantroom | FD 65 | South Labs Plantroom | 1/S/2/1 | 3118-3122-3127-3134-5052-5059 | Extract
P14-016-05 | South Labs-Plantroom | FD 66 | South Labs Plantroom AHU 1/S/4 | AHU 1/S/4 | 3112 | Supply |  |  | - | - | Exception | No | No routine access to fire damper | Ductwork to be modified to allow
P14-016-05 | South Labs-Plantroom | FD 66A | South Labs Plantroom AHU 1/S/4 | AHU 1/S/4 | 3112 | Supply |  |  | Light | No | Standard | Yes |  | Ductwork to be modified to allow new access door to be fitted
P14-016-05 | South Labs-Plantroom | FD 66B | South Labs Ground Floor Corridor Riser Cupboard | AHU 1/S/10 | 3102 | Supply |  |  | Clean | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 67 | South Labs Plantroom AHU | 1/S/19 | 3116 | Supply
P14-016-06 | South Labs-Plantroom | FD 67A | South Labs Plantroom AHU | 1/S/18 | 3120 | Supply
P14-016-05 | South Labs-Plantroom | FD 68 | South Labs Plantroom AHU | Capped off | N/A Not In Use | N/A
P14-016-05 | South Labs-Plantroom | FD 69 | South Labs Plantroom AHU | 1/S/11 |  | Supply
P14-016-06 | South Labs-Plantroom | FD 69A | South Labs Plantroom AHU | 1/S/19 |  | Supply
P14-016-05 | South Labs-Plantroom | FD 70 | South Labs Plantroom AHU | 1/S/11 |  | Supply
P14-016-05 | South Labs-Plantroom | FD 71 | South Labs Plantroom AHU | 1/S/3 | N/A Not In Use | Supply
P14-016-05 | South Labs-Plantroom | FD 72 | South Labs Plantroom AHU | 1/S/3 | N/A Not In Use | Supply
P14-016-05 | South Labs-Plantroom | FD 73 | South Labs Plantroom AHU | 1/S/3 | N/A Not In Use | Supply
P14-016-05 | South Labs-Plantroom | FD 74 | South Labs Plantroom AHU | 1/S/3 | N/A Not In Use | Supply
P14-016-05 | South Labs-Plantroom | FD 75 | South Labs Plantroom AHU | 1/S/32 | 3114 | Supply
P14-016-05 | South Labs-Plantroom | FD 76 | South Labs Plantroom AHU | 1/S/21 | 5038 | Supply
P14-016-05 | South Labs-Plantroom | FD 77 | South Labs Plantroom AHU | 1/S/21 | 5038 | Supply
P14-016-05 | South Labs-Plantroom | FD 78 | South Labs Plantroom | Goes to ex box on outside wall | 3114 | Extract
P14-016-05 | South Labs-Plantroom | FD 79 | South Labs Plantroom | Asset 1368 | 3114 | Extract
P14-016-05 | South Labs-Plantroom | FD 80 | South Labs Plantroom AHU | Asset 1367 1/S/32 | 3108 | Supply
P14-016-05 | South Labs-Plantroom | FD 81 | South Labs Plantroom | Ex box on outside wall | 3108 | Extract
P14-016-05 | South Labs-Plantroom | FD 82 | South Labs Plantroom AHU | 1/S/32 | 3103 | Supply
P14-016-05 | South Labs-Plantroom | FD 83 | South Labs Plantroom AHU | 1/S/10 | Coloured PCR suite 3098-3102-3103-3104-3103a | Supply
P14-016-05 | South Labs-Plantroom | FD 84 | South Labs Plantroom AHU | 1/S/32 | 3103 | Supply
P14-016-05 | South Labs-Plantroom | FD 85 | South Labs Plantroom | 1/S/38/1 Asset 2160 | Coloured PCR suite 3095-3106 | Extract
P14-016-05 | South Labs-Plantroom | FD 86 | South Labs Plantroom AHU | 1/S/7 | 5035 | Supply
P14-016-05 | South Labs-Plantroom | FD 87 | South Labs Plantroom AHU | 1/S/7 | 5035 | Supply
P14-016-05 | South Labs-Plantroom | FD 88 | South Labs Plantroom AHU | 1/S/28 | 5032 | Supply
P14-016-05 | South Labs-Plantroom | FD 89 | South Labs Plantroom AHU | 1/S/22 | 5038 | Supply
P14-016-05 | South Labs-Plantroom | FD 90 | South Labs Plantroom AHU | 1/S/22 | 5038 | Supply
P14-016-05 | South Labs-Plantroom | FD 91 | South Labs Plantroom AHU | Asset 1365 | 3103 | Supply
P14-016-05 | South Labs-Plantroom | FD 92 | South Labs Plantroom | 1/S/38/1 | PCR coloured suite | Extract
P14-016-05 | South Labs-Plantroom | FD 93 | South Labs Plantroom | Ex box on outside wall | 3103 | Extract
P14-016-05 | South Labs-Plantroom | FD 94 | South Labs Plantroom AHU | 1/S/10 | Coloured PCR suite 3098-3102-3103-3104-3103a | Supply |  |  | - | - | Exception | No | No routine access to fire damper | Ductwork to be modified to allow new access door to be fitted
P14-016-05 | South Labs-Plantroom | FD 95 | South Labs Plantroom | 1/S/24/1 | Coloured PCR suite 3088-3089-3090-3091-3094-3095 | Extract
P14-016-05 | South Labs-Plantroom | FD 96 | Still to be tested | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find
P14-016-05 | South Labs-Plantroom | FD 97 | Still to be tested | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find | Can't find
P14-016-05 | South Labs-Plantroom | FD 98 | South Labs Plantroom | Asset 2158, 1/S/37/1 | 3097 | Extract
P14-016-05 | South Labs-Plantroom | FD 99 | South Labs Plantroom | Asset 2159, 1/S/37/2 | 3097 | Extract
P14-016-05 | South Labs-Plantroom | FD 100 | South Labs Plantroom AHU | 1/S/33, PCR | 3087-3088-3089-3090-3097-3098-3101-3103-3108-3114. Retro | Supply
P14-016-05 | South Labs-Plantroom | FD 101 | South Labs Plantroom AHU | 1/S/33, PCR | 3087-3088-3089-3090-3097-3098-3101-3103-3108-3114. Retro | Supply
P14-016-05 | South Labs-Plantroom | FD 102 | South Labs Plantroom AHU | 1/S/33, PCR | 3087-3088-3089-3090-3097-3098-3101-3103-3108-3114. Retro | Supply
P14-016-05 | South Labs-Plantroom | FD 103 | South Labs Plantroom | Asset 1375 | 3087 | Extract
P14-016-05 | South Labs-Plantroom | FD 104 | South Labs Plantroom | Ex box on outside wall. No asset no: |  | Extract
P14-016-05 | South Labs-Plantroom | FD 105 | South Labs Plantroom AHU | No asset, no no: |  | Supply
P14-016-05 | South Labs-Plantroom | FD 106 | South Labs Plantroom AHU | No asset, no no: |  | Supply
P14-016-05 | South Labs-Plantroom | FD 107 | South Labs Plantroom | Ex box on outside wall. No asset no: |  | Extract
P14-016-05 | South Labs-Plantroom | FD 108 | South Labs Plantroom | Asset 1379 1/S/33/3 | 3089 | Extract
P14-016-05 | South Labs-Plantroom | FD 109 | South Labs Plantroom | Asset 1380 1/S/33/4 | 3090 | Extract
P14-016-05 | South Labs-Plantroom | FD 111 | South Labs Plantroom Void AHU 1/S/2 | 1/S/2 | 3118-3122-3127-3134-5052-5059 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 112 | South Labs First Floor Lab EX 1/S/2/1 | EX 1/S/2/1 | 3118-3122-3127-3134-5052 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 113 | South Labs First Floor Lab EX 1/S/2/1 | EX 1/S/2/1 | 3118-3122-3127-3134-5052 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 114 | South Labs Plantroom EX 1/S/4/1 | EX 1/S/4/1. Asset 1218 | 3112 | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 114A | South Labs Plantroom EX 1/S/34/1 | EX 1/S/34/1. Asset 1381 | 5041 | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 115 | South Labs Plantroom through wall EX1/S/10/1 | EX 1/S/10/1 high level | 3098-3102-3103-3104-3103a | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom | FD 116 | South Labs Plantroom EX 1/S/10/1 | EX 1/S/10/1 | Coloured PCR suite 3098-3102-3103-3104-3103a | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-05 | South Labs-Plantroom | FD 116A | South Labs Corridor, Ground Floor Riser Cupboard EX 1/S/10/1 | EX 1/S/10/1 | Coloured PCR suite 3098-3102-3103-3104-3103a | Extract |  |  | Light | No | Standard | Yes
P14-016-05 | South Labs-Plantroom |  | South Labs Plantroom Void AHU 1/S/38 PCR labs | AHU 1/S/38 | Coloured PCR suite 3094- 3095-3104-3105-3106 | Supply
P14-016-05 | South Labs-Plantroom |  | South Labs Plantroom Void AHU 1/S/38 PCR labs | AHU 1/S/38 | Coloured PCR suite 3094- 3095-3104-3105-3106 | Supply
P14-016-06 | South Labs-Plantroom | FD 120 | South Labs Plantroom EX 1/S/33/2. Asset no: 1377 | 1/S/33/2 | 3088 | Extract
P14-016-07 | South Labs-Plantroom | FD 121 | South Labs Plantroom | 1/S/24/1 | Coloured PCR suite 3088-3089-3090-3091-3094-3095 | Extract
P14-016-05 | South Labs-Plantroom | FD 122 | South Labs Plantroom. In bulkhead wall | 1/S/29 | Not In Use. 3095, PCR | Supply
P14-016-08 | Biotec-Plantroom | FD 01 | Biotech Plantroom - AHU& 7/1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Standard | Yes |  | Switching off AHU affects the pressures in the CL3 labs B20 & B32
P14-016-08 | Biotec-Plantroom | FD 02 | Biotech Plantroom - B37 | 07/1/1- Asset 1263 | North side.B32-B34-B37-B39-B40-B41-B49 | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 03 | Biotech Plantroom - B37 | 07/1/1- Asset 1263 | North side.B32-B34-B37-B39-B40-B41-B49 | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 04 | Biotech Plantroom - AHU 7/1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Standard | Yes |  | Switching off AHU affects the pressures in the CL3 labs B20 & B32
P14-016-08 | Biotec-Plantroom | FD 05 | Biotech Plantroom - AHU 7/1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Exception | No | Fire damper faulty and will not release | Fire damper mechanism to be checked or new fire damper fitted. Switching off AHU affects the pressures in the CL3 labs B20 & B32
P14-016-08 | Biotec-Plantroom | FD 06 | Biotech Plantroom | 07/1/1- Asset 1263 | North side.B32-B34-B37-B39-B40-B41-B49 | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 07 | Biotech Plantroom - AHU 7/1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Standard | Yes |  | Switching off AHU affects the pressures in the CL3 labs B20 & B32
P14-016-08 | Biotec-Plantroom | FD 08 | Biotech Plantroom - B37 | 07/1/1- Asset 1263 | North side.B32-B34-B37-B39-B40-B41-B49 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 09 | Biotech Plantroom - AHU /1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 10 | Biotech Plantroom - AHU 7/1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Standard | Yes |  | Switching off AHU affects the pressures in the CL3 labs B20 & B32
P14-016-08 | Biotec-Plantroom | FD 11 | Biotech Plantroom - AHU 7/1 | 7/1 | North side.B32-B34-B37-B39-B40-B41-B49 | Supply |  |  | Moderate | Yes | Standard | Yes | Hole in slab, will need fire rating seal | Switching off AHU affects the pressures in the CL3 labs B20 & B32
P14-016-08 | Biotec-Plantroom | FD 12 | Biotech Plantroom | 07/1/1- Asset 1263 |  | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 13 | Biotech Plantroom | 07/1/1- Asset 1263 |  | Extract |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-08 | Biotec-Plantroom | FD 14 | Biotech Plantroom | 7/5 | Toilets | Supply |  |  | - | - | Exception | No | Fire damper faulty and will not close | Fire damper to be replaced
P14-016-08 | Biotec-Plantroom | FD 15 | Biotech Plantroom Toilet | 7/2 |  | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 16 | Biotech Plantroom Toilet | 7/2 |  | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 17 | Biotech Plantroom - AHU 7/2 | 7/2 | South side. B16-B19-B21-B23-B25 | Supply |  |  | Moderate | Yes | Standard | Yes |  | New fusible link fitted
P14-016-08 | Biotec-Plantroom | FD 18 | Biotech Plantroom - AHU 7/2 | 7/2 | South side. B16-B19-B21-B23-B25 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 19 | Biotech Plantroom | 7/2 | B21 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 20 | Biotech Plantroom | 7/2 | B23 | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 21 | Biotech Plantroom - AHU 7/2 | 7/2 | South side. B16-B19-B21-B23-B25 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 22 | Biotech Plantroom | 7/2 |  | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 23 | Biotech Plantroom | 7/2 |  | Extract |  |  | Heavy | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 24 | Biotech Plantroom - AHU 7/2 | 7/2 | South side. B16-B19-B21-B23-B25 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 25 | Biotech Plantroom - AHU 7/2 | 7/2 | South side. B16-B19-B21-B23-B25 | Supply |  |  | Moderate | Yes | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 26 | Biotech Plantroom - AHU 7/5 | 7/5 | B29 | Supply |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 27 | Biotech Plantroom - AHU 7/5 | 7/5 | B29 | Supply |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 28 | Biotech Plantroom - AHU 7/5 | 7/5 | B29 | Supply |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 29 | Biotech Plantroom - Extract Fans 1 & 2 | Asset 1265 |  | Extract |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 30 | Biotech Plantroom - Extract Fans 1 & 2 | Asset 1265 |  | Extract |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 31 | Biotech Plantroom - AHU 7/5 | 7/5 Asset 1257 | B29 | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-08 | Biotec-Plantroom | FD 32 | Biotech Plantroom - Extract Fans 1 & 2 far end |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 33 | Biotech Plantroom - Extract Fans 1 & 2 far end |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 34 | Biotech Plantroom - Extract Fans 1 & 2 |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 35 | Biotech Plantroom - Extract Fans 1 & 2 | asset 1265 |  | Extract |  |  | Light | No | Standard | Yes
P14-016-08 | Biotec-Plantroom | FD 36 | Biotech Plantroom - AHU 7/6 | AHU 7/6 | B20 | Supply |  |  |  |  | Standard
P14-016-08 | Biotec-Plantroom | FD 37 | Biotech Plantroom - EX/7/6 | AHU 7/6 | B20 | Extract |  |  |  |  | Standard
P14-016-08 | Biotec-Plantroom | FD 38 | Biotech Plantroom - |  |  | Supply |  |  |  |  | Standard
P14-016-14 | Biotech-Undercroft- Transformer room B03 | FD 01 | Undercroft, Fridge Room - AHU 7/7- Transformer room B03 | AHU 7/7 | Undercroft, Fridge Room | [5 empty] | Standard |  | No fire damper fitted | Recommend fire damper be fitted as duct is a fire hazard as it is fed through a high voltage plantroom.
P14-016-14 | Biotech-Undercroft | FD 02 | Undercroft, Fridge Room - AHU 7/7- Transformer room B03 | AHU 7/7 | Undercroft, Fridge Room | [5 empty] | Standard |  | No fire damper fitted | Recommend fire damper be fitted as duct is a fire hazard as it is fed through a high voltage plantroom.
P14-016-14 | Biotech-Undercroft | FD 03 | Transformer room B03 | [7 empty] | Standard |  | Access poor | Label required
P14-016-14 | Biotech-Undercroft | FD 04 | Biotech Riser behind lift shaft | [7 empty] | Standard |  | Access poor | Label required
P14-016-14 | Biotech-Undercroft | FD 05 | Biotech Riser behind lift shaft | [7 empty] | Standard |  | Access poor | Label required
P14-016-14 | Biotech-Undercroft | FD 06 | Biotech Riser behind lift shaft | [7 empty] | Standard |  | Access poor | Label required
P14-016-08 | Biotec-Plantroom |  | Biotech Plantroom - B31 CL3 | AHU7/4 | B31 | Supply
P14-016-06 | CBRM-Plantroom Level | FD 01 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 02 | CBRM Upper Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 03 | CBRM Upper Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 04 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 04A | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 05 | CBRM Upper Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 06 | CBRM Upper Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 07 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 08 | CBRM Upper Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 09 | CBRM Upper Plantroom |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 10 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 11 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 12 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 13 | CBRM Upper Plantroom |  |  | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 14 | CBRM Upper Plantroom |  |  | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 15 | CBRM Upper Plantroom |  |  | Extract |  |  | - | - | Exception | No | Access to fire damper restricted by wall
P14-016-06 | CBRM-Plantroom Level | FD 16 | CBRM Upper Plantroom |  |  | Extract |  |  | - | - | Exception | No
P14-016-06 | CBRM-Plantroom Level | FD 17 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 18 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-06 | CBRM-Plantroom Level | FD 19 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 20 | CBRM Plantroom Landing |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 21 | CBRM Plantroom Landing |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 22
P14-016-07 | CBRM-Plantroom Level | FD 23
P14-016-07 | CBRM-Plantroom Level | FD 24 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 25 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | - | - | Exception | No | No access door fitted
P14-016-07 | CBRM-Plantroom Level | FD 26 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | - | - | Exception | No | Unable to access fire damper due to pipework in the way | Pipework blocking access to be removed or ductwork altered to provide new access section.
P14-016-07 | CBRM-Plantroom Level | FD 27 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | - | - | Exception | Yes | No access door fitted | New access section to be installed.
P14-016-07 | CBRM-Plantroom Level | FD 28 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | - | - | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 29 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 30 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 30A | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 30B | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 30C | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 31
P14-016-07 | CBRM-Plantroom Level | FD 32
P14-016-07 | CBRM-Plantroom Level | FD 33
P14-016-07 | CBRM-Plantroom Level | FD 34 | CBRM Walk on Ceiling Access 3 |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 35 | CBRM Walk on Ceiling Access 3 |  |  | Extract |  |  | Moderate | Yes | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 36 | Above ceiling in Room 2.12 Dry Goods & 2.13 |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 37 | Above ceiling in Room 2.12 Dry Goods & 2.13 |  |  | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-07 | CBRM-Plantroom Level | FD 38 | Above ceiling in Room 2.12 Dry Goods & 2.13 |  |  | Supply |  |  | - | - | Exception | No | No access door fitted | New access section to be installed.
P14-016-07 | CBRM-Plantroom Level | FD 39 | Above ceiling in Room 2.12 Dry Goods & 2.13 |  |  | Supply |  |  | Clean | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 40 | Above ceiling in Room 2.12 Dry Goods & 2.13 |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 41 | Above ceiling in Room 2.12 Dry Goods & 2.13 |  |  | Supply |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 42 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 43 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 44 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 45 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 46 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 47 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 48 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 49 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 50 | Above ceiling in Room 2.12 Dry Goods & 2.13
P14-016-07 | CBRM-Plantroom Level | FD 51
P14-016-07 | CBRM-Plantroom Level | FD 52
P14-016-07 | CBRM-Plantroom Level | FD 53
P14-016-07 | CBRM-Plantroom Level | FD 54
P14-016-07 | CBRM-Plantroom Level | FD 55
P14-016-06 | CBRM-Plantroom Level | FD 56 | CBRM Upper Plantroom |  |  | Extract |  |  | Light | No | Standard | Yes
P14-016-07 | CBRM-Plantroom Level | FD 56
P14-016-07 | CBRM-Plantroom Level | FD 57
P14-016-07 | CBRM-Plantroom Level | FD 58
P14-016-07 | CBRM-Plantroom Level | FD 59
P14-016-07 | CBRM-Plantroom Level | FD 60
P14-016-07 | CBRM-Plantroom Level | FD 61
P14-016-07 | CBRM-Plantroom Level | FD 62
P14-016-07 | CBRM-Plantroom Level | FD 63
P14-016-07 | CBRM-Plantroom Level | FD 64
P14-016-07 | CBRM-Plantroom Level | FD 65
P14-016-07 | CBRM-Plantroom Level | FD 66
P14-016-07 | CBRM-Plantroom Level | FD 67
P14-016-07 | CBRM-Plantroom Level | FD 68
P14-016-07 | CBRM-Plantroom Level | FD 69
| CBRM-Plantroom Level |  | 1.03-1.05-1.06-1.07-1.08-1.09-1.10-1.11-1.12-1.13-1.14-1.15-1.16-1.17-1.23-1.24 | AHU-1
| CBRM-Plantroom Level |  | 3.1-3.11-3.35 | AHU2
| CBRM-Plantroom Level |  | 2.19-2.2 | AHU3
| CBRM-Plantroom Level |  | 3.07-3.08-3.34 | AHU4
| CBRM-Plantroom Level |  | 2.21-2.18-1.17-3.02.3.01-.3.19-3.05-3.18-3.17-3.24 | AHU5
| CBRM-Plantroom Level |  | 3.16-3.2-3.22-3.23-3.3 | AHU6
| CBRM-Plantroom Level |  | 2.08-2.14-2.15 | AHU7
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 01 | Building 4 , Plantroom Level, - AHU 4/2 | AHU 4/2 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Supply
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 02 | Building 4 , Plantroom Level, - AHU 4/2 | AHU 4/2 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Supply
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 03 | Building 4 , Plantroom Level, - AHU 4/2 | AHU 4/2 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Supply
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 04 | Building 4 , Plantroom Level, - AHU 4/2 | AHU 4/2 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Supply
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 05 | Building 4 , Plantroom Level - AHU 4/2 | AHU 4/2 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Supply
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 06 | Building 4, Plantroom Level, - EX/4/2/1 | EX/4/2/1 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Extract
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 07 | Building 4, Plantroom Level, - EX/4/2/1 | EX/4/2/1 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Extract
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 08 | Building 4, Plantroom Level, - EX/4/2/1 | EX/4/2/1 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Extract
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 09 | Building 4, Plantroom Level, - EX/4/2/1 | EX/4/2/1 | 6077-6078-6079-6083-6084-6085-6086-6087-6088-6089-6091-6092-6093-6094-6095-6096-6097-6098-6099-6100-6101-6102-6103-6113-6114-6115-6116-6117-6118-6119-6121-6122-6132-6145-6146-6150-6151-6152-6153-6154-6155-6156-6157-6158-6159-6160-6161-6162 | Extract
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 10 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 11 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 12 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 13 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 14 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 15 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 16 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 17 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 18 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 19 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 20 | Still to be tested
P14-016-13-2 | BSD, PLANTROOM LEVEL | FD 21 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 01 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 02 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 03 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 04 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 05 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 06 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 07 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 08 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 09 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 10 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 11 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 12 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 13 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 14 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 15 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 16 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 17 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 18 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 19 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 20 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 21 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 22 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 23 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 24 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 25 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 26 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 27 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 28 | Still to be tested
P14-016-13 | BSD, LOWER FLOOR PLANTROOM | FD 29 | Still to be tested
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 01 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 02 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 03 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 04 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 05 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 06 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 07 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 08 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 09 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061- | Supply
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 10 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061- | Supply
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 11 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061- | Extract
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 12 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061- | Supply | [6 empty] | Unable to access due to solid ceiling in the way | Solid ceiling blocking access to be modified or ductwork altered to provide new access section
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 13 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061- | Extract | [6 empty] | Unable to access due to solid ceiling in the way | Solid ceiling blocking access to be modified or ductwork altered to provide new access section
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 14 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 15 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 16 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 17 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 18 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 19 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 20 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 21 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 22 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 23 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 24 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 25 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 26 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-4 | BSD, PLANTROOM AHU 4/4 | FD 27 |  |  | 7042-7043-7044-7045-7046-7047-7047a-7048-7048a-7049-7050-7051-7052-7053-7054-7055-7056-7057-7058-7059-7060-7061-
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 01 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 02 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 03 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 04 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 05 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 06 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 07 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 08 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 09 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 10 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 11 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 12 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 13 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 14 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 15 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 16 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 17 | Building 4, Plantroom Level - AHU 4/5 | AHU 4/5 | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031 | Supply
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 18 | Building 4, Plantroom Level - AHU 4/5 | AHU 4/5 | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031 | Supply
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 19 | Building 4, Plantroom Level - AHU 4/5 | AHU 4/5 | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031 | Extract
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 20 | Building 4, Plantroom Level, above Plantroom Door AHU 4/5 | AHU 4/5 | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031 | Supply
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 21 | Building 4, Plantroom Level (Mezz) - AHU 4/5 | AHU 4/5 | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031 | Extract
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 22 | Building 4, Plantroom Level - AHU 4/5 | AHU 4/5 | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031 | Extract
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 23 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 24 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 25 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-14-5 | BSD, PLANTROOM - AHU 4/5 | FD 26 | Still to be tested |  | 7009-7010-7011-7015-7016-7017-7018-7019-7020-7021-7022-7023-7024-7025-7026-7027-7028-7029-7030-7031
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 01 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 02 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 03 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 04 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 05 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 06 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 07 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 08 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 09 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 10 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 11 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 12 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 13 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 14 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 15 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 16 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 17 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 18 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 19 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 20 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 21 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 22 | Still to be tested |  | 6124-6125-6126-6127-6128
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 23 | Still to be tested |  | 6124-6125-6126-6127-6128 | Supply
P14-016-13--9 | BSD, PLANTROOM LEVEL 4/9 | FD 24 | Still to be tested |  | 6124-6125-6126-6127-6128 | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 01 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 02 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 03 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 04 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 05 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 06 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 07 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 08 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 09 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 10 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 11 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 12 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 13 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 14 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 15 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 16 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 17 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 18 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 19 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 20 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 21 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 22 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 23 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 24 | Still to be tested
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 25 | Building 4, Plantroom Level - AHU 4/10 | AHU 4/10 | 7008-7012-7013 | Supply
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 26 | Building 4, Plantroom Level - AHU 4/10/1 | EX/4/10/1 | 7008-7012-7013 | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 27 | Building 4, Plantroom Level - EX/4/10/1 | EX/4/10/1 | 7008-7012-7013 | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 28 | Building 4, Upper level on Roof in Void 7 - AHU 4/10/1 | AHU 4/10 | 7008-7012-7013 | Supply
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 29 | Building 4, Upper level on Roof in Void 7 - AHU EX/4/10/1 | AHU 4/10 | 7008-7012-7013 | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 30 | Building 4, Plantroom - AHU 4/3 | AHU 4/3 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Supply | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 31 | Building 4, Plantroom - AHU 4/3 | AHU 4/3 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Supply | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 32 | Building 4, Plantroom - EX/4/3/1 | EX/4/3/1 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Extract | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 33 | Building 4, Plantroom - AHU 4/3 | AHU 4/3 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Supply | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 34 | Building 4, Plantroom - EX/4/3/1 | EX/4/3/1 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Extract | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 35 | Building 4, Plantroom - AHU 4/3 | AHU 4/3 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Supply | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 36 | Building 4, Plantroom - EX/4/3/1 | EX/4/3/1 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Extract | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 37 | Building 4, Plantroom - EX/4/3/1 | EX/4/3/1 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Extract | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 38 | Building 4, Plantroom - AHU 4/3 | AHU 4/3 | 6133-6135-6136-6134-6134a-6138-6138a-6139-6134-6140-6142-6144-6141 | Supply | [6 empty] | ACF 4/3 is interlocked with 4/2
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 39 | Building 4, Plantroom Void through Latch Door |  |  | Supply
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 40 | Building 4, Plantroom, Void Extract |  |  | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 41 | Building 4, Plantroom, Void Extract |  |  | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 42 | Building 4, Plantroom, Void Extract |  |  | Extract
P14-016-14-10 | BSD, PLANTROOM LEVEL | FD 43 | Building 4, Plantroom, Void Extract |  |  | Extract
| BSD |  | BSD out side on the grass adjacent to 6080 | AHU 4/12 | 6080-6081-6082- | Supply
| BSD |  | BSD out side on the grass adjacent to 6080 | AHU 4/12 | 6080-6081-6082- | Supply
| BSD |  | BSD out side on the grass adjacent to 6080 | AHU 4/12 | 6080-6081-6082- | Supply
| BSD |  | BSD out side on the grass adjacent to 6080 | AHU 4/12 | 6080-6081-6082- | Supply
P14-016-10 | IRC/Stem Cell Bank | FD01 | Near and above stairwell |  | Near and above stairwell | Extract
P14-016-10 | IRC/Stem Cell Bank | FD02 | Near and above stairwell |  | Near and above stairwell | Supply
P14-016-10 | IRC/Stem Cell Bank | FD03 | Near and above stairwell |  | Near and above stairwell | Extract
P14-016-10 | IRC/Stem Cell Bank | FD04 | Near and above stairwell |  | Near and above stairwell | Extract
P14-016-12 | Kitchen | FD01 | Plantroom above Kitchen |  | Plantroom above Kitchen | Supply
P14-016-12 | Kitchen | FD02 | Plantroom above Kitchen |  | Plantroom above Kitchen | Extract
P14-016-12 | Kitchen | FD03 | Plantroom above Kitchen-Main Kitchen by Dishwasher |  | Plantroom above Kitchen-Main Kitchen by Dishwasher | Supply
P14-016-12 | Kitchen | FD04 | Plantroom above Kitchen-Main Kitchen by Dishwasher |  | Plantroom above Kitchen-Main Kitchen by Dishwasher | Extract
CBI LABS, ROOF
20507-03 | CBI Labs, Roof | [11 empty] | No fire dampers found
CBI ADVANCED THERAPIES, LABS
20507-01 | CBI Advanced Therapies, Labs | [11 empty] | No fire dampers found
NCTC GROUND FLOOR
M-NCTC-GF-M5129 | NCTC Ground Floor |  | - | - | - | - | [6 empty] | No fire dampers found
FLEXIBLE CONTAINMENT SUITE - PLANTROOM
P14-016-08 | Flexible containment Suite - Plantroom |  | Plantroom |  | 3048, 3049,3050,3051,3052, 3053,3054 & 3035 | [7 empty] | No fire dampers found. Plantroom wall appears to be a fire wall and the requirement for fire dampers needs to be investigated.
CBRM - PLANTROOM LEVEL