Part 2 – ITQ – Specification - Kettering Swimming Pool, London Rd. Kettering – Repairs and Refurbishment of Ventilation System.


PART TWO
SPECIFICATION

PREAMBLE

General Requirements
Tenders are invited from Kettering Borough Council for the Repairs & Refurbishment of the Ventilation System at Kettering Swimming Pool, London Road, Kettering, Northamptonshire. NN15 7QA.

Information, Costs and Expenses

Contractors are responsible for obtaining all information necessary for the preparation of their Quotation and all costs expenses and liabilities incurred in connection with the preparation and submission of a quotation.

Submission of Quotation

Your quotation should be submitted together with any Pricing Schedule and Supporting Information to:

webprocurement@kettering.gov.uk.

Further information and Queries

Please address any queries or requests for further information to:

webprocurement@kettering.gov.uk 

Freedom of Information Act 2000:
a. Information in relation to this tender may be made available on demand in accordance with the requirements of the Freedom of Information Act 2000.

b. Contractors should state if any of the information supplied by them is confidential or commercially sensitive or should not be disclosed in response to a request for information under the Act.  Contractors should state why they consider the information to be confidential or commercially sensitive.  This will not guarantee that the information will not be disclosed but will be examined in the light of the exemptions provided in the Act.

c. It is important to note that information may be commercially sensitive for a time (e.g. during a tender process) but afterwards it may not be.  The timing of any request for information may be extremely important in determining whether information is exempt.  However contactors should note that no information is likely to be regarded as exempt forever.

OUTLINE SPECIFICATION
Location
Kettering Swimming Pool is located close to Kettering town centre next to a busy junction and a long stay car park at London Road, Kettering NN15 7QA and is managed by our leisure operator. 

The Swimming Pool is part of a small complex that includes a reception area, gymnasium, changing rooms and offices associated with the buildings use. 

 Background 

The Swimming Pool opened in 1984 with the last major works to the Swimming Pool Plant and equipment being undertaken approximately 15 years ago when the facility was expanded, the Pool area refurbished and re-tiled.  In 2016 some minor works were undertaken around the Pool when the ceiling was repaired and lined without the pool being emptied.  

For approximately 7 year’s no work has been undertaken on the Ventilation System and it is no longer working as was originally intended. 

 Following a recent non-intrusive inspection of the Ventilation System it was found that: 

1. The ventilation unit serving the Plant Room required repair and servicing.

2. The ventilation units serving the Gents Changing Room and Foyer & Foyer Toilets required replacement.

3. The ventilation units serving the Female Changing Room, Showers and Toilets required servicing.

4. All the Ductwork and Pipework required cleansing and minor repairs.

5. The whole system required a major service. 

Execution of Works and Access to the Works Area  

 It is anticipated that all the works to the Ventilation System will be undertaken as a continuous operation with the Pool and changing rooms being available to the public for the shortest practicable time. 

 Contractors should include the number of days when the Pool will not be available in their quotation. 

Access for the work will be via the double doors to the rear of the swimming pool from Kettering Borough Council’s London Road Car Park. 

 Spaces for the Contractors equipment and vehicles adjacent to the Plant Rooms entrance to the London Road car park will be reserved whilst the works are being undertaken. 

Contractors can undertake works during the normal opening hours for the Gymnasium at the site:  
Monday to Friday inclusive: 07:00 to 22:00, Saturday: 07:00 to 17:00 and Sunday from 07:00 to 20:30 

Contractors must ensure that the Swimming Pool and Changing Rooms are available for use over Bank Holiday periods: 

Contractors will be able to work in the Plant Room alone outside Opening Hours following a request to do so being approved by Hazelwebb@kettering.gov.uk.

Introduction and Outline of Works
The current Menerga ventilation units serving Kettering Swimming Pool are in a poor state of repair and are not currently working as intended. When last fully operational to the original specification the 5 units provided satisfactory Ventilation to the Pool side of the complex with exception of the accommodation next to the reception desk. The intention is to repair and refurbish the ventilation system as part of the works to be executed at the complex and to install one or more air conditioning units to serve the accommodation next to the reception desk.  

Core Works

Repairs and refurbishment of the existing ventilation system as part of an exercise to undertake all repairs and some updates to the Swimming Pool including works to the Plant Room and to the Heating & Hot Water systems.

It is intended to improve the Ventilation system at the Swimming Pool by:

1. Installing a new Air Conditioning unit in or next to the Foyer to serve the proposed First Aid / Staff room, the Managers Office and room to the rear of the reception area.

2. Repair and Servicing of the Roof level, Plant Room ventilation unit that serves the Pool Area.

3. Replacement of the Roof level ventilation unit and Servicing of all the ductwork and filters that serve the Gents Changing rooms.

4. Replacement of the Roof level ventilation unit and Servicing of the ductwork and filters that serve the Foyer and Foyer Toilets.

5. Servicing of the Roof Level Ventilation unit and the ductwork and filters that serve the Female Changing rooms.
6. Servicing of the Roof Level Ventilation unit and the ductwork and filters that serve the Female Changing rooms.

It is envisaged that there will be a minimum of disturbance to customers and staff at the Swimming Pool complex and any equipment and / or materials arising from the works should be removed from site and properly disposed of.

Contractors should indicate the area of the works that they will require in London Road Car Park to undertake the work and / or install any scaffolding or access platforms.

Contractors should indicate the intended sites for storage of materials when submitting their tender.

Contractors should indicate the measures that they will take and the time that they have allowed to undertake the works and how they will allow the complex to be used during the period for which they are likely to be on site.

Responsibilities

The Pubic Services Team is responsible for the contract with Legacy Leisure who manage the complex for Kettering Borough Council. and for these works being executed. 

Use of Site

The Swimming Pool Complex is used by occasional and regular users including Schools, Local Clubs, Local Specialist Groups and private hire.

Any bookings for use outside the normal opening hours are made at least 14 working days in advance and the successful contractor will be given 10 days notice of any of these bookings.
It is essential that the works are arranged in a manner that does not allow the public to access the work areas from the public car park or areas within the swimming pool complex. 

 It is essential that the amount of time that the Pool is not available for use is minimised and it is not anticipated that any request to work outside opening hours will be refused. Contractors should indicate their working hours and the time that the Pool will be closed in their quotation return. 

 It is essential that the works area/s are secured when work is not being undertaken particularly overnight and at weekends to prevent any person/s having access to the site area.
1

